## MtEmVd
Type | Template Fullname | Property Name | Prop. Name SetId | Prop. Name EnumId | Prop. Id | Requ. | Write-able | Priority Flag | Data Type Id | Data Type | Display Prec. (IP) | Display Prec. ID (IP) | Unit (IP) | Unit Id (IP) | Default | Min Value (IP) | Max Value (IP) | Min Prop. (IP) | Max Prop. (IP) | Display Prec. (SI) | Display Prec. ID (SI) | Unit (SI) | Unit Id (SI) | Min Value (SI) | Max Value (SI) | Min Prop. (SI) | Max Prop. (SI) | String Max Length | UseIds | MultiState SetId | MultiState Enums | Remarks | Type | Model Fullname | EM Object Id | Attribute | Data Src./Trgt. Object | Data Src./Trgt. Attribute | Used as Pres. Ind. | Trend Buffer Size | Trend Interv. [s] | Presence Indicator | FC-Bus BACnet | FC-Bus Modbus | FC-Bus N2 | Remarks | Type | Internal View | Minor Group | Folder Fullname (Long) | Point (Long) | Name SetId (Long) | Name EnumId (Long) | Custom Name | Folder Fullname (Short) | Point (Short) | Name SetId (Short) | Name EnumId (Short) | Presence Indicator | Remarks
Tmpl | Templates.York RTU | [31 empty] | Model | York RTU | 1
Prop | Templates.York RTU | Unit Status | 1675 | 0 | 7000 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | SE RTU Unit Status | 1737 | Idle | [6 empty] | SE RTU Unit Status | 1737 | [5 empty] | Unit Status | 1737 | 0 = Idle 1 = SD Alarm 2 = Purge Command 3 = Self Test ... |  | Attr | York RTU | 1 | Unit Status | UCBapp.newUCB.Unit_Status | Present Value | FALSE |  |  |  | MV:29803 | IR:280 | ADI:1 |  | Value |  |  | Views.Status.Status | Unit Status | 1675 | 0 |  | Views.Status.Status | Unit-S | 1709 | 0
Prop | Templates.York RTU | Unit Status | 1675 | 0 | 7000 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | SE RTU Unit Status | 1737 | Idle | [6 empty] | SE RTU Unit Status | 1737 | [5 empty] | Unit Status | 1737 | 0 = Idle 1 = SD Alarm 2 = Purge Command 3 = Self Test ... |  | Attr | York RTU | 1 | Unit Status | UCBapp.newUCB.Unit_Status | Present Value | FALSE |  |  |  | MV:29803 | IR:280 | ADI:1 |  | Value |  |  | Views.Summary.Unit | Unit Status | 1675 | 0 |  | Views.Summary.Unit | Unit-S | 1709 | 0
Prop | Templates.York RTU | Unit Name | 1675 | 1 | 7001 | TRUE | TRUE | FALSE | 7 | String | [17 empty] | 30 |  |  |  |  | Attr | York RTU | 1 | Unit Name | UCBapp | System Name | FALSE |  |  |  | CSV:29804 |  |  |  | Value |  |  | Views.Summary.Unit | Unit Name | 1675 | 1 |  | Views.Summary.Unit | Name | 1709 | 1
Prop | Templates.York RTU | Unit Name | 1675 | 1 | 7001 | TRUE | TRUE | FALSE | 7 | String | [17 empty] | 30 |  |  |  |  | Attr | York RTU | 1 | Unit Name | UCBapp | System Name | FALSE |  |  |  | CSV:29804 |  |  |  | Value |  |  | Views.Clone.Full Clone | Unit Name | 1675 | 1 |  |  | Name | 1709 | 1
Prop | Templates.York RTU | Unit Model Number | 1675 | 3 | 7002 | TRUE | TRUE | FALSE | 7 | String | [17 empty] | 40 |  |  |  |  | Attr | York RTU | 1 | Unit Model Number | EM Variable: RTUxxxxx |  | FALSE |  |  |  | CSV:29805 |  |  |  | Value |  |  | Views.Summary.Unit | Unit Model Number | 1675 | 3 |  | Views.Summary.Unit | Model# | 1709 | 2
Prop | Templates.York RTU | Unit Model Number | 1675 | 3 | 7002 | TRUE | TRUE | FALSE | 7 | String | [17 empty] | 40 |  |  |  |  | Attr | York RTU | 1 | Unit Model Number | EM Variable: RTUxxxxx |  | FALSE |  |  |  | CSV:29805 |  |  |  | Value |  |  | Views.Clone.Full Clone | Unit Model Number | 1675 | 3 |  |  | Model# | 1709 | 2
Prop | Templates.York RTU | Unit Serial Number | 1675 | 4 | 7003 | TRUE | TRUE | FALSE | 7 | String | [17 empty] | 40 |  |  |  |  | Attr | York RTU | 1 | Unit Serial Number | 8-1/Provision Manager | Serial Number | FALSE |  |  |  | CSV:29806 |  |  |  | Value |  |  | Views.Summary.Unit | Unit Serial Number | 1675 | 4 |  | Views.Summary.Unit | Serial# | 1709 | 3
Prop | Templates.York RTU | Unit Serial Number | 1675 | 4 | 7003 | TRUE | TRUE | FALSE | 7 | String | [17 empty] | 40 |  |  |  |  | Attr | York RTU | 1 | Unit Serial Number | 8-1/Provision Manager | Serial Number | FALSE |  |  |  | CSV:29806 |  |  |  | Value |  |  | Views.Clone.Full Clone | Unit Serial Number | 1675 | 4 |  |  | Serial# | 1709 | 3
Prop | Templates.York RTU | Firmware Version | 1675 | 5 | 7004 | TRUE | FALSE | FALSE | 7 | String | [17 empty] | 30 | Firmware Version |  |  |  | Attr | York RTU | 1 | Firmware Version | 8-1/Provision Manager | Package Version | FALSE |  |  |  | CSV:29807 |  |  |  | Value |  |  | Views.Controller.Firmware.UCB | Firmware Version | 1675 | 5 |  | Views.Controller.Firm.UCB | FirmVer | 1709 | 4
Prop | Templates.York RTU | Firmware Version | 1675 | 5 | 7004 | TRUE | FALSE | FALSE | 7 | String | [17 empty] | 30 | Firmware Version |  |  |  | Attr | York RTU | 1 | Firmware Version | 8-1/Provision Manager | Package Version | FALSE |  |  |  | CSV:29807 |  |  |  | Value |  |  | Views.Controller.Controller Info | Firmware Version | 1675 | 5 |  | Views.Controller.Controller Info | Firmware Version | 1675 | 5
Prop | Templates.York RTU | Firmware Status | 1675 | 146 | 7005 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | PMO Firmware Versions Status | 1727 | [7 empty] | PMO Firmware Versions Status | 1727 | [6 empty] | 1727 | 0 = Firmware Versions OK 1 = Firmware Versions Do Not Match the Package |  | Attr | York RTU | 1 | Firmware Status | 8-1/Provision Manager | System Package Mismatch Information | FALSE | [7 empty] | Value |  |  | Views.Controller.Firmware.UCB | Firmware Status | 1675 | 146 |  | Views.Controller.Firm.UCB | Firm-S | 1709 | 5
Prop | Templates.York RTU | Firmware Status | 1675 | 146 | 7005 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | PMO Firmware Versions Status | 1727 | [7 empty] | PMO Firmware Versions Status | 1727 | [6 empty] | 1727 | 0 = Firmware Versions OK 1 = Firmware Versions Do Not Match the Package |  | Attr | York RTU | 1 | Firmware Status | 8-1/Provision Manager | System Package Mismatch Information | FALSE | [7 empty] | Value |  |  | Views.Controller.Controller Info | Firmware Status | 1675 | 146 |  | Views.Controller.Controller Info | Firmware Status | 1675 | 146
Prop | Templates.York RTU | Heating Control Type | 1675 | 107 | 7006 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Heat Cool Type | 1608 | Off | [6 empty] | Heat Cool Type | 1608 | [5 empty] | Heating Control Type | 1608 | 0 = Staged 1 = Proportional |  | Attr | York RTU | 1 | Heating Control Type | UCBapp.newUCB.Hydronic_Heating_Enable | Relinquish Default | TRUE |  |  |  | MV:29501 |  |  |  | Value |  |  | Views.Commissioning.Options | Heating Control Type | 1675 | 107 |  | Views.Commission.Options | Htg-Type | 1709 | 6
Prop | Templates.York RTU | Heating Control Type | 1675 | 107 | 7006 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Heat Cool Type | 1608 | Off | [6 empty] | Heat Cool Type | 1608 | [5 empty] | Heating Control Type | 1608 | 0 = Staged 1 = Proportional |  | Attr | York RTU | 1 | Heating Control Type | UCBapp.newUCB.Hydronic_Heating_Enable | Relinquish Default | TRUE |  |  |  | MV:29501 |  |  |  | Value |  |  | Views.Details.Heating.Setup | Heating Control Type | 1675 | 107 |  | Views.Details.Htg.Setup | Htg-Type | 1709 | 6
Prop | Templates.York RTU | Exhaust Type | 1675 | 147 | 7008 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | SE RTU Exhaust Setup | 1639 | None | [6 empty] | SE RTU Exhaust Setup | 1639 | [6 empty] | 1639 | 0 = None 1 = Non-Modulating 2 = Modulating Damper 3 = Variable Frequency Fan |  | Attr | York RTU | 1 | Exhaust Type | EconApp.Econ.Exhaust Setup | Relinquish Default | TRUE |  |  | York RTU.System Controllers.Econ Controller:Present Value <> Not Present | MV:29503 | HR:412 | ADI:129 |  | Value |  |  | Views.Commissioning.Options | Exhaust Type | 1675 | 147 |  | Views.Commission.Options | ExFType | 1709 | 8
Prop | Templates.York RTU | Exhaust Type | 1675 | 147 | 7008 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | SE RTU Exhaust Setup | 1639 | None | [6 empty] | SE RTU Exhaust Setup | 1639 | [6 empty] | 1639 | 0 = None 1 = Non-Modulating 2 = Modulating Damper 3 = Variable Frequency Fan |  | Attr | York RTU | 1 | Exhaust Type | EconApp.Econ.Exhaust Setup | Relinquish Default | TRUE |  |  | York RTU.System Controllers.Econ Controller:Present Value <> Not Present | MV:29503 | HR:412 | ADI:129 |  | Value |  |  | Views.Details.Power Exhaust.Setup | Exhaust Type | 1675 | 147 |  | Views.Details.PowerEx.Setup | ExFType | 1709 | 8
Prop | Templates.York RTU | UCB 24VAC Input | 1675 | 148 | 7009 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | V | 507:5 | N/A |  |  |  |  | 10ths | 0 | V | 507:5 | [9 empty] | Attr | York RTU | 1 | UCB 24VAC Input | UCBapp.newUCB.24VAC_VOLTS | Present Value | FALSE | [7 empty] | Value |  |  | Views.Status.Status | UCB 24VAC Input | 1675 | 148 |  | Views.Status.Status | UCB24VForOutp | 1709 | 9
Prop | Templates.York RTU | Cancel ASCD Timers | 1675 | 336 | 7010 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Off/On | 647 | No | [6 empty] | Off/On | 647 | [6 empty] | 647 | 0 = Off 1 = On |  | Attr | York RTU | 1 | Cancel ASCD Timers | UCBapp.newUCB.Clear_ASCD_Timers | Present Value | FALSE
Prop | Templates.York RTU | Reset Lockouts | 1675 | 337 | 7011 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Off/On | 647 | Off | [6 empty] | Off/On | 647 | [5 empty] | Reset Lockout | 647 | 0 = Off 1 = On |  | Attr | York RTU | 1 | Reset Lockouts | UCBapp.newUCB.SYS_RESET | Present Value | FALSE |  |  |  | MV:29826 | HR:80 | ADI:2 |  | Value |  |  | Views.Summary.Unit | Reset Lockouts | 1675 | 337 |  | Views.Summary.Unit | ResetLO | 1709 | 464
Prop | Templates.York RTU | Outputs Disabled Due to Low Input Voltage | 1675 | 338 | 7012 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Normal | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU | 1 | Outputs Disabled Due to Low Input Voltage | UCBapp.newUCB.Effective_Blackout_State | Present Value | FALSE
Prop | Templates.York RTU | Outputs Limited Due to Low Input Voltage | 1675 | 339 | 7013 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Normal | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU | 1 | Outputs Limited Due to Low Input Voltage | UCBapp.newUCB.Effective_Brownout_State | Present Value | FALSE
Prop | Templates.York RTU | Model Name | 1675 | 448 | 7014 | TRUE | FALSE | FALSE | 7 | String | [17 empty] | 30 |  |  |  |  | Attr | York RTU | 1 | Model Name | UCBapp | Model Name | FALSE | [7 empty] | Value |  |  | Views.Summary.Unit | Model Name | 1675 | 448 |  | Views.Summary.Unit | ModelName | 1709 | 583
Prop | Templates.York RTU | Model Name | 1675 | 448 | 7014 | TRUE | FALSE | FALSE | 7 | String | [17 empty] | 30 |  |  |  |  | Attr | York RTU | 1 | Model Name | UCBapp | Model Name | FALSE | [7 empty] | Value |  |  | Views.Clone.Full Clone | Model Name | 1675 | 448 |  |  | ModelName | 1709 | 583
Prop | Templates.York RTU | CCS Online | 1675 | 477 | 7015 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | No | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU | 1 | CCS Online | UCBapp.newUCB.CCS | Present Value | TRUE
Prop | Templates.York RTU | Rooftop Controller Type | 1675 | 466 | 7017 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | LCCS Controller Type | 1244 | Constant_Volume | [6 empty] | LCCS Controller Type | 1244 | [6 empty] | 1244 | 0 = Changeover Bypass 1 = VAV 2 = Constant Volume 3 = TEC |  | Attr | York RTU | 1 | Rooftop Controller Type | UCBapp.newUCB.Rooftop_Controller_Type | Relinquish Default | TRUE | [7 empty] | Value |  |  | Views.Controller.Description | Rooftop Controller Type | 1675 | 466 |  | Views.Controller.Descrip | CntrlType | 1709 | 639
Prop | Templates.York RTU | Rooftop Controller Type | 1675 | 466 | 7017 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | LCCS Controller Type | 1244 | Constant_Volume | [6 empty] | LCCS Controller Type | 1244 | [6 empty] | 1244 | 0 = Changeover Bypass 1 = VAV 2 = Constant Volume 3 = TEC |  | Attr | York RTU | 1 | Rooftop Controller Type | UCBapp.newUCB.Rooftop_Controller_Type | Relinquish Default | TRUE | [7 empty] | Value |  |  | Views.Details.Verasys | Rooftop Controller Type | 1675 | 466 |  | Views.Details.Verasys | CntrlType | 1709 | 639
Prop | Templates.York RTU | Rooftop Equipment Type | 1675 | 467 | 7018 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | LCCS Equipment Type | 1368 | RTU | [6 empty] | LCCS Equipment Type | 1368 | [6 empty] | 1368 | 0 = Unknown 1 = RTU 2 = Split 3 = HeatPump |  | Attr | York RTU | 1 | Rooftop Equipment Type | UCBapp.newUCB.Rooftop_Equipment_Type | Relinquish Default | FALSE | [7 empty] | Value |  |  | Views.Controller.Description | Rooftop Equipment Type | 1675 | 467 |  | Views.Controller.Descrip | EquipType | 1709 | 640
Prop | Templates.York RTU | Unit Enable | 1675 | 462 | 7019 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Shutdown/Enable | 349 | Enable | [6 empty] | Shutdown/Enable | 349 | [5 empty] | Shutdown Command ; Unit Enable | 349 | 0 = Shutdown 1 = Enable |  | Attr | York RTU | 1 | Unit Enable | UCBapp.newUCB.UNITEN_MODE | Relinquish Default | FALSE |  |  |  | MV:29896 | HR:411 | ADI:128 |  | Value |  |  | Views.Summary.Unit | Unit Enable | 1675 | 462 |  | Views.Summary.Unit | UnitEn | 1709 | 641
Prop | Templates.York RTU | SZ VAV Enabled | 1675 | 491 | 7020 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Off/On | 647 | Off | [6 empty] | Off/On | 647 | [6 empty] | 647 | 0 = Off 1 = On |  | Attr | York RTU | 1 | SZ VAV Enabled | UCBapp.newUCB.Single_Zone_VAV_Enabled | Relinquish Default | TRUE |  |  |  | MV:29908 | IR:399 | ADI:118 |  | Value |  |  | Views.Commissioning.Options | SZ VAV Enabled | 1675 | 491 |  | Views.Commission.Options | SZVAVEn | 1709 | 623
Prop | Templates.York RTU | SZ VAV Enabled | 1675 | 491 | 7020 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Off/On | 647 | Off | [6 empty] | Off/On | 647 | [6 empty] | 647 | 0 = Off 1 = On |  | Attr | York RTU | 1 | SZ VAV Enabled | UCBapp.newUCB.Single_Zone_VAV_Enabled | Relinquish Default | TRUE |  |  |  | MV:29908 | IR:399 | ADI:118 |  | Value |  |  | Views.Details.Single Zone VAV.Setup | SZ VAV Enabled | 1675 | 491 |  | Views.Details.SZ VAV.Setup | SZVAVEn | 1709 | 623
Prop | Templates.York RTU | SZ VAV Enabled | 1675 | 491 | 7020 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Off/On | 647 | Off | [6 empty] | Off/On | 647 | [6 empty] | 647 | 0 = Off 1 = On |  | Attr | York RTU | 1 | SZ VAV Enabled | UCBapp.newUCB.Single_Zone_VAV_Enabled | Relinquish Default | TRUE |  |  |  | MV:29908 | IR:399 | ADI:118 |  | Value |  |  | Views.Clone.Partial Clone 1 | SZ VAV Enabled | 1675 | 491 |  |  | SZVAVEn | 1709 | 623
Prop | Templates.York RTU | Hardware Reset | 1675 | 499 | 7021 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Off | [6 empty] | No/Yes | 854 | [5 empty] | Hardware Reset | 854 | 0 = No 1 = Yes |  | Attr | York RTU | 1 | Hardware Reset | UCBapp.newUCB.Hardware_Reset | Present Value | FALSE |  |  |  | MV:29909 | HR:126 | ADI:109 |  | Value |  |  | Views.Summary.Unit | Hardware Reset | 1675 | 499 |  | Views.Summary.Unit | HdwrReset | 1709 | 631
Prop | Templates.York RTU | Software Version | 1675 | 742 | 7022 | TRUE | TRUE | FALSE | 18 | UnsignedInteger | 1s | 6 |  | 507:95 |  | 0 | 100000 |  |  | 1s | 0 |  | 507:95 | 0 | 100000 |  |  |  | Application Version |  |  |  | Attr | York RTU | 1 | Software Version | EM Variable: 12292 |  | FALSE
Prop | Templates.York RTU | Event 1 Value | 1675 | 825 | 7023 | TRUE | FALSE | FALSE | 18 | UnsignedInteger | 1s | 6 |  | 507:95 | [5 empty] | 1s | 0 |  | 507:95 | [9 empty] | Attr | York RTU | 1 | Event 1 Value | 8-1/Events List | Event 1 Value | FALSE |  |  |  | AV:29938 | IR:268
Prop | Templates.York RTU | Event 2 Value | 1675 | 827 | 7024 | TRUE | FALSE | FALSE | 18 | UnsignedInteger | 1s | 6 |  | 507:95 | [5 empty] | 1s | 0 |  | 507:95 | [9 empty] | Attr | York RTU | 1 | Event 2 Value | 8-1/Events List | Event 2 Value | FALSE |  |  |  | AV:29940 | IR:269
Prop | Templates.York RTU | Event 3 Value | 1675 | 829 | 7025 | TRUE | FALSE | FALSE | 18 | UnsignedInteger | 1s | 6 |  | 507:95 | [5 empty] | 1s | 0 |  | 507:95 | [9 empty] | Attr | York RTU | 1 | Event 3 Value | 8-1/Events List | Event 3 Value | FALSE |  |  |  | AV:29942 | IR:276
Prop | Templates.York RTU | Event 4 Value | 1675 | 831 | 7026 | TRUE | FALSE | FALSE | 18 | UnsignedInteger | 1s | 6 |  | 507:95 | [5 empty] | 1s | 0 |  | 507:95 | [9 empty] | Attr | York RTU | 1 | Event 4 Value | 8-1/Events List | Event 4 Value | FALSE |  |  |  | AV:29944 | IR:277
Prop | Templates.York RTU | Event 5 Value | 1675 | 833 | 7027 | TRUE | FALSE | FALSE | 18 | UnsignedInteger | 1s | 6 |  | 507:95 | [5 empty] | 1s | 0 |  | 507:95 | [9 empty] | Attr | York RTU | 1 | Event 5 Value | 8-1/Events List | Event 5 Value | FALSE |  |  |  | AV:29946 | IR:278
Prop | Templates.York RTU | Event 1 Set | 1675 | 824 | 7028 | TRUE | FALSE | FALSE | 18 | UnsignedInteger | 1s | 6 |  | 507:95 | [5 empty] | 1s | 0 |  | 507:95 | [9 empty] | Attr | York RTU | 1 | Event 1 Set | 8-1/Events List | Event 1 Set | FALSE |  |  |  | AV:29939 | IR:394
Prop | Templates.York RTU | Event 2 Set | 1675 | 826 | 7029 | TRUE | FALSE | FALSE | 18 | UnsignedInteger | 1s | 6 |  | 507:95 | [5 empty] | 1s | 0 |  | 507:95 | [9 empty] | Attr | York RTU | 1 | Event 2 Set | 8-1/Events List | Event 2 Set | FALSE |  |  |  | AV:29941 | IR:395
Prop | Templates.York RTU | Event 3 Set | 1675 | 828 | 7030 | TRUE | FALSE | FALSE | 18 | UnsignedInteger | 1s | 6 |  | 507:95 | [5 empty] | 1s | 0 |  | 507:95 | [9 empty] | Attr | York RTU | 1 | Event 3 Set | 8-1/Events List | Event 3 Set | FALSE |  |  |  | AV:29943 | IR:396
Prop | Templates.York RTU | Event 4 Set | 1675 | 830 | 7031 | TRUE | FALSE | FALSE | 18 | UnsignedInteger | 1s | 6 |  | 507:95 | [5 empty] | 1s | 0 |  | 507:95 | [9 empty] | Attr | York RTU | 1 | Event 4 Set | 8-1/Events List | Event 4 Set | FALSE |  |  |  | AV:29945 | IR:397
Prop | Templates.York RTU | Event 5 Set | 1675 | 832 | 7032 | TRUE | FALSE | FALSE | 18 | UnsignedInteger | 1s | 6 |  | 507:95 | [5 empty] | 1s | 0 |  | 507:95 | [9 empty] | Attr | York RTU | 1 | Event 5 Set | 8-1/Events List | Event 5 Set | FALSE |  |  |  | AV:29947 | IR:398
Prop | Templates.York RTU | HVAC Space | 1675 | 1319 | 7036 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | [7 empty] | No/Yes | 854 | [5 empty] | Circle of Comfort ; HVAC Space | 854 | 0 = No 1 = Yes |  | Attr | York RTU | 1 | HVAC Space | EM Variable: 1 |  | FALSE
Prop | Templates.York RTU | High Alarm Text | 1675 | 1519 | 7037 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | SE Event Active Critical Codes | 1716 | [7 empty] | SE Event Active Critical Codes | 1716 | [6 empty] | 1716 | 0 = None 1 = Event Generator Configuration Error 2 = Calibration Error 100 = Parameters Not Configured, Use Default ... |  | Attr | York RTU | 1 | High Alarm Text | 8-1/MVCriticalActiveEvent | Present Value | FALSE |  |  |  |  | IR:834
Prop | Templates.York RTU | Low Alarm Text | 1675 | 1520 | 7038 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | SE Event Inactive Critical Codes | 1719 | [7 empty] | SE Event Inactive Critical Codes | 1719 | [6 empty] | 1719 | 0 = None 1 = Event Generator Configuration Error 2 = Calibration Error 100 = Parameters Not Configured, Use Default ... |  | Attr | York RTU | 1 | Low Alarm Text | 8-1/MVCriticalInactiveEvent | Present Value | FALSE |  |  |  |  | IR:835
Prop | Templates.York RTU | High Alarm Text | 1675 | 1519 | 7039 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | SE Event Active Service Priority Codes | 1717 | [7 empty] | SE Event Active Service Priority Codes | 1717 | [6 empty] | 1717 | 0 = None 1 = Firmware versions do not match package 100 = FDD Firmware Failure 101 = No Dehum Due to Space Humidity ... |  | Attr | York RTU | 1 | High Alarm Text | 8-1/MVServicePriorityActiveEvent | Present Value | FALSE |  |  |  |  | IR:836
Prop | Templates.York RTU | Low Alarm Text | 1675 | 1520 | 7040 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | SE Event Inactive Service Priority Codes | 1720 | [7 empty] | SE Event Inactive Service Priority Codes | 1720 | [6 empty] | 1720 | 0 = None 1 = Firmware versions do not match package 100 = FDD Firmware Failure 101 = No Dehum Due to Space Humidity ... |  | Attr | York RTU | 1 | Low Alarm Text | 8-1/MVServicePriorityInactiveEvent | Present Value | FALSE |  |  |  |  | IR:837
Prop | Templates.York RTU | High Alarm Text | 1675 | 1519 | 7041 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | SE Event Active Service Codes | 1718 | [7 empty] | SE Event Active Service Codes | 1718 | [6 empty] | 1718 | 0 = None 1 = Reboot 100 = Econ Not Economizing When It Should 101 = Econ Economizing When It Should Not ... |  | Attr | York RTU | 1 | High Alarm Text | 8-1/MVServiceActiveEvent | Present Value | FALSE |  |  |  |  | IR:838
Prop | Templates.York RTU | Low Alarm Text | 1675 | 1520 | 7042 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | SE Event Inactive Service Codes | 1721 | [7 empty] | SE Event Inactive Service Codes | 1721 | [6 empty] | 1721 | 0 = None 1 = Reboot 100 = Econ Not Economizing When It Should 101 = Econ Economizing When It Should Not ... |  | Attr | York RTU | 1 | Low Alarm Text | 8-1/MVServiceInactiveEvent | Present Value | FALSE |  |  |  |  | IR:839
Prop | Templates.York RTU | Unique Equipment Identifier | 1675 | 1567 | 7043 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | SE RTU Equipment Configuration | 3356 | Standard | [6 empty] | SE RTU Equipment Configuration | 3356 | [6 empty] | 3356 | 0 = Standard 1 = Tandem Cir1 With 2 Stage Cir2 2 = 2 Stage Cir1 With 2 Stage Cir2 3 = 2 Stage Cir1 With Single Cir2 ... |  | Attr | York RTU | 1 | Unique Equipment Identifier | UCBapp.newUCB.Equipment_Configuration | Relinquish Default | FALSE | [7 empty] | Value |  |  | Views.Commissioning.Quick Start | Unique Equipment Identifier | 1675 | 1567 |  | Views.Commission.Quick Start | Unique Equipment Identifier | 1675 | 1567
Prop | Templates.York RTU | Unique Equipment Identifier | 1675 | 1567 | 7043 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | SE RTU Equipment Configuration | 3356 | Standard | [6 empty] | SE RTU Equipment Configuration | 3356 | [6 empty] | 3356 | 0 = Standard 1 = Tandem Cir1 With 2 Stage Cir2 2 = 2 Stage Cir1 With 2 Stage Cir2 3 = 2 Stage Cir1 With Single Cir2 ... |  | Attr | York RTU | 1 | Unique Equipment Identifier | UCBapp.newUCB.Equipment_Configuration | Relinquish Default | FALSE | [7 empty] | Value |  |  | Views.Commissioning.Standard | Unique Equipment Identifier | 1675 | 1567 |  | Views.Commission.Standard | Unique Equipment Identifier | 1675 | 1567
Prop | Templates.York RTU | Serial Flash Size | 1675 | 1680 | 7044 | TRUE | FALSE | FALSE | 2 | UnsignedLong | 1s | 6 |  | 507:95 | [5 empty] | 1s | 0 |  | 507:95 | [9 empty] | Attr | York RTU | 1 | Serial Flash Size | UCBapp | Total Serial Flash Size | FALSE | [7 empty] | Value |  |  | Views.Controller.Firmware.UCB | Serial Flash Size | 1675 | 1680 |  | Views.Controller.Firm.UCB | SerialFlashSize | 1709 | 738
Prop | Templates.York RTU | Unique Equipment Identifier | 1675 | 1567 | 7045 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 |  | 507:95 | 0 |  |  |  |  | 1s | 0 |  | 507:95 | [8 empty] | read only version | Attr | York RTU | 1 | Unique Equipment Identifier | UCBapp.newUCB.Equip_Config_AV_Src | Present Value | TRUE | [6 empty] | Effective Equipment Configuration
Prop | Templates.York RTU | Neutral Air ModHGR Enable | 1714 | 281 | 7046 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Disable/Enable | 658 | Disable | [6 empty] | Disable/Enable | 658 | [6 empty] | 658 | 0 = Disable 1 = Enable |  | Attr | York RTU | 1 | Neutral Air ModHGR Enable | UCBapp.newUCB.Neutral_Air_ModHGR_Enable | Relinquish Default | TRUE
Prop | Templates.York RTU | Dual Fuel HP Enable | 1714 | 283 | 7047 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Disable/Enable | 658 | Disable | [6 empty] | Disable/Enable | 658 | [6 empty] | 658 | 0 = Disable 1 = Enable |  | Attr | York RTU | 1 | Dual Fuel HP Enable | UCBapp.newUCB.Dual_Fuel_HP_Enable | Relinquish Default | TRUE
Tmpl | Templates.Thermostat Control | [31 empty] | Model | York RTU.Thermostat Control | 2
Prop | Templates.Thermostat Control | Y1 - Thermostat | 1675 | 150 | 7000 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [5 empty] | Y1 | 647 | 0 = Off 1 = On |  | Attr | York RTU.Thermostat Control | 2 | Y1 - Thermostat | UCBapp.newUCB.Y1_S | Present Value | FALSE |  |  |  | MV:29504 | IR:281 | BI:1 |  | Value |  |  | Views.Status.Thermostat | Y1 - Thermostat | 1675 | 150 |  | Views.Status.Thermostat | Y1-Tstat | 1709 | 11
Prop | Templates.Thermostat Control | Y1 - Thermostat | 1675 | 150 | 7000 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [5 empty] | Y1 | 647 | 0 = Off 1 = On |  | Attr | York RTU.Thermostat Control | 2 | Y1 - Thermostat | UCBapp.newUCB.Y1_S | Present Value | FALSE |  |  |  | MV:29504 | IR:281 | BI:1 |  | Value |  |  | Views.Details.Cooling.Service.Unit | Y1 - Thermostat | 1675 | 150 |  | Views.Details.Clg.Service.Unit | Y1-Tstat | 1709 | 11
Prop | Templates.Thermostat Control | Y2 - Thermostat | 1675 | 151 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [5 empty] | Y2 | 647 | 0 = Off 1 = On |  | Attr | York RTU.Thermostat Control | 2 | Y2 - Thermostat | UCBapp.newUCB.Y2_S | Present Value | FALSE |  |  | York RTU.Cooling Control.Number of Cooling Stages Installed:Present Value > 1 | MV:29505 | IR:282 | BI:2 |  | Value |  |  | Views.Status.Thermostat | Y2 - Thermostat | 1675 | 151 |  | Views.Status.Thermostat | Y2-Tstat | 1709 | 12
Prop | Templates.Thermostat Control | Y2 - Thermostat | 1675 | 151 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [5 empty] | Y2 | 647 | 0 = Off 1 = On |  | Attr | York RTU.Thermostat Control | 2 | Y2 - Thermostat | UCBapp.newUCB.Y2_S | Present Value | FALSE |  |  | York RTU.Cooling Control.Number of Cooling Stages Installed:Present Value > 1 | MV:29505 | IR:282 | BI:2 |  | Value |  |  | Views.Details.Cooling.Service.Unit | Y2 - Thermostat | 1675 | 151 |  | Views.Details.Clg.Service.Unit | Y2-Tstat | 1709 | 12
Prop | Templates.Thermostat Control | Y3 - Thermostat | 1675 | 152 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [5 empty] | Y3 | 647 | 0 = Off 1 = On |  | Attr | York RTU.Thermostat Control | 2 | Y3 - Thermostat | FourStageApp.FourStage.Y3_S | Present Value | FALSE |  |  | York RTU.Cooling Control.Number of Cooling Stages Installed:Present Value > 2 | MV:29506 | IR:283 | BI:3 |  | Value |  |  | Views.Status.Thermostat | Y3 - Thermostat | 1675 | 152 |  | Views.Status.Thermostat | Y3-Tstat | 1709 | 13
Prop | Templates.Thermostat Control | Y3 - Thermostat | 1675 | 152 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [5 empty] | Y3 | 647 | 0 = Off 1 = On |  | Attr | York RTU.Thermostat Control | 2 | Y3 - Thermostat | FourStageApp.FourStage.Y3_S | Present Value | FALSE |  |  | York RTU.Cooling Control.Number of Cooling Stages Installed:Present Value > 2 | MV:29506 | IR:283 | BI:3 |  | Value |  |  | Views.Details.Cooling.Service.Unit | Y3 - Thermostat | 1675 | 152 |  | Views.Details.Clg.Service.Unit | Y3-Tstat | 1709 | 13
Prop | Templates.Thermostat Control | Y4 - Thermostat | 1675 | 153 | 7003 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [5 empty] | Y4 | 647 | 0 = Off 1 = On |  | Attr | York RTU.Thermostat Control | 2 | Y4 - Thermostat | FourStageApp.FourStage.Y4_S | Present Value | FALSE |  |  | York RTU.Cooling Control.Number of Cooling Stages Installed:Present Value > 3 | MV:29507 | IR:284 | BI:4 |  | Value |  |  | Views.Status.Thermostat | Y4 - Thermostat | 1675 | 153 |  | Views.Status.Thermostat | Y4-Tstat | 1709 | 14
Prop | Templates.Thermostat Control | Y4 - Thermostat | 1675 | 153 | 7003 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [5 empty] | Y4 | 647 | 0 = Off 1 = On |  | Attr | York RTU.Thermostat Control | 2 | Y4 - Thermostat | FourStageApp.FourStage.Y4_S | Present Value | FALSE |  |  | York RTU.Cooling Control.Number of Cooling Stages Installed:Present Value > 3 | MV:29507 | IR:284 | BI:4 |  | Value |  |  | Views.Details.Cooling.Service.Unit | Y4 - Thermostat | 1675 | 153 |  | Views.Details.Clg.Service.Unit | Y4-Tstat | 1709 | 14
Prop | Templates.Thermostat Control | W1 - Thermostat | 1675 | 154 | 7004 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [5 empty] | W1 | 647 | 0 = Off 1 = On |  | Attr | York RTU.Thermostat Control | 2 | W1 - Thermostat | UCBapp.newUCB.W1_S | Present Value | FALSE |  |  | York RTU.Heating Control.Staged Heat Control.Number of Heating Stages Installed:Present Value > 0 | MV:29508 | IR:285 | BI:5 |  | Value |  |  | Views.Status.Thermostat | W1 - Thermostat | 1675 | 154 |  | Views.Status.Thermostat | W1-Tstat | 1709 | 15
Prop | Templates.Thermostat Control | W1 - Thermostat | 1675 | 154 | 7004 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [5 empty] | W1 | 647 | 0 = Off 1 = On |  | Attr | York RTU.Thermostat Control | 2 | W1 - Thermostat | UCBapp.newUCB.W1_S | Present Value | FALSE |  |  | York RTU.Heating Control.Staged Heat Control.Number of Heating Stages Installed:Present Value > 0 | MV:29508 | IR:285 | BI:5 |  | Value |  |  | Views.Details.Heating.Service | W1 - Thermostat | 1675 | 154 |  | Views.Details.Htg.Service | W1-Tstat | 1709 | 15
Prop | Templates.Thermostat Control | W1 - Thermostat | 1675 | 154 | 7004 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [5 empty] | W1 | 647 | 0 = Off 1 = On |  | Attr | York RTU.Thermostat Control | 2 | W1 - Thermostat | UCBapp.newUCB.W1_S | Present Value | FALSE |  |  | York RTU.Heating Control.Staged Heat Control.Number of Heating Stages Installed:Present Value > 0 | MV:29508 | IR:285 | BI:5 |  | Value |  |  | Views.Details.Heating.Proportional.Service | W1 - Thermostat | 1675 | 154 |  | Views.Details.Htg.Prop.Service | W1-Tstat | 1709 | 15
Prop | Templates.Thermostat Control | W2 - Thermostat | 1675 | 155 | 7005 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [5 empty] | W2 | 647 | 0 = Off 1 = On |  | Attr | York RTU.Thermostat Control | 2 | W2 - Thermostat | UCBapp.newUCB.W2_S | Present Value | FALSE |  |  | York RTU.Heating Control.Staged Heat Control.Number of Heating Stages Installed:Present Value > 1 | MV:29509 | IR:286 | BI:6 |  | Value |  |  | Views.Status.Thermostat | W2 - Thermostat | 1675 | 155 |  | Views.Status.Thermostat | W2-Tstat | 1709 | 16
Prop | Templates.Thermostat Control | W2 - Thermostat | 1675 | 155 | 7005 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [5 empty] | W2 | 647 | 0 = Off 1 = On |  | Attr | York RTU.Thermostat Control | 2 | W2 - Thermostat | UCBapp.newUCB.W2_S | Present Value | FALSE |  |  | York RTU.Heating Control.Staged Heat Control.Number of Heating Stages Installed:Present Value > 1 | MV:29509 | IR:286 | BI:6 |  | Value |  |  | Views.Details.Heating.Service | W2 - Thermostat | 1675 | 155 |  | Views.Details.Htg.Service | W2-Tstat | 1709 | 16
Prop | Templates.Thermostat Control | W2 - Thermostat | 1675 | 155 | 7005 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [5 empty] | W2 | 647 | 0 = Off 1 = On |  | Attr | York RTU.Thermostat Control | 2 | W2 - Thermostat | UCBapp.newUCB.W2_S | Present Value | FALSE |  |  | York RTU.Heating Control.Staged Heat Control.Number of Heating Stages Installed:Present Value > 1 | MV:29509 | IR:286 | BI:6 |  | Value |  |  | Views.Details.Heating.Proportional.Service | W2 - Thermostat | 1675 | 155 |  | Views.Details.Htg.Prop.Service | W2-Tstat | 1709 | 16
Prop | Templates.Thermostat Control | W3 - Thermostat | 1675 | 156 | 7006 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [5 empty] | W3 | 647 | 0 = Off 1 = On |  | Attr | York RTU.Thermostat Control | 2 | W3 - Thermostat | FourStageApp.FourStage.W3_S | Present Value | FALSE |  |  | York RTU.Heating Control.Staged Heat Control.Number of Heating Stages Installed:Present Value > 2 | MV:29510 | IR:287 | BI:7 |  | Value |  |  | Views.Status.Thermostat | W3 - Thermostat | 1675 | 156 |  | Views.Status.Thermostat | W3-Tstat | 1709 | 17
Prop | Templates.Thermostat Control | W3 - Thermostat | 1675 | 156 | 7006 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [5 empty] | W3 | 647 | 0 = Off 1 = On |  | Attr | York RTU.Thermostat Control | 2 | W3 - Thermostat | FourStageApp.FourStage.W3_S | Present Value | FALSE |  |  | York RTU.Heating Control.Staged Heat Control.Number of Heating Stages Installed:Present Value > 2 | MV:29510 | IR:287 | BI:7 |  | Value |  |  | Views.Details.Heating.Service | W3 - Thermostat | 1675 | 156 |  | Views.Details.Htg.Service | W3-Tstat | 1709 | 17
Prop | Templates.Thermostat Control | G - Thermostat | 1675 | 157 | 7007 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | 0 | [6 empty] | Off/On | 647 | [6 empty] | 647 | 0 = Off 1 = On |  | Attr | York RTU.Thermostat Control | 2 | G - Thermostat | UCBapp.newUCB.G_S | Present Value | FALSE |  |  |  | MV:29511 | IR:288 | BI:8 |  | Value |  |  | Views.Status.Thermostat | G - Thermostat | 1675 | 157 |  | Views.Status.Thermostat | G-Tstat | 1709 | 18
Prop | Templates.Thermostat Control | G - Thermostat | 1675 | 157 | 7007 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | 0 | [6 empty] | Off/On | 647 | [6 empty] | 647 | 0 = Off 1 = On |  | Attr | York RTU.Thermostat Control | 2 | G - Thermostat | UCBapp.newUCB.G_S | Present Value | FALSE |  |  |  | MV:29511 | IR:288 | BI:8 |  | Value |  |  | Views.Details.Heating.Service | G - Thermostat | 1675 | 157 |  | Views.Details.Htg.Service | G-Tstat | 1709 | 18
Prop | Templates.Thermostat Control | G - Thermostat | 1675 | 157 | 7007 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | 0 | [6 empty] | Off/On | 647 | [6 empty] | 647 | 0 = Off 1 = On |  | Attr | York RTU.Thermostat Control | 2 | G - Thermostat | UCBapp.newUCB.G_S | Present Value | FALSE |  |  |  | MV:29511 | IR:288 | BI:8 |  | Value |  |  | Views.Details.Indoor Fan.Service | G - Thermostat | 1675 | 157 |  | Views.Details.Fan.Service | G-Tstat | 1709 | 18
Prop | Templates.Thermostat Control | X-OUT | 1675 | 159 | 7009 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | 55 | [6 empty] | Off/On | 647 | [6 empty] | 647 | 0 = Off 1 = On |  | Attr | York RTU.Thermostat Control | 2 | X-OUT | UCBapp.newUCB.X_C | Present Value | FALSE |  |  |  | MV:29513 | IR:289 | BO:1
Prop | Templates.Thermostat Control | Thermostat Only Control Enabled | 1675 | 160 | 7010 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Yes | [6 empty] | No/Yes | 854 | [5 empty] | Thermostat Only | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Thermostat Control | 2 | Thermostat Only Control Enabled | UCBapp.newUCB.Thermostat_Only | Relinquish Default | TRUE |  |  |  | MV:29514 | HR:413 | BI:42 |  | Value |  |  | Views.Commissioning.Standard | Thermostat Only Control Enabled | 1675 | 160 |  | Views.Commission.Standard | Tstat-Only | 1709 | 21
Prop | Templates.Thermostat Control | Thermostat Only Control Enabled | 1675 | 160 | 7010 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Yes | [6 empty] | No/Yes | 854 | [5 empty] | Thermostat Only | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Thermostat Control | 2 | Thermostat Only Control Enabled | UCBapp.newUCB.Thermostat_Only | Relinquish Default | TRUE |  |  |  | MV:29514 | HR:413 | BI:42 |  | Value |  |  | Views.Commissioning.Quick Start | Thermostat Only Control Enabled | 1675 | 160 |  | Views.Commission.Quick Start | Tstat-Only | 1709 | 21
Prop | Templates.Thermostat Control | Thermostat Only Control Enabled | 1675 | 160 | 7010 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Yes | [6 empty] | No/Yes | 854 | [5 empty] | Thermostat Only | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Thermostat Control | 2 | Thermostat Only Control Enabled | UCBapp.newUCB.Thermostat_Only | Relinquish Default | TRUE |  |  |  | MV:29514 | HR:413 | BI:42 |  | Value |  |  | Views.Clone.Partial Clone 1 | Thermostat Only Control Enabled | 1675 | 160 |  |  | Tstat-Only | 1709 | 21
Prop | Templates.Thermostat Control | Local Occupancy Input - Thermostat | 1675 | 158 | 7008 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | On/Off | 1686 | Occupied | [6 empty] | On/Off | 1686 | [6 empty] | 1686 | 0 = On 1 = Off |  | Attr | York RTU.Thermostat Control | 2 | Local Occupancy Input - Thermostat | UCBapp.newUCB.OCC_S | Present Value | FALSE |  |  |  | MV:29512 |  |  |  | Value |  |  | Views.Status.Thermostat | Local Occupancy Input - Thermostat | 1675 | 158 |  | Views.Status.Thermostat | Occ-Tstat | 1709 | 19
Tmpl | Templates.Fan Control | [31 empty] | Model | York RTU.Fan Control | 3
Prop | Templates.Fan Control | Fan Status | 1675 | 168 | 7000 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | SE RTU Fan Status | 1739 | Off_Idle | [6 empty] | SE RTU Fan Status | 1739 | [5 empty] | Fan Status | 1739 | 0 = Off-Idle 1 = On-Purge 2 = On-Gas Valve or Limit Fault 3 = On-Defrost ... |  | Attr | York RTU.Fan Control | 3 | Fan Status | UCBapp.newUCB.Fan_Status | Present Value | FALSE |  |  |  | MV:29550 | IR:302 | ADI:23 |  | Value |  |  | Views.Status.Status | Fan Status | 1675 | 168 |  | Views.Status.Status | Fan-S | 1709 | 66
Prop | Templates.Fan Control | Fan Status | 1675 | 168 | 7000 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | SE RTU Fan Status | 1739 | Off_Idle | [6 empty] | SE RTU Fan Status | 1739 | [5 empty] | Fan Status | 1739 | 0 = Off-Idle 1 = On-Purge 2 = On-Gas Valve or Limit Fault 3 = On-Defrost ... |  | Attr | York RTU.Fan Control | 3 | Fan Status | UCBapp.newUCB.Fan_Status | Present Value | FALSE |  |  |  | MV:29550 | IR:302 | ADI:23 |  | Value |  |  | Views.Details.Indoor Fan.Service | Fan Status | 1675 | 168 |  | Views.Details.Fan.Service | Fan-S | 1709 | 66
Prop | Templates.Fan Control | Fan % Command | 1675 | 169 | 7001 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | N/A |  |  |  |  | 1s | 0 | % | 507:98 | [5 empty] | Fan Command |  |  |  | Attr | York RTU.Fan Control | 3 | Fan % Command | UCBapp.newUCB.SFPCT_O | Present Value | FALSE |  |  | York RTU.Fan Control.Fan Control Type:Present Value <> Single Speed | AV:29551 | IR:157 | AO:1 |  | Value |  |  | Views.Details.FanVFD.Service | Fan % Command | 1675 | 169 |  | Views.Details.FanVFD.Service | FanVFD | 1709 | 67
Prop | Templates.Fan Control | Fan % Command | 1675 | 169 | 7001 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | N/A |  |  |  |  | 1s | 0 | % | 507:98 | [5 empty] | Fan Command |  |  |  | Attr | York RTU.Fan Control | 3 | Fan % Command | UCBapp.newUCB.SFPCT_O | Present Value | FALSE |  |  | York RTU.Fan Control.Fan Control Type:Present Value <> Single Speed | AV:29551 | IR:157 | AO:1 |  | Value |  |  | Views.Details.Single Zone VAV.Service | Fan % Command | 1675 | 169 |  | Views.Details.SZ VAV.Service | FanVFD | 1709 | 67
Prop | Templates.Fan Control | Fan VFD Fault | 1675 | 170 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | N/A | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Fan Control | 3 | Fan VFD Fault | UCBapp.newUCB.SFANVFDFAULT_S | Present Value | FALSE |  |  | York RTU.Fan Control.Fan Control Type:Present Value <> Single Speed | MV:29552 | IR:303 | BI:10 |  | Value |  |  | Views.Details.Indoor Fan.Service | Fan VFD Fault | 1675 | 170 |  | Views.Details.Fan.Service | FanVFDFlt | 1709 | 68
Prop | Templates.Fan Control | Fan Overload | 1675 | 171 | 7003 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Fan Control | 3 | Fan Overload | UCBapp.newUCB.Fan_Overload | Present Value | FALSE |  |  |  | MV:29553 | IR:304 | BI:11 |  | Value |  |  | Views.Details.Indoor Fan.Service | Fan Overload | 1675 | 171 |  | Views.Details.Fan.Service | FanOvrload | 1709 | 69
Prop | Templates.Fan Control | Fan Accumulated Runtime | 1675 | 172 | 7004 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | hours | 507:71 |  | 0 | 10000 |  |  | 1s | 0 | hours | 507:71 | 0 | 10000 | [7 empty] | Attr | York RTU.Fan Control | 3 | Fan Accumulated Runtime | 8-1/UCBApp.Supply_Fan_Runtime_Totalization | Present Value | FALSE |  |  |  | AV:29554 | IR:9 | ADF:30 |  | Value |  |  | Views.Details.Indoor Fan.Service | Fan Accumulated Runtime | 1675 | 172 |  | Views.Details.Fan.Service | Fan-RT | 1709 | 70
Prop | Templates.Fan Control | Fan Accumulated Runtime | 1675 | 172 | 7004 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | hours | 507:71 |  | 0 | 10000 |  |  | 1s | 0 | hours | 507:71 | 0 | 10000 | [7 empty] | Attr | York RTU.Fan Control | 3 | Fan Accumulated Runtime | 8-1/UCBApp.Supply_Fan_Runtime_Totalization | Present Value | FALSE |  |  |  | AV:29554 | IR:9 | ADF:30 |  | Value |  |  | Views.Clone.Full Clone | Fan Accumulated Runtime | 1675 | 172 |  |  | Fan-RT | 1709 | 70
Prop | Templates.Fan Control | Fan Control Type | 1675 | 173 | 7005 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | SE RTU Fan Control Type | 1619 | Single_Speed | [6 empty] | SE RTU Fan Control Type | 1619 | [5 empty] | Fan Control Type ; Use Alternate Cooling Setpoint ; Use Alternate Heating Setpoint | 1619 | 0 = Single Speed 1 = Not Used 2 = Fixed Variable 3 = Variable Speed |  | Attr | York RTU.Fan Control | 3 | Fan Control Type | UCBapp.newUCB.SF_TYPE | Relinquish Default | TRUE |  |  |  | MV:29555 | HR:400 | ADI:119 |  | Value |  |  | Views.Commissioning.Options | Fan Control Type | 1675 | 173 |  | Views.Commission.Options | FanCtl-Type | 1709 | 71
Prop | Templates.Fan Control | Fan Control Type | 1675 | 173 | 7005 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | SE RTU Fan Control Type | 1619 | Single_Speed | [6 empty] | SE RTU Fan Control Type | 1619 | [5 empty] | Fan Control Type ; Use Alternate Cooling Setpoint ; Use Alternate Heating Setpoint | 1619 | 0 = Single Speed 1 = Not Used 2 = Fixed Variable 3 = Variable Speed |  | Attr | York RTU.Fan Control | 3 | Fan Control Type | UCBapp.newUCB.SF_TYPE | Relinquish Default | TRUE |  |  |  | MV:29555 | HR:400 | ADI:119 |  | Value |  |  | Views.Details.Indoor Fan.Setup | Fan Control Type | 1675 | 173 |  | Views.Details.Fan.Setup | FanCtl-Type | 1709 | 71
Prop | Templates.Fan Control | Fan Control Type | 1675 | 173 | 7005 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | SE RTU Fan Control Type | 1619 | Single_Speed | [6 empty] | SE RTU Fan Control Type | 1619 | [5 empty] | Fan Control Type ; Use Alternate Cooling Setpoint ; Use Alternate Heating Setpoint | 1619 | 0 = Single Speed 1 = Not Used 2 = Fixed Variable 3 = Variable Speed |  | Attr | York RTU.Fan Control | 3 | Fan Control Type | UCBapp.newUCB.SF_TYPE | Relinquish Default | TRUE |  |  |  | MV:29555 | HR:400 | ADI:119 |  | Value |  |  | Views.Details.FanVFD.Setup | Fan Control Type | 1675 | 173 |  | Views.Details.FanVFD.Setup | FanCtl-Type | 1709 | 71
Prop | Templates.Fan Control | Fan Control Type | 1675 | 173 | 7005 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | SE RTU Fan Control Type | 1619 | Single_Speed | [6 empty] | SE RTU Fan Control Type | 1619 | [5 empty] | Fan Control Type ; Use Alternate Cooling Setpoint ; Use Alternate Heating Setpoint | 1619 | 0 = Single Speed 1 = Not Used 2 = Fixed Variable 3 = Variable Speed |  | Attr | York RTU.Fan Control | 3 | Fan Control Type | UCBapp.newUCB.SF_TYPE | Relinquish Default | TRUE |  |  |  | MV:29555 | HR:400 | ADI:119 |  | Value |  |  | Views.Details.ERV | Fan Control Type | 1675 | 173 |  | Views.Details.ERV | FanCtl-Type | 1709 | 71
Prop | Templates.Fan Control | Fan Control Type | 1675 | 173 | 7005 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | SE RTU Fan Control Type | 1619 | Single_Speed | [6 empty] | SE RTU Fan Control Type | 1619 | [5 empty] | Fan Control Type ; Use Alternate Cooling Setpoint ; Use Alternate Heating Setpoint | 1619 | 0 = Single Speed 1 = Not Used 2 = Fixed Variable 3 = Variable Speed |  | Attr | York RTU.Fan Control | 3 | Fan Control Type | UCBapp.newUCB.SF_TYPE | Relinquish Default | TRUE |  |  |  | MV:29555 | HR:400 | ADI:119 |  | Value |  |  | Views.Commissioning.Quick Start | Fan Control Type | 1675 | 173 |  | Views.Commission.Quick Start | FanCtl-Type | 1709 | 71
Prop | Templates.Fan Control | Air Proving Switch Setup | 1675 | 174 | 7006 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Fan Setup | 1622 | None | [6 empty] | Fan Setup | 1622 | [6 empty] | 1622 | 0 = Constant Volume 1 = Variable Volume 2 = None |  | Attr | York RTU.Fan Control | 3 | Air Proving Switch Setup | UCBapp.newUCB.Fan_Setup | Relinquish Default | FALSE |  |  |  | MV:29556 | HR:414 | ADI:130 |  | Value |  |  | Views.Commissioning.Options | Air Proving Switch Setup | 1675 | 174 |  | Views.Commission.Options | APSSetup | 1709 | 72
Prop | Templates.Fan Control | Air Proving Switch Setup | 1675 | 174 | 7006 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Fan Setup | 1622 | None | [6 empty] | Fan Setup | 1622 | [6 empty] | 1622 | 0 = Constant Volume 1 = Variable Volume 2 = None |  | Attr | York RTU.Fan Control | 3 | Air Proving Switch Setup | UCBapp.newUCB.Fan_Setup | Relinquish Default | FALSE |  |  |  | MV:29556 | HR:414 | ADI:130 |  | Value |  |  | Views.Details.Indoor Fan.Setup | Air Proving Switch Setup | 1675 | 174 |  | Views.Details.Fan.Setup | APSSetup | 1709 | 72
Prop | Templates.Fan Control | Air Proving Switch | 1675 | 175 | 7007 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [6 empty] | 647 | 0 = Off 1 = On |  | Attr | York RTU.Fan Control | 3 | Air Proving Switch | UCBapp.newUCB.APSORHUM_S | Present Value | FALSE |  |  |  | MV:29557 | IR:305 | BI:12 |  | Value |  |  | Views.Details.Indoor Fan.Service | Air Proving Switch | 1675 | 175 |  | Views.Details.Fan.Service | APS | 1709 | 73
Prop | Templates.Fan Control | Fan On Delay for Cool | 1675 | 176 | 7008 | TRUE | TRUE | FALSE | 17 | SignedInteger | 1s | 6 | seconds | 507:73 | 0 | 0 | 30 |  |  | 1s | 0 | seconds | 507:73 | 0 | 30 | [7 empty] | Attr | York RTU.Fan Control | 3 | Fan On Delay for Cool | UCBapp.newUCB.Cool_Fan_On_Delay | Relinquish Default | FALSE |  |  |  | AV:29558 | HR:90 | ADI:24 |  | Value |  |  | Views.Details.Indoor Fan.Setup | Fan On Delay for Cool | 1675 | 176 |  | Views.Details.Fan.Setup | FanOnDlyCool | 1709 | 74
Prop | Templates.Fan Control | Fan Off Delay for Cool | 1675 | 177 | 7009 | TRUE | TRUE | FALSE | 17 | SignedInteger | 1s | 6 | seconds | 507:73 | 30 | 0 | 255 |  |  | 1s | 0 | seconds | 507:73 | 0 | 255 | [7 empty] | Attr | York RTU.Fan Control | 3 | Fan Off Delay for Cool | UCBapp.newUCB.Cool_Fan_Off_Delay | Relinquish Default | FALSE |  |  |  | AV:29559 | HR:415 | ADI:131 |  | Value |  |  | Views.Details.Indoor Fan.Setup | Fan Off Delay for Cool | 1675 | 177 |  | Views.Details.Fan.Setup | FanOffDlyCool | 1709 | 75
Prop | Templates.Fan Control | Fan On Delay for Heat | 1675 | 178 | 7010 | TRUE | TRUE | FALSE | 17 | SignedInteger | 1s | 6 | seconds | 507:73 | 30 | 0 | 30 |  |  | 1s | 0 | seconds | 507:73 | 0 | 30 | [7 empty] | Attr | York RTU.Fan Control | 3 | Fan On Delay for Heat | UCBapp.newUCB.Heat_Fan_On_Delay | Relinquish Default | FALSE |  |  | UCBapp.newUCB.Electric_Heat_Installed:Present Value = Inactive | AV:29560 | HR:416 | ADI:132 |  | Value |  |  | Views.Details.Indoor Fan.Setup | Fan On Delay for Heat | 1675 | 178 |  | Views.Details.Fan.Setup | FanOnDlyHeat | 1709 | 76
Prop | Templates.Fan Control | Fan Off Delay for Heat | 1675 | 179 | 7011 | TRUE | TRUE | FALSE | 17 | SignedInteger | 1s | 6 | seconds | 507:73 | 120 | 0 | 255 |  |  | 1s | 0 | seconds | 507:73 | 0 | 255 | [7 empty] | Attr | York RTU.Fan Control | 3 | Fan Off Delay for Heat | UCBapp.newUCB.Heat_Fan_Off_Delay | Relinquish Default | FALSE |  |  | York RTU.Heating Control.Staged Heat Control.Number of Heating Stages Installed:Present Value <> 0 | AV:29561 | HR:417 | ADI:133 |  | Value |  |  | Views.Details.Indoor Fan.Setup | Fan Off Delay for Heat | 1675 | 179 |  | Views.Details.Fan.Setup | FanOffDlyHeat | 1709 | 77
Prop | Templates.Fan Control | Dirty Filter Switch | 1675 | 180 | 7012 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | N/A | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Fan Control | 3 | Dirty Filter Switch | UCBapp.newUCB.DF_S | Present Value | FALSE |  |  | York RTU.Fan Control.Dirty Filter Switch Installed:Present Value = Yes | MV:29562 | IR:306 | BI:13 |  | Value |  |  | Views.Status.Status | Dirty Filter Switch | 1675 | 180 |  | Views.Status.Status | DFS | 1709 | 78
Prop | Templates.Fan Control | Dirty Filter Switch | 1675 | 180 | 7012 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | N/A | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Fan Control | 3 | Dirty Filter Switch | UCBapp.newUCB.DF_S | Present Value | FALSE |  |  | York RTU.Fan Control.Dirty Filter Switch Installed:Present Value = Yes | MV:29562 | IR:306 | BI:13 |  | Value |  |  | Views.Details.Indoor Fan.Setup | Dirty Filter Switch | 1675 | 180 |  | Views.Details.Fan.Setup | DFS | 1709 | 78
Prop | Templates.Fan Control | Fan Command | 1675 | 181 | 7013 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | Off | [6 empty] | Off/On | 647 | [5 empty] | Fan Output | 647 | 0 = Off 1 = On |  | Attr | York RTU.Fan Control | 3 | Fan Command | UCBapp.newUCB.SF_C | Present Value | FALSE |  |  |  | MV:29563 | IR:307 | BO:2 |  | Value |  |  | Views.Details.Indoor Fan.Service | Fan Command | 1675 | 181 |  | Views.Details.Fan.Service | Fan | 1709 | 79
Prop | Templates.Fan Control | Fan Command | 1675 | 181 | 7013 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | Off | [6 empty] | Off/On | 647 | [5 empty] | Fan Output | 647 | 0 = Off 1 = On |  | Attr | York RTU.Fan Control | 3 | Fan Command | UCBapp.newUCB.SF_C | Present Value | FALSE |  |  |  | MV:29563 | IR:307 | BO:2 |  | Value |  |  | Views.Details.ERV | Fan Command | 1675 | 181 |  | Views.Details.ERV | Fan | 1709 | 79
Prop | Templates.Fan Control | Supply Air Temperature | 1675 | 182 | 7014 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | N/A |  |  |  |  | 10ths | 0 | deg C | 507:62 | [5 empty] | Discharge Air Temperature |  |  |  | Attr | York RTU.Fan Control | 3 | Supply Air Temperature | UCBapp.newUCB.SA_T | Present Value | FALSE |  |  |  | AV:29564 | IR:158 | AI:3 |  | Value |  |  | Views.Summary.Sensors.Sensors | Supply Air Temperature | 1675 | 182 |  | Views.Summary.Sensors.Sensors | SAT | 1709 | 80
Prop | Templates.Fan Control | Supply Air Temperature | 1675 | 182 | 7014 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | N/A |  |  |  |  | 10ths | 0 | deg C | 507:62 | [5 empty] | Discharge Air Temperature |  |  |  | Attr | York RTU.Fan Control | 3 | Supply Air Temperature | UCBapp.newUCB.SA_T | Present Value | FALSE |  |  |  | AV:29564 | IR:158 | AI:3 |  | Value |  |  | Views.Details.Cooling.Service.Unit | Supply Air Temperature | 1675 | 182 |  | Views.Details.Clg.Service.Unit | SAT | 1709 | 80
Prop | Templates.Fan Control | Supply Air Temperature | 1675 | 182 | 7014 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | N/A |  |  |  |  | 10ths | 0 | deg C | 507:62 | [5 empty] | Discharge Air Temperature |  |  |  | Attr | York RTU.Fan Control | 3 | Supply Air Temperature | UCBapp.newUCB.SA_T | Present Value | FALSE |  |  |  | AV:29564 | IR:158 | AI:3 |  | Value |  |  | Views.Details.Heating.Proportional.Service | Supply Air Temperature | 1675 | 182 |  | Views.Details.Htg.Prop.Service | SAT | 1709 | 80
Prop | Templates.Fan Control | Supply Air Temperature | 1675 | 182 | 7014 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | N/A |  |  |  |  | 10ths | 0 | deg C | 507:62 | [5 empty] | Discharge Air Temperature |  |  |  | Attr | York RTU.Fan Control | 3 | Supply Air Temperature | UCBapp.newUCB.SA_T | Present Value | FALSE |  |  |  | AV:29564 | IR:158 | AI:3 |  | Value |  |  | Views.Details.Economizer.Service | Supply Air Temperature | 1675 | 182 |  | Views.Details.Econ.Service | SAT | 1709 | 80
Prop | Templates.Fan Control | Supply Air Temperature | 1675 | 182 | 7014 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | N/A |  |  |  |  | 10ths | 0 | deg C | 507:62 | [5 empty] | Discharge Air Temperature |  |  |  | Attr | York RTU.Fan Control | 3 | Supply Air Temperature | UCBapp.newUCB.SA_T | Present Value | FALSE |  |  |  | AV:29564 | IR:158 | AI:3 |  | Value |  |  | Views.Details.FanVFD.Service | Supply Air Temperature | 1675 | 182 |  | Views.Details.FanVFD.Service | SAT | 1709 | 80
Prop | Templates.Fan Control | Supply Air Temperature | 1675 | 182 | 7014 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | N/A |  |  |  |  | 10ths | 0 | deg C | 507:62 | [5 empty] | Discharge Air Temperature |  |  |  | Attr | York RTU.Fan Control | 3 | Supply Air Temperature | UCBapp.newUCB.SA_T | Present Value | FALSE |  |  |  | AV:29564 | IR:158 | AI:3 |  | Value |  |  | Views.Details.Single Zone VAV.Service | Supply Air Temperature | 1675 | 182 |  | Views.Details.SZ VAV.Service | SAT | 1709 | 80
Prop | Templates.Fan Control | Supply Air Temperature | 1675 | 182 | 7014 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | N/A |  |  |  |  | 10ths | 0 | deg C | 507:62 | [5 empty] | Discharge Air Temperature |  |  |  | Attr | York RTU.Fan Control | 3 | Supply Air Temperature | UCBapp.newUCB.SA_T | Present Value | FALSE |  |  |  | AV:29564 | IR:158 | AI:3 |  | Value |  |  | Views.Commissioning.Quick Start | Supply Air Temperature | 1675 | 182 |  | Views.Commission.Quick Start | SAT | 1709 | 80
Prop | Templates.Fan Control | Supply Air Temperature | 1675 | 182 | 7014 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | N/A |  |  |  |  | 10ths | 0 | deg C | 507:62 | [5 empty] | Discharge Air Temperature |  |  |  | Attr | York RTU.Fan Control | 3 | Supply Air Temperature | UCBapp.newUCB.SA_T | Present Value | FALSE |  |  |  | AV:29564 | IR:158 | AI:3 |  | Value |  |  | Views.Details.Heating.Service | Supply Air Temperature | 1675 | 182 |  | Views.Details.Htg.Service | SAT | 1709 | 80
Prop | Templates.Fan Control | Duct Static Pressure | 1675 | 183 | 7015 | TRUE | FALSE | FALSE | 4 | Float | 100ths | 4 | in wc | 507:58 | N/A |  |  |  |  | 100ths | 0 | kPa | 507:54 | [9 empty] | Attr | York RTU.Fan Control | 3 | Duct Static Pressure | UCBapp.newUCB.DUCT_P | Present Value | FALSE |  |  | York RTU.Fan Control.Fan Control Type:Present Value = Variable Speed | AV:29565 | IR:159 | AI:4 |  | Value |  |  | Views.Summary.Sensors.Sensors | Duct Static Pressure | 1675 | 183 |  | Views.Summary.Sensors.Sensors | DctPrs | 1709 | 81
Prop | Templates.Fan Control | Duct Static Pressure | 1675 | 183 | 7015 | TRUE | FALSE | FALSE | 4 | Float | 100ths | 4 | in wc | 507:58 | N/A |  |  |  |  | 100ths | 0 | kPa | 507:54 | [9 empty] | Attr | York RTU.Fan Control | 3 | Duct Static Pressure | UCBapp.newUCB.DUCT_P | Present Value | FALSE |  |  | York RTU.Fan Control.Fan Control Type:Present Value = Variable Speed | AV:29565 | IR:159 | AI:4 |  | Value |  |  | Views.Details.Power Exhaust.Setup | Duct Static Pressure | 1675 | 183 |  | Views.Details.PowerEx.Setup | DctPrs | 1709 | 81
Prop | Templates.Fan Control | Duct Static Pressure | 1675 | 183 | 7015 | TRUE | FALSE | FALSE | 4 | Float | 100ths | 4 | in wc | 507:58 | N/A |  |  |  |  | 100ths | 0 | kPa | 507:54 | [9 empty] | Attr | York RTU.Fan Control | 3 | Duct Static Pressure | UCBapp.newUCB.DUCT_P | Present Value | FALSE |  |  | York RTU.Fan Control.Fan Control Type:Present Value = Variable Speed | AV:29565 | IR:159 | AI:4 |  | Value |  |  | Views.Details.FanVFD.Service | Duct Static Pressure | 1675 | 183 |  | Views.Details.FanVFD.Service | DctPrs | 1709 | 81
Prop | Templates.Fan Control | Duct Pressure Setpoint | 1675 | 184 | 7016 | TRUE | TRUE | FALSE | 4 | Float | 100ths | 4 | in wc | 507:58 | 1.5 | 0 | 5 |  |  | 100ths | 0 | kPa | 507:54 | 0 | 1.25 | [7 empty] | Attr | York RTU.Fan Control | 3 | Duct Pressure Setpoint | UCBapp.newUCB.DAP_SP | Relinquish Default | FALSE |  |  | York RTU.Fan Control.Fan Control Type:Present Value = Variable Speed | AV:29566 | HR:10 | ADF:31 |  | Value |  |  | Views.Details.FanVFD.Setup | Duct Pressure Setpoint | 1675 | 184 |  | Views.Details.FanVFD.Setup | DctPrs-Sp | 1709 | 82
Prop | Templates.Fan Control | Duct Pressure Setpoint | 1675 | 184 | 7016 | TRUE | TRUE | FALSE | 4 | Float | 100ths | 4 | in wc | 507:58 | 1.5 | 0 | 5 |  |  | 100ths | 0 | kPa | 507:54 | 0 | 1.25 | [7 empty] | Attr | York RTU.Fan Control | 3 | Duct Pressure Setpoint | UCBapp.newUCB.DAP_SP | Relinquish Default | FALSE |  |  | York RTU.Fan Control.Fan Control Type:Present Value = Variable Speed | AV:29566 | HR:10 | ADF:31 |  | Value |  |  | Views.Details.FanVFD.Service | Duct Pressure Setpoint | 1675 | 184 |  | Views.Details.FanVFD.Service | DctPrs-Sp | 1709 | 82
Prop | Templates.Fan Control | Duct Pressure Setpoint | 1675 | 184 | 7016 | TRUE | TRUE | FALSE | 4 | Float | 100ths | 4 | in wc | 507:58 | 1.5 | 0 | 5 |  |  | 100ths | 0 | kPa | 507:54 | 0 | 1.25 | [7 empty] | Attr | York RTU.Fan Control | 3 | Duct Pressure Setpoint | UCBapp.newUCB.DAP_SP | Relinquish Default | FALSE |  |  | York RTU.Fan Control.Fan Control Type:Present Value = Variable Speed | AV:29566 | HR:10 | ADF:31 |  | Value |  |  | Views.Clone.Partial Clone 1 | Duct Pressure Setpoint | 1675 | 184 |  |  | DctPrs-Sp | 1709 | 82
Prop | Templates.Fan Control | Duct Pressure Shutdown Setpoint | 1675 | 185 | 7017 | TRUE | TRUE | FALSE | 4 | Float | 100ths | 4 | in wc | 507:58 | 4.5 | 0 | 5 |  |  | 100ths | 0 | kPa | 507:54 | 0 | 1.25 | [7 empty] | Attr | York RTU.Fan Control | 3 | Duct Pressure Shutdown Setpoint | UCBapp.newUCB.Duct_Pressure_Shutdown_SP | Relinquish Default | FALSE |  |  | York RTU.Fan Control.Fan Control Type:Present Value = Variable Speed | AV:29567 | HR:11 | ADF:32 |  | Value |  |  | Views.Details.FanVFD.Setup | Duct Pressure Shutdown Setpoint | 1675 | 185 |  | Views.Details.FanVFD.Setup | DctShutdownSp | 1709 | 83
Prop | Templates.Fan Control | Duct Pressure Shutdown Setpoint | 1675 | 185 | 7017 | TRUE | TRUE | FALSE | 4 | Float | 100ths | 4 | in wc | 507:58 | 4.5 | 0 | 5 |  |  | 100ths | 0 | kPa | 507:54 | 0 | 1.25 | [7 empty] | Attr | York RTU.Fan Control | 3 | Duct Pressure Shutdown Setpoint | UCBapp.newUCB.Duct_Pressure_Shutdown_SP | Relinquish Default | FALSE |  |  | York RTU.Fan Control.Fan Control Type:Present Value = Variable Speed | AV:29567 | HR:11 | ADF:32 |  | Value |  |  | Views.Clone.Partial Clone 1 | Duct Pressure Shutdown Setpoint | 1675 | 185 |  |  | DctShutdownSp | 1709 | 83
Prop | Templates.Fan Control | Continuous Fan Operation in Occupied Mode | 1675 | 186 | 7018 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Yes/No | 1698 | On | [6 empty] | Yes/No | 1698 | [6 empty] | 1698 | 0 = Yes 1 = No |  | Attr | York RTU.Fan Control | 3 | Continuous Fan Operation in Occupied Mode | UCBapp.newUCB.Continuous_Fan_Op_in_Occ_Mode | Relinquish Default | FALSE |  |  | York RTU.Fan Control.Fan Control Type:Present Value <> Variable Speed | MV:29568 | HR:91 | ADI:25 |  | Value |  |  | Views.Commissioning.Standard | Continuous Fan Operation in Occupied Mode | 1675 | 186 |  | Views.Commission.Standard | FanOnOcc | 1709 | 84
Prop | Templates.Fan Control | Continuous Fan Operation in Occupied Mode | 1675 | 186 | 7018 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Yes/No | 1698 | On | [6 empty] | Yes/No | 1698 | [6 empty] | 1698 | 0 = Yes 1 = No |  | Attr | York RTU.Fan Control | 3 | Continuous Fan Operation in Occupied Mode | UCBapp.newUCB.Continuous_Fan_Op_in_Occ_Mode | Relinquish Default | FALSE |  |  | York RTU.Fan Control.Fan Control Type:Present Value <> Variable Speed | MV:29568 | HR:91 | ADI:25 |  | Value |  |  | Views.Details.Indoor Fan.Setup | Continuous Fan Operation in Occupied Mode | 1675 | 186 |  | Views.Details.Fan.Setup | FanOnOcc | 1709 | 84
Prop | Templates.Fan Control | Continuous Fan Operation in Occupied Mode | 1675 | 186 | 7018 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Yes/No | 1698 | On | [6 empty] | Yes/No | 1698 | [6 empty] | 1698 | 0 = Yes 1 = No |  | Attr | York RTU.Fan Control | 3 | Continuous Fan Operation in Occupied Mode | UCBapp.newUCB.Continuous_Fan_Op_in_Occ_Mode | Relinquish Default | FALSE |  |  | York RTU.Fan Control.Fan Control Type:Present Value <> Variable Speed | MV:29568 | HR:91 | ADI:25 |  | Value |  |  | Views.Clone.Partial Clone 1 | Continuous Fan Operation in Occupied Mode | 1675 | 186 |  |  | FanOnOcc | 1709 | 84
Prop | Templates.Fan Control | Continuous Fan Operation in Occupied Mode | 1675 | 186 | 7018 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Yes/No | 1698 | On | [6 empty] | Yes/No | 1698 | [6 empty] | 1698 | 0 = Yes 1 = No |  | Attr | York RTU.Fan Control | 3 | Continuous Fan Operation in Occupied Mode | UCBapp.newUCB.Continuous_Fan_Op_in_Occ_Mode | Relinquish Default | FALSE |  |  | York RTU.Fan Control.Fan Control Type:Present Value <> Variable Speed | MV:29568 | HR:91 | ADI:25 |  | Value |  |  | Views.Commissioning.Quick Start | Continuous Fan Operation in Occupied Mode | 1675 | 186 |  | Views.Commission.Quick Start | FanOnOcc | 1709 | 84
Prop | Templates.Fan Control | Turn Off Continuous Fan Operation When Starting Heat | 1675 | 187 | 7019 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Yes/No | 1698 | Off | [6 empty] | Yes/No | 1698 | [6 empty] | 1698 | 0 = Yes 1 = No |  | Attr | York RTU.Fan Control | 3 | Turn Off Continuous Fan Operation When Starting Heat | UCBapp.newUCB.Heat_Fan_Mode | Relinquish Default | FALSE |  |  | York RTU.Fan Control.Fan Control Type:Present Value <> Variable Speed | MV:29569 | HR:92 | ADI:26 |  | Value |  |  | Views.Details.Indoor Fan.Setup | Turn Off Continuous Fan Operation When Starting Heat | 1675 | 187 |  | Views.Details.Fan.Setup | FanOffStartHeat | 1709 | 85
Prop | Templates.Fan Control | Turn Off Continuous Fan Operation When Starting Heat | 1675 | 187 | 7019 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Yes/No | 1698 | Off | [6 empty] | Yes/No | 1698 | [6 empty] | 1698 | 0 = Yes 1 = No |  | Attr | York RTU.Fan Control | 3 | Turn Off Continuous Fan Operation When Starting Heat | UCBapp.newUCB.Heat_Fan_Mode | Relinquish Default | FALSE |  |  | York RTU.Fan Control.Fan Control Type:Present Value <> Variable Speed | MV:29569 | HR:92 | ADI:26 |  | Value |  |  | Views.Clone.Partial Clone 1 | Turn Off Continuous Fan Operation When Starting Heat | 1675 | 187 |  |  | FanOffStartHeat | 1709 | 85
Prop | Templates.Fan Control | Occupied: No Heat or Cool % Command | 1675 | 188 | 7020 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 50 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Fan Control | 3 | Occupied: No Heat or Cool % Command | UCBapp.newUCB.Fan_Only_Speed | Relinquish Default | FALSE |  |  | York RTU.Fan Control.Fan Control Type:Present Value = Fixed Variable | AV:29570 | HR:12 | ADF:33 |  | Value |  |  | Views.Details.Indoor Fan.Setup | Occupied: No Heat or Cool % Command | 1675 | 188 |  | Views.Details.Fan.Setup | FanOnly-%Cmd | 1709 | 86
Prop | Templates.Fan Control | Occupied: No Heat or Cool % Command | 1675 | 188 | 7020 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 50 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Fan Control | 3 | Occupied: No Heat or Cool % Command | UCBapp.newUCB.Fan_Only_Speed | Relinquish Default | FALSE |  |  | York RTU.Fan Control.Fan Control Type:Present Value = Fixed Variable | AV:29570 | HR:12 | ADF:33 |  | Value |  |  | Views.Clone.Partial Clone 1 | Occupied: No Heat or Cool % Command | 1675 | 188 |  |  | FanOnly-%Cmd | 1709 | 86
Prop | Templates.Fan Control | Occupied: One Stage of Cool % Command | 1675 | 189 | 7021 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 70 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Fan Control | 3 | Occupied: One Stage of Cool % Command | UCBapp.newUCB.Occ_One_Stg_of_Cool_Per_Cmd | Relinquish Default | FALSE |  |  | York RTU.Fan Control.Fan Control Type:Present Value = Fixed Variable | AV:29571 | HR:13 | ADF:34 |  | Value |  |  | Views.Details.Indoor Fan.Setup | Occupied: One Stage of Cool % Command | 1675 | 189 |  | Views.Details.Fan.Setup | 1ClgStg-%Cmd | 1709 | 87
Prop | Templates.Fan Control | Occupied: One Stage of Cool % Command | 1675 | 189 | 7021 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 70 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Fan Control | 3 | Occupied: One Stage of Cool % Command | UCBapp.newUCB.Occ_One_Stg_of_Cool_Per_Cmd | Relinquish Default | FALSE |  |  | York RTU.Fan Control.Fan Control Type:Present Value = Fixed Variable | AV:29571 | HR:13 | ADF:34 |  | Value |  |  | Views.Clone.Partial Clone 1 | Occupied: One Stage of Cool % Command | 1675 | 189 |  |  | 1ClgStg-%Cmd | 1709 | 87
Prop | Templates.Fan Control | Occupied: Two Stage of Cool % Command | 1675 | 190 | 7022 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 80 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Fan Control | 3 | Occupied: Two Stage of Cool % Command | UCBapp.newUCB.Occ_Two_Stg_of_Cool_Per_Cmd | Relinquish Default | FALSE |  |  | York RTU.Fan Control.Fan Control Type:Present Value = Fixed Variable | AV:29572 | HR:14 | ADF:35 |  | Value |  |  | Views.Details.Indoor Fan.Setup | Occupied: Two Stage of Cool % Command | 1675 | 190 |  | Views.Details.Fan.Setup | 2ClgStg-%Cmd | 1709 | 88
Prop | Templates.Fan Control | Occupied: Two Stage of Cool % Command | 1675 | 190 | 7022 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 80 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Fan Control | 3 | Occupied: Two Stage of Cool % Command | UCBapp.newUCB.Occ_Two_Stg_of_Cool_Per_Cmd | Relinquish Default | FALSE |  |  | York RTU.Fan Control.Fan Control Type:Present Value = Fixed Variable | AV:29572 | HR:14 | ADF:35 |  | Value |  |  | Views.Clone.Partial Clone 1 | Occupied: Two Stage of Cool % Command | 1675 | 190 |  |  | 2ClgStg-%Cmd | 1709 | 88
Prop | Templates.Fan Control | Occupied: One Stage of Heat % Command | 1675 | 191 | 7023 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 100 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Fan Control | 3 | Occupied: One Stage of Heat % Command | UCBapp.newUCB.Occ_One_Stg_of_Heat_Per_Cmd | Relinquish Default | FALSE |  |  | UCBapp.newUCB.NotElectricHeat_And_FixedVar:Present Value = Active | AV:29573 | HR:17 | ADF:38 |  | Value |  |  | Views.Details.Indoor Fan.Setup | Occupied: One Stage of Heat % Command | 1675 | 191 |  | Views.Details.Fan.Setup | 1HtgStg-%Cmd | 1709 | 89
Prop | Templates.Fan Control | Occupied: One Stage of Heat % Command | 1675 | 191 | 7023 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 100 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Fan Control | 3 | Occupied: One Stage of Heat % Command | UCBapp.newUCB.Occ_One_Stg_of_Heat_Per_Cmd | Relinquish Default | FALSE |  |  | UCBapp.newUCB.NotElectricHeat_And_FixedVar:Present Value = Active | AV:29573 | HR:17 | ADF:38 |  | Value |  |  | Views.Clone.Partial Clone 1 | Occupied: One Stage of Heat % Command | 1675 | 191 |  |  | 1HtgStg-%Cmd | 1709 | 89
Prop | Templates.Fan Control | Occupied: Two Stage of Heat % Command | 1675 | 192 | 7024 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 100 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Fan Control | 3 | Occupied: Two Stage of Heat % Command | UCBapp.newUCB.Occ_Two_Stg_of_Heat_Per_Cmd | Relinquish Default | FALSE |  |  | UCBapp.newUCB.NotElectricHeat_And_FixedVar:Present Value = Active | AV:29574 | HR:18 | ADF:39 |  | Value |  |  | Views.Details.Indoor Fan.Setup | Occupied: Two Stage of Heat % Command | 1675 | 192 |  | Views.Details.Fan.Setup | 2HtgStg-%Cmd | 1709 | 90
Prop | Templates.Fan Control | Occupied: Two Stage of Heat % Command | 1675 | 192 | 7024 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 100 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Fan Control | 3 | Occupied: Two Stage of Heat % Command | UCBapp.newUCB.Occ_Two_Stg_of_Heat_Per_Cmd | Relinquish Default | FALSE |  |  | UCBapp.newUCB.NotElectricHeat_And_FixedVar:Present Value = Active | AV:29574 | HR:18 | ADF:39 |  | Value |  |  | Views.Clone.Partial Clone 1 | Occupied: Two Stage of Heat % Command | 1675 | 192 |  |  | 2HtgStg-%Cmd | 1709 | 90
Prop | Templates.Fan Control | Supply Air Temperature Sensor Fault | 1675 | 306 | 7025 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Fan Control | 3 | Supply Air Temperature Sensor Fault | UCBapp.newUCB.Supply_Air_Temp_Sensor_Fault | Present Value | FALSE
Prop | Templates.Fan Control | Duct Static Pressure Sensor Fault | 1675 | 307 | 7026 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Fan Control | 3 | Duct Static Pressure Sensor Fault | UCBapp.newUCB.DSP_Sensor_Fault | Present Value | FALSE
Prop | Templates.Fan Control | Occupied: Three Stage of Cool % Command | 1675 | 320 | 7027 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 90 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Fan Control | 3 | Occupied: Three Stage of Cool % Command | UCBapp.newUCB.Occ_Three_Stg_of_Cool_Per_Cmd | Relinquish Default | FALSE |  |  | York RTU.Fan Control.Fan Control Type:Present Value = Fixed Variable | AV:29819 | HR:15 | ADF:36 |  | Value |  |  | Views.Details.Indoor Fan.Setup | Occupied: Three Stage of Cool % Command | 1675 | 320 |  | Views.Details.Fan.Setup | 3ClgStg-%Cmd | 1709 | 442
Prop | Templates.Fan Control | Occupied: Three Stage of Cool % Command | 1675 | 320 | 7027 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 90 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Fan Control | 3 | Occupied: Three Stage of Cool % Command | UCBapp.newUCB.Occ_Three_Stg_of_Cool_Per_Cmd | Relinquish Default | FALSE |  |  | York RTU.Fan Control.Fan Control Type:Present Value = Fixed Variable | AV:29819 | HR:15 | ADF:36 |  | Value |  |  | Views.Clone.Partial Clone 1 | Occupied: Three Stage of Cool % Command | 1675 | 320 |  |  | 3ClgStg-%Cmd | 1709 | 442
Prop | Templates.Fan Control | Occupied: Four Stage of Cool % Command | 1675 | 321 | 7028 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 100 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Fan Control | 3 | Occupied: Four Stage of Cool % Command | UCBapp.newUCB.Occ_Four_Stg_of_Cool_Per_Cmd | Relinquish Default | FALSE |  |  | York RTU.Fan Control.Fan Control Type:Present Value = Fixed Variable | AV:29820 | HR:16 | ADF:37 |  | Value |  |  | Views.Details.Indoor Fan.Setup | Occupied: Four Stage of Cool % Command | 1675 | 321 |  | Views.Details.Fan.Setup | 4ClgStg-%Cmd | 1709 | 443
Prop | Templates.Fan Control | Occupied: Four Stage of Cool % Command | 1675 | 321 | 7028 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 100 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Fan Control | 3 | Occupied: Four Stage of Cool % Command | UCBapp.newUCB.Occ_Four_Stg_of_Cool_Per_Cmd | Relinquish Default | FALSE |  |  | York RTU.Fan Control.Fan Control Type:Present Value = Fixed Variable | AV:29820 | HR:16 | ADF:37 |  | Value |  |  | Views.Clone.Partial Clone 1 | Occupied: Four Stage of Cool % Command | 1675 | 321 |  |  | 4ClgStg-%Cmd | 1709 | 443
Prop | Templates.Fan Control | Occupied: Three Stage of Heat % Command | 1675 | 322 | 7029 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 100 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Fan Control | 3 | Occupied: Three Stage of Heat % Command | UCBapp.newUCB.Occ_Three_Stg_of_Heat_Per_Cmd | Relinquish Default | FALSE |  |  | UCBapp.newUCB.NotElectricHeat_And_FixedVar:Present Value = Active | AV:29821 | HR:19 | ADF:40 |  | Value |  |  | Views.Details.Indoor Fan.Setup | Occupied: Three Stage of Heat % Command | 1675 | 322 |  | Views.Details.Fan.Setup | 3HtgStg-%Cmd | 1709 | 444
Prop | Templates.Fan Control | Occupied: Three Stage of Heat % Command | 1675 | 322 | 7029 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 100 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Fan Control | 3 | Occupied: Three Stage of Heat % Command | UCBapp.newUCB.Occ_Three_Stg_of_Heat_Per_Cmd | Relinquish Default | FALSE |  |  | UCBapp.newUCB.NotElectricHeat_And_FixedVar:Present Value = Active | AV:29821 | HR:19 | ADF:40 |  | Value |  |  | Views.Clone.Partial Clone 1 | Occupied: Three Stage of Heat % Command | 1675 | 322 |  |  | 3HtgStg-%Cmd | 1709 | 444
Prop | Templates.Fan Control | Unit Locked Out Due to Air Proving Switch | 1675 | 340 | 7030 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Fan Control | 3 | Unit Locked Out Due to Air Proving Switch | UCBapp.newUCB.Unit_Locked_Out_Due_to_APS | Present Value | FALSE
Prop | Templates.Fan Control | Unit Shutdown Due to Air Proving Switch | 1675 | 341 | 7031 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | SE Airflow State | 1621 | Normal_Off | [6 empty] | SE Airflow State | 1621 | [6 empty] | 1621 | 0 = Normal Off 1 = Startup 2 = Normal On 3 = Proof Lost OK ... |  | Attr | York RTU.Fan Control | 3 | Unit Shutdown Due to Air Proving Switch | UCBapp.newUCB.APS_Stuck_Closed | Present Value | FALSE
Prop | Templates.Fan Control | Unit Shutdown Due High Duct Static Pressure | 1675 | 343 | 7033 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Fan Control | 3 | Unit Shutdown Due High Duct Static Pressure | UCBapp.newUCB.Unit_Shutdown_Due_High_DSP | Present Value | FALSE
Prop | Templates.Fan Control | Unit Locked Out Supply Fan Overload | 1675 | 344 | 7034 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Fan Control | 3 | Unit Locked Out Supply Fan Overload | UCBapp.newUCB.Unit_Locked_Out_SF_Overload | Present Value | FALSE
Prop | Templates.Fan Control | Dirty Filter Switch Installed | 1675 | 364 | 7035 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | [7 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Fan Control | 3 | Dirty Filter Switch Installed | EM Variable: 1 |  | TRUE | [7 empty] | Value |  |  | Views.Commissioning.Options | Dirty Filter Switch Installed | 1675 | 364 |  | Views.Commission.Options | DFSInst | 1709 | 475
Prop | Templates.Fan Control | Air Proving Switch Stuck Closed | 1675 | 365 | 7036 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | SE Airflow State | 1621 | Normal_Off | [6 empty] | SE Airflow State | 1621 | [6 empty] | 1621 | 0 = Normal Off 1 = Startup 2 = Normal On 3 = Proof Lost OK ... |  | Attr | York RTU.Fan Control | 3 | Air Proving Switch Stuck Closed | UCBapp.newUCB.APS_Stuck_Closed | Present Value | FALSE
Prop | Templates.Fan Control | SZ VAV Minimum Fan Speed | 1675 | 627 | 7037 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 66 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Fan Control | 3 | SZ VAV Minimum Fan Speed | UCBapp.newUCB.SZ_VAV_Min_Fan_Speed | Relinquish Default | FALSE |  |  | York RTU.SZ VAV Enabled:Present Value = On | AV:29913 | HR:73 | ADF:159 |  | Value |  |  | Views.Details.Single Zone VAV.Setup | SZ VAV Minimum Fan Speed | 1675 | 627 |  | Views.Details.SZ VAV.Setup | SZVAVMinFanSpd | 1709 | 647
Prop | Templates.Fan Control | SZ VAV Minimum Fan Speed | 1675 | 627 | 7037 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 66 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Fan Control | 3 | SZ VAV Minimum Fan Speed | UCBapp.newUCB.SZ_VAV_Min_Fan_Speed | Relinquish Default | FALSE |  |  | York RTU.SZ VAV Enabled:Present Value = On | AV:29913 | HR:73 | ADF:159 |  | Value |  |  | Views.Clone.Partial Clone 1 | SZ VAV Minimum Fan Speed | 1675 | 627 |  |  | SZVAVMinFanSpd | 1709 | 647
Prop | Templates.Fan Control | Low Pressure Limit 1 | 1714 | 122 | 7038 | FALSE | TRUE | FALSE | 4 | Float | 100ths | 4 | in wc | 507:58 | 0.05 | 0.01 | 1 |  |  | 100ths | 0 | Pa | 507:53 | 2.5 | 250 | [7 empty] | Attr | York RTU.Fan Control | 3 | Low Pressure Limit 1 | UCBapp.newUCB.Min_Duct_Static_Proof | Relinquish Default | FALSE |  |  | York RTU.Fan Control.Fan Control Type:Present Value = Variable Speed | AV:30072 | HR:846 | ADF:194 |  | Value |  |  | Views.Details.FanVFD.Setup | Discharge Air Static Pressure Minimum | 2644 | 227 |  | Views.Details.FanVFD.Setup | DAP-Min | 2645 | 244
Prop | Templates.Fan Control | Time | 1709 | 342 | 7040 | FALSE | TRUE | FALSE | 18 | UnsignedInteger | 1s | 6 | seconds | 507:73 | 90 | 0 | 600 |  |  | 1s | 0 | seconds | 507:73 | 0 | 600 | [7 empty] | Attr | York RTU.Fan Control | 3 | Time | UCBapp.newUCB.Min_Duct_Static_Proof_Delay | Relinquish Default | FALSE |  |  | York RTU.Fan Control.Fan Control Type:Present Value = Variable Speed | AV:30073 | HR:847 | ADF:195 |  | Value |  |  | Views.Details.FanVFD.Setup | Discharge Air Static Pressure Alarm Delay | 2644 | 228 |  | Views.Details.FanVFD.Setup | DAP-AlmDly | 2645 | 245
Prop | Templates.Fan Control | DFSInst | 1709 | 475 | 7041 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm | This is the Effective DFS Alarm. used only to trigger the alarms, not to indicate actual hardware state. | Attr | York RTU.Fan Control | 3 | DFSInst | UCBapp.newUCB.EFF_DFS_ALARM | Present Value | FALSE |  |  | York RTU.Fan Control.Dirty Filter Switch Installed:Present Value = Yes
Prop | Templates.Fan Control | Dehumidification % Command | 1714 | 234 | 7042 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 80 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Fan Control | 3 | Dehumidification % Command | UCBapp.newUCB.Dehum_Fan_Speed | Relinquish Default | FALSE |  |  | York RTU.Fan Control.Fan Control Type:Present Value >= Fixed Variable | AV:29948 | HR:851 | ADF:190 |  | Value |  |  | Views.Details.Indoor Fan.Setup | Dehumidification % Command | 1714 | 234 |  | Views.Details.Fan.Setup | Dehum%Cmd | 1709 | 731
Prop | Templates.Fan Control | A2L Fan Speed | 2644 | 549 | 7043 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 50 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Fan Control | 3 | A2L Fan Speed | UCBapp.newUCB.A2L_Fan_Speed | Relinquish Default | FALSE
Tmpl | Templates.Cooling Control | [31 empty] | Model | York RTU.Cooling Control | 4
Prop | Templates.Cooling Control | Cooling Mode Enabled For Operation | 1675 | 66 | 7000 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | On | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Cooling Control | 4 | Cooling Mode Enabled For Operation | UCBapp.newUCB.CLG_EN | Relinquish Default | FALSE |  |  |  | MV:29575 | HR:93 | ADI:27 |  | Value |  |  | Views.Commissioning.Standard | Cooling Mode Enabled For Operation | 1675 | 66 |  | Views.Commission.Standard | Clg-En | 1709 | 91
Prop | Templates.Cooling Control | Cooling Mode Enabled For Operation | 1675 | 66 | 7000 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | On | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Cooling Control | 4 | Cooling Mode Enabled For Operation | UCBapp.newUCB.CLG_EN | Relinquish Default | FALSE |  |  |  | MV:29575 | HR:93 | ADI:27 |  | Value |  |  | Views.Commissioning.Quick Start | Cooling Mode Enabled For Operation | 1675 | 66 |  | Views.Commission.Quick Start | Clg-En | 1709 | 91
Prop | Templates.Cooling Control | Number of Cooling Stages Installed | 1675 | 67 | 7001 | TRUE | TRUE | FALSE | 16 | Byte | 1s | 6 |  | 507:95 | 1 | 1 | 4 |  |  | 1s | 0 |  | 507:95 | 1 | 4 |  |  |  | Number of Cooling Stages |  |  |  | Attr | York RTU.Cooling Control | 4 | Number of Cooling Stages Installed | UCBapp.newUCB.Max_Cooling_Stages | Relinquish Default | TRUE |  |  |  | AV:29576 | HR:401 | ADI:120 |  | Value |  |  | Views.Commissioning.Standard | Number of Cooling Stages Installed | 1675 | 67 |  | Views.Commission.Standard | #ClgStgs | 1709 | 92
Prop | Templates.Cooling Control | Number of Cooling Stages Installed | 1675 | 67 | 7001 | TRUE | TRUE | FALSE | 16 | Byte | 1s | 6 |  | 507:95 | 1 | 1 | 4 |  |  | 1s | 0 |  | 507:95 | 1 | 4 |  |  |  | Number of Cooling Stages |  |  |  | Attr | York RTU.Cooling Control | 4 | Number of Cooling Stages Installed | UCBapp.newUCB.Max_Cooling_Stages | Relinquish Default | TRUE |  |  |  | AV:29576 | HR:401 | ADI:120 |  | Value |  |  | Views.Commissioning.Quick Start | Number of Cooling Stages Installed | 1675 | 67 |  | Views.Commission.Quick Start | #ClgStgs | 1709 | 92
Prop | Templates.Cooling Control | Cooling Status | 1675 | 69 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | SE RTU Cooling Control Status | 1740 | Off_Idle | [6 empty] | SE RTU Cooling Control Status | 1740 | [6 empty] | 1740 | 0 = Off-Idle 1 = Thermostat Cooling 2 = Unoccupied Cooling 3 = Occupied Cooling ... |  | Attr | York RTU.Cooling Control | 4 | Cooling Status | UCBapp.newUCB.Cooling_Status | Present Value | FALSE |  |  |  | MV:29577 | IR:308 | ADI:28 |  | Value |  |  | Views.Status.Status | Cooling Status | 1675 | 69 |  | Views.Status.Status | Clg-S | 1709 | 93
Prop | Templates.Cooling Control | Cooling Status | 1675 | 69 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | SE RTU Cooling Control Status | 1740 | Off_Idle | [6 empty] | SE RTU Cooling Control Status | 1740 | [6 empty] | 1740 | 0 = Off-Idle 1 = Thermostat Cooling 2 = Unoccupied Cooling 3 = Occupied Cooling ... |  | Attr | York RTU.Cooling Control | 4 | Cooling Status | UCBapp.newUCB.Cooling_Status | Present Value | FALSE |  |  |  | MV:29577 | IR:308 | ADI:28 |  | Value |  |  | Views.Details.Cooling.Service.Unit | Cooling Status | 1675 | 69 |  | Views.Details.Clg.Service.Unit | Clg-S | 1709 | 93
Prop | Templates.Cooling Control | Cooling Status | 1675 | 69 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | SE RTU Cooling Control Status | 1740 | Off_Idle | [6 empty] | SE RTU Cooling Control Status | 1740 | [6 empty] | 1740 | 0 = Off-Idle 1 = Thermostat Cooling 2 = Unoccupied Cooling 3 = Occupied Cooling ... |  | Attr | York RTU.Cooling Control | 4 | Cooling Status | UCBapp.newUCB.Cooling_Status | Present Value | FALSE |  |  |  | MV:29577 | IR:308 | ADI:28 |  | Value |  |  | Views.Details.Economizer.Service | Cooling Status | 1675 | 69 |  | Views.Details.Econ.Service | Clg-S | 1709 | 93
Prop | Templates.Cooling Control | Cooling Status | 1675 | 69 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | SE RTU Cooling Control Status | 1740 | Off_Idle | [6 empty] | SE RTU Cooling Control Status | 1740 | [6 empty] | 1740 | 0 = Off-Idle 1 = Thermostat Cooling 2 = Unoccupied Cooling 3 = Occupied Cooling ... |  | Attr | York RTU.Cooling Control | 4 | Cooling Status | UCBapp.newUCB.Cooling_Status | Present Value | FALSE |  |  |  | MV:29577 | IR:308 | ADI:28 |  | Value |  |  | Views.Details.FanVFD.Service | Cooling Status | 1675 | 69 |  | Views.Details.FanVFD.Service | Clg-S | 1709 | 93
Prop | Templates.Cooling Control | Cooling Status | 1675 | 69 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | SE RTU Cooling Control Status | 1740 | Off_Idle | [6 empty] | SE RTU Cooling Control Status | 1740 | [6 empty] | 1740 | 0 = Off-Idle 1 = Thermostat Cooling 2 = Unoccupied Cooling 3 = Occupied Cooling ... |  | Attr | York RTU.Cooling Control | 4 | Cooling Status | UCBapp.newUCB.Cooling_Status | Present Value | FALSE |  |  |  | MV:29577 | IR:308 | ADI:28 |  | Value |  |  | Views.Commissioning.Quick Start | Cooling Status | 1675 | 69 |  | Views.Commission.Quick Start | Clg-S | 1709 | 93
Prop | Templates.Cooling Control | Minimum Runtime for a Cooling Stage | 1675 | 71 | 7003 | TRUE | TRUE | FALSE | 16 | Byte | 1s | 6 | minutes | 507:72 | 180 | 3 | 10 |  |  | 1s | 0 | minutes | 507:72 | 3 | 10 | [7 empty] | Attr | York RTU.Cooling Control | 4 | Minimum Runtime for a Cooling Stage | UCBapp.newUCB.Cooling_Minimum_On_Time | Relinquish Default | FALSE |  |  |  | AV:29578 | IR:20 | ADF:41 |  | Value |  |  | Views.Details.Cooling.Setup | Minimum Runtime for a Cooling Stage | 1675 | 71 |  | Views.Details.Clg.Setup | MinRtCoolStg | 1709 | 94
Prop | Templates.Cooling Control | Lead/Lag Equalize Cooling Stage Runtime Enabled | 1675 | 72 | 7004 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Off | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Cooling Control | 4 | Lead/Lag Equalize Cooling Stage Runtime Enabled | UCBapp.newUCB.Lead_Lag_Equal_Cool_Stg Run_En | Relinquish Default | FALSE |  |  | UCBapp.newUCB.Lead_Lag_Display:Present Value = Inactive | MV:29579 | HR:402 | ADI:121 |  | Value |  |  | Views.Commissioning.Options | Lead/Lag Equalize Cooling Stage Runtime Enabled | 1675 | 72 |  | Views.Commission.Options | LeadLag-En | 1709 | 95
Prop | Templates.Cooling Control | Lead/Lag Equalize Cooling Stage Runtime Enabled | 1675 | 72 | 7004 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Off | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Cooling Control | 4 | Lead/Lag Equalize Cooling Stage Runtime Enabled | UCBapp.newUCB.Lead_Lag_Equal_Cool_Stg Run_En | Relinquish Default | FALSE |  |  | UCBapp.newUCB.Lead_Lag_Display:Present Value = Inactive | MV:29579 | HR:402 | ADI:121 |  | Value |  |  | Views.Details.Cooling.Setup | Lead/Lag Equalize Cooling Stage Runtime Enabled | 1675 | 72 |  | Views.Details.Clg.Setup | LeadLag-En | 1709 | 95
Prop | Templates.Cooling Control | Low Ambient Fan Pre-run Time For Cooling | 1675 | 73 | 7005 | TRUE | TRUE | FALSE | 17 | SignedInteger | 1s | 6 | seconds | 507:73 | 60 | 0 | 255 |  |  | 1s | 0 | seconds | 507:73 | 0 | 255 | [7 empty] | Attr | York RTU.Cooling Control | 4 | Low Ambient Fan Pre-run Time For Cooling | UCBapp.newUCB.Low_Amb_Fan_Pre_run_T_For_Cool | Relinquish Default | FALSE |  |  |  | AV:29580 | HR:418 | ADI:134 |  | Value |  |  | Views.Commissioning.Options | Low Ambient Fan Pre-run Time For Cooling | 1675 | 73 |  | Views.Commission.Options | LowAmbFanPrerunCool | 1709 | 96
Prop | Templates.Cooling Control | Low Ambient Fan Pre-run Time For Cooling | 1675 | 73 | 7005 | TRUE | TRUE | FALSE | 17 | SignedInteger | 1s | 6 | seconds | 507:73 | 60 | 0 | 255 |  |  | 1s | 0 | seconds | 507:73 | 0 | 255 | [7 empty] | Attr | York RTU.Cooling Control | 4 | Low Ambient Fan Pre-run Time For Cooling | UCBapp.newUCB.Low_Amb_Fan_Pre_run_T_For_Cool | Relinquish Default | FALSE |  |  |  | AV:29580 | HR:418 | ADI:134 |  | Value |  |  | Views.Details.Cooling.Setup | Low Ambient Fan Pre-run Time For Cooling | 1675 | 73 |  | Views.Details.Clg.Setup | LowAmbFanPrerunCool | 1709 | 96
Prop | Templates.Cooling Control | Low Ambient Fan Pre-run Time For Cooling | 1675 | 73 | 7005 | TRUE | TRUE | FALSE | 17 | SignedInteger | 1s | 6 | seconds | 507:73 | 60 | 0 | 255 |  |  | 1s | 0 | seconds | 507:73 | 0 | 255 | [7 empty] | Attr | York RTU.Cooling Control | 4 | Low Ambient Fan Pre-run Time For Cooling | UCBapp.newUCB.Low_Amb_Fan_Pre_run_T_For_Cool | Relinquish Default | FALSE |  |  |  | AV:29580 | HR:418 | ADI:134 |  | Value |  |  | Views.Details.Indoor Fan.Setup | Low Ambient Fan Pre-run Time For Cooling | 1675 | 73 |  | Views.Details.Fan.Setup | LowAmbFanPrerunCool | 1709 | 96
Prop | Templates.Cooling Control | OAT Cooling Cutout Enabled | 1675 | 127 | 7006 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Enable | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Cooling Control | 4 | OAT Cooling Cutout Enabled | UCBapp.newUCB.OAT_Cooling_Cutout_Enabled | Relinquish Default | FALSE |  |  |  | MV:29581 | HR:94 | ADI:29 |  | Value |  |  | Views.Commissioning.Standard | OAT Cooling Cutout Enabled | 1675 | 127 |  | Views.Commission.Standard | ClgOATCutout-En | 1709 | 97
Prop | Templates.Cooling Control | OAT Cooling Cutout Enabled | 1675 | 127 | 7006 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Enable | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Cooling Control | 4 | OAT Cooling Cutout Enabled | UCBapp.newUCB.OAT_Cooling_Cutout_Enabled | Relinquish Default | FALSE |  |  |  | MV:29581 | HR:94 | ADI:29 |  | Value |  |  | Views.Details.Cooling.Setup | OAT Cooling Cutout Enabled | 1675 | 127 |  | Views.Details.Clg.Setup | ClgOATCutout-En | 1709 | 97
Prop | Templates.Cooling Control | OAT Cooling Cutout Enabled | 1675 | 127 | 7006 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Enable | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Cooling Control | 4 | OAT Cooling Cutout Enabled | UCBapp.newUCB.OAT_Cooling_Cutout_Enabled | Relinquish Default | FALSE |  |  |  | MV:29581 | HR:94 | ADI:29 |  | Value |  |  | Views.Clone.Partial Clone 1 | OAT Cooling Cutout Enabled | 1675 | 127 |  |  | ClgOATCutout-En | 1709 | 97
Prop | Templates.Cooling Control | OAT Cooling Cutout | 1675 | 74 | 7007 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 45 | 0 | 100 |  |  | 1s | 0 | deg C | 507:62 | -18 | 38 | [7 empty] | Attr | York RTU.Cooling Control | 4 | OAT Cooling Cutout | UCBapp.newUCB.OA_Cooling_Lockout_SP | Relinquish Default | FALSE |  |  | York RTU.Unique Equipment Identifier:Present Value = 0 | AV:29582 | HR:21 | ADF:42 |  | Value |  |  | Views.Commissioning.Standard | OAT Cooling Cutout | 1675 | 74 |  | Views.Commission.Standard | ClgOATCutout | 1709 | 98
Prop | Templates.Cooling Control | OAT Cooling Cutout | 1675 | 74 | 7007 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 45 | 0 | 100 |  |  | 1s | 0 | deg C | 507:62 | -18 | 38 | [7 empty] | Attr | York RTU.Cooling Control | 4 | OAT Cooling Cutout | UCBapp.newUCB.OA_Cooling_Lockout_SP | Relinquish Default | FALSE |  |  | York RTU.Unique Equipment Identifier:Present Value = 0 | AV:29582 | HR:21 | ADF:42 |  | Value |  |  | Views.Details.Cooling.Setup | OAT Cooling Cutout | 1675 | 74 |  | Views.Details.Clg.Setup | ClgOATCutout | 1709 | 98
Prop | Templates.Cooling Control | OAT Cooling Cutout | 1675 | 74 | 7007 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 45 | 0 | 100 |  |  | 1s | 0 | deg C | 507:62 | -18 | 38 | [7 empty] | Attr | York RTU.Cooling Control | 4 | OAT Cooling Cutout | UCBapp.newUCB.OA_Cooling_Lockout_SP | Relinquish Default | FALSE |  |  | York RTU.Unique Equipment Identifier:Present Value = 0 | AV:29582 | HR:21 | ADF:42 |  | Value |  |  | Views.Clone.Partial Clone 1 | OAT Cooling Cutout | 1675 | 74 |  |  | ClgOATCutout | 1709 | 98
Prop | Templates.Cooling Control | Economizer Loading Enabled | 1675 | 76 | 7008 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Disable | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Cooling Control | 4 | Economizer Loading Enabled | UCBapp.newUCB.Economizer_Loading_Enabled | Relinquish Default | FALSE |  |  | York RTU.System Controllers.Econ Controller:Present Value <> Not Present | MV:29583 | HR:95 | ADI:30 |  | Value |  |  | Views.Details.Economizer.Setup | Economizer Loading Enabled | 1675 | 76 |  | Views.Details.Econ.Setup | EconLoad-En | 1709 | 99
Prop | Templates.Cooling Control | All Compressors Off in Free Cooling | 1675 | 77 | 7009 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | FALSE | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Cooling Control | 4 | All Compressors Off in Free Cooling | UCBapp.newUCB.All_Comp_Off_in_Free_Cooling | Relinquish Default | FALSE |  |  | York RTU.System Controllers.Econ Controller:Present Value <> Not Present | MV:29584 | HR:96 | ADI:31 |  | Value |  |  | Views.Details.Economizer.Setup | All Compressors Off in Free Cooling | 1675 | 77 |  | Views.Details.Econ.Setup | AllCompOff-Econ | 1709 | 100
Prop | Templates.Cooling Control | Low Ambient Cooling Stages 10 on 5 off Setpoint | 1675 | 78 | 7010 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 45 | 0 | 60 |  |  | 1s | 0 | deg C | 507:62 | -18 | 15 | [7 empty] | Attr | York RTU.Cooling Control | 4 | Low Ambient Cooling Stages 10 on 5 off Setpoint | UCBapp.newUCB.Low_Ambient_Setpoint | Relinquish Default | FALSE |  |  |  | AV:29585 | HR:419 | ADF:177 |  | Value |  |  | Views.Details.Cooling.Setup | Low Ambient Cooling Stages 10 on 5 off Setpoint | 1675 | 78 |  | Views.Details.Clg.Setup | LowAmb10On5OffSp | 1709 | 101
Prop | Templates.Cooling Control | Temperature/Humidity (Return) Control Enable | 1675 | 79 | 7011 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Off | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Cooling Control | 4 | Temperature/Humidity (Return) Control Enable | UCBapp.newUCB.Temp_Humidity_Return_Cntrl_En | Relinquish Default | TRUE |  |  |  | MV:29586 | HR:97 | ADI:32 |  | Value |  |  | Views.Details.Cooling.Misc | Temperature/Humidity (Return) Control Enable | 1675 | 79 |  | Views.Details.Clg.Misc | TempHumCtrl-En | 1709 | 102
Prop | Templates.Cooling Control | Temperature/Humidity Setpoint | 1675 | 80 | 7012 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | %RH | 507:29 | 50 | 20 | 80 |  |  | 1s | 0 | %RH | 507:29 | 20 | 80 | [7 empty] | Attr | York RTU.Cooling Control | 4 | Temperature/Humidity Setpoint | UCBapp.newUCB.Temperature_Humidity_SP | Relinquish Default | FALSE |  |  | York RTU.Cooling Control.Temperature/Humidity (Return) Control Enable:Present Value = Yes | AV:29587 | HR:22 | ADF:43 |  | Value |  |  | Views.Details.Cooling.Misc | Temperature/Humidity Setpoint | 1675 | 80 |  | Views.Details.Clg.Misc | TempHum-Sp | 1709 | 103
Prop | Templates.Cooling Control | Maximum Temperature / Humidity Setpoint Offset | 1675 | 81 | 7013 | TRUE | TRUE | FALSE | 4 | Float | 10ths | 5 | delta deg F | 507:120 | 3 | 0 | 5 |  |  | 10ths | 0 | delta deg C | 507:359 | 0 | 3 | [7 empty] | Attr | York RTU.Cooling Control | 4 | Maximum Temperature / Humidity Setpoint Offset | UCBapp.newUCB.Maximum_Temp_Hum_SP_Offset | Relinquish Default | FALSE |  |  | York RTU.Cooling Control.Temperature/Humidity (Return) Control Enable:Present Value = Yes | AV:29588 | HR:23 | ADF:44 |  | Value |  |  | Views.Details.Cooling.Misc | Maximum Temperature / Humidity Setpoint Offset | 1675 | 81 |  | Views.Details.Clg.Misc | MaxTempHumSpOff | 1709 | 104
Prop | Templates.Cooling Control | Temperature / Humidity Value per Degree Offset | 1675 | 82 | 7014 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | %RH | 507:29 | 5 | 1 | 10 |  |  | 1s | 0 | %RH | 507:29 | 1 | 10 | [7 empty] | Attr | York RTU.Cooling Control | 4 | Temperature / Humidity Value per Degree Offset | UCBapp.newUCB.Temp_Hum_Value_per_Deg_Offset | Relinquish Default | FALSE |  |  | York RTU.Cooling Control.Temperature/Humidity (Return) Control Enable:Present Value = Yes | AV:29589 | HR:24 | ADF:45 |  | Value |  |  | Views.Details.Cooling.Misc | Temperature / Humidity Value per Degree Offset | 1675 | 82 |  | Views.Details.Clg.Misc | TempHumValPerDegOff | 1709 | 105
Prop | Templates.Cooling Control | SAT Limit for Cooling Enable | 1675 | 143 | 7015 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | TRUE | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Cooling Control | 4 | SAT Limit for Cooling Enable | UCBapp.newUCB.SAT_Limit_for_Cooling_Enable | Relinquish Default | FALSE |  |  |  | MV:29590 | HR:98 | ADI:33 |  | Value |  |  | Views.Commissioning.Standard | SAT Limit for Cooling Enable | 1675 | 143 |  | Views.Commission.Standard | SATCoolLimit-En | 1709 | 106
Prop | Templates.Cooling Control | SAT Limit for Cooling Enable | 1675 | 143 | 7015 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | TRUE | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Cooling Control | 4 | SAT Limit for Cooling Enable | UCBapp.newUCB.SAT_Limit_for_Cooling_Enable | Relinquish Default | FALSE |  |  |  | MV:29590 | HR:98 | ADI:33 |  | Value |  |  | Views.Details.Cooling.Setup | SAT Limit for Cooling Enable | 1675 | 143 |  | Views.Details.Clg.Setup | SATCoolLimit-En | 1709 | 106
Prop | Templates.Cooling Control | SAT Limit for Cooling Enable | 1675 | 143 | 7015 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | TRUE | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Cooling Control | 4 | SAT Limit for Cooling Enable | UCBapp.newUCB.SAT_Limit_for_Cooling_Enable | Relinquish Default | FALSE |  |  |  | MV:29590 | HR:98 | ADI:33 |  | Value |  |  | Views.Clone.Partial Clone 1 | SAT Limit for Cooling Enable | 1675 | 143 |  |  | SATCoolLimit-En | 1709 | 106
Prop | Templates.Cooling Control | SAT Limit for Cooling Setpoint | 1675 | 75 | 7016 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 45 | 40 | 65 |  |  | 1s | 0 | deg C | 507:62 | 4 | 18 | [7 empty] | Attr | York RTU.Cooling Control | 4 | SAT Limit for Cooling Setpoint | UCBapp.newUCB.Excessive_SAT_Setpoint | Relinquish Default | FALSE |  |  |  | AV:29591 | HR:25 | ADF:46 |  | Value |  |  | Views.Commissioning.Standard | SAT Limit for Cooling Setpoint | 1675 | 75 |  | Views.Commission.Standard | SATCoolLimit-Sp | 1709 | 107
Prop | Templates.Cooling Control | SAT Limit for Cooling Setpoint | 1675 | 75 | 7016 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 45 | 40 | 65 |  |  | 1s | 0 | deg C | 507:62 | 4 | 18 | [7 empty] | Attr | York RTU.Cooling Control | 4 | SAT Limit for Cooling Setpoint | UCBapp.newUCB.Excessive_SAT_Setpoint | Relinquish Default | FALSE |  |  |  | AV:29591 | HR:25 | ADF:46 |  | Value |  |  | Views.Details.Cooling.Setup | SAT Limit for Cooling Setpoint | 1675 | 75 |  | Views.Details.Clg.Setup | SATCoolLimit-Sp | 1709 | 107
Prop | Templates.Cooling Control | SAT Limit for Cooling Setpoint | 1675 | 75 | 7016 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 45 | 40 | 65 |  |  | 1s | 0 | deg C | 507:62 | 4 | 18 | [7 empty] | Attr | York RTU.Cooling Control | 4 | SAT Limit for Cooling Setpoint | UCBapp.newUCB.Excessive_SAT_Setpoint | Relinquish Default | FALSE |  |  |  | AV:29591 | HR:25 | ADF:46 |  | Value |  |  | Views.Clone.Partial Clone 1 | SAT Limit for Cooling Setpoint | 1675 | 75 |  |  | SATCoolLimit-Sp | 1709 | 107
Prop | Templates.Cooling Control | Freeze Condition Setpoint | 1675 | 99 | 7017 | TRUE | TRUE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | 26 | 20 | 32 |  |  | 10ths | 0 | deg C | 507:62 | -7 | 0 | [7 empty] | Attr | York RTU.Cooling Control | 4 | Freeze Condition Setpoint | UCBapp.newUCB.Freeze_Stat_Setpoint | Relinquish Default | FALSE |  |  |  | AV:29592 | HR:420 | ADF:178 |  | Value |  |  | Views.Details.Cooling.Setup | Freeze Condition Setpoint | 1675 | 99 |  | Views.Details.Clg.Setup | Freeze-Sp | 1709 | 108
Prop | Templates.Cooling Control | Condenser Fan 1 | 1675 | 128 | 7018 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [6 empty] | 647 | 0 = Off 1 = On |  | Attr | York RTU.Cooling Control | 4 | Condenser Fan 1 | UCBapp.newUCB.CF1_C | Present Value | FALSE |  |  |  | MV:29593 | IR:309 | BO:3 |  | Value |  |  | Views.Details.Cooling.Service.Unit | Condenser Fan 1 | 1675 | 128 |  | Views.Details.Clg.Service.Unit | CN-Fan | 1709 | 109
Prop | Templates.Cooling Control | Condenser Fan 2 | 1675 | 129 | 7019 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [6 empty] | 647 | 0 = Off 1 = On |  | Attr | York RTU.Cooling Control | 4 | Condenser Fan 2 | FourStageApp.FourStage.CF2_C | Present Value | FALSE |  |  | York RTU.System Controllers.4 Stage Controller:Present Value <> Not Present | MV:29594 | IR:310 | BO:4 |  | Value |  |  | Views.Details.Cooling.Service.Unit | Condenser Fan 2 | 1675 | 129 |  | Views.Details.Clg.Service.Unit | CF2 | 1709 | 110
Prop | Templates.Cooling Control | Unit Type | 1675 | 130 | 7020 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | SE RTU Equipment Type | 1685 | Package_Cool | [6 empty] | SE RTU Equipment Type | 1685 | [6 empty] | 1685 | 0 = Not Used 1 = Package Cool 2 = Package HP 3 = Split Cool ... |  | Attr | York RTU.Cooling Control | 4 | Unit Type | FDDApp.FDD.UNIT_TYPE | Relinquish Default | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | MV:29595 | HR:403 | ADI:122 |  | Value |  |  | Views.Controller.FDD | Unit Type | 1675 | 130 |  | Views.Controller.FDD | UnitType | 1709 | 111
Prop | Templates.Cooling Control | EER | 1675 | 131 | 7021 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 |  | 507:95 | 10.8 | 0 | 20 |  |  | 1s | 0 |  | 507:95 | 0 | 20 | [7 empty] | Attr | York RTU.Cooling Control | 4 | EER | FDDApp.FDD.EER | Relinquish Default | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | AV:29596 | HR:404 | ADF:175 |  | Value |  |  | Views.Controller.FDD | EER | 1675 | 131 |  | Views.Controller.FDD | EER | 1709 | 112
Prop | Templates.Cooling Control | Subcooling Goal | 1675 | 132 | 7022 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 10 | -10 | 20 |  |  | 1s | 0 | deg C | 507:62 | -23 | -6 | [7 empty] | Attr | York RTU.Cooling Control | 4 | Subcooling Goal | FDDApp.FDD.SUBCOOLING_GOAL_VALUE | Relinquish Default | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | AV:29597 | HR:421 | ADF:179 |  | Value |  |  | Views.Controller.FDD | Subcooling Goal | 1675 | 132 |  | Views.Controller.FDD | SubcoolGoal | 1709 | 113
Prop | Templates.Cooling Control | Refrigerant Type | 1675 | 133 | 7023 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | SE RTU Refrigerant Type | 1682 | R454B | [6 empty] | SE RTU Refrigerant Type | 1682 | [6 empty] | 1682 | 0 = R22 1 = R12 2 = R500 3 = R134A ... |  | Attr | York RTU.Cooling Control | 4 | Refrigerant Type | UCBapp.newUCB.Refrigerant_Type_Src | Relinquish Default | FALSE |  |  |  | MV:29598 | IR:405 | ADI:123 |  | Value |  |  | Views.Controller.FDD | Refrigerant Type | 1675 | 133 |  | Views.Controller.FDD | RefrigType | 1709 | 114
Prop | Templates.Cooling Control | High Side Port Location | 1675 | 134 | 7024 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | SE RTU High Side Port | 1681 | Discharge | [6 empty] | SE RTU High Side Port | 1681 | [6 empty] | 1681 | 0 = Liquid 1 = Discharge |  | Attr | York RTU.Cooling Control | 4 | High Side Port Location | FDDApp.FDD.HIGH_SIDE_PORT_LOCATION | Relinquish Default | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | MV:29599 | HR:422 | ADI:135 |  | Value |  |  | Views.Controller.FDD | High Side Port Location | 1675 | 134 |  | Views.Controller.FDD | HiSidePortLoc | 1709 | 115
Prop | Templates.Cooling Control | Evaporator Coil Type | 1675 | 101 | 7025 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Cooling Coil Type | 1722 | [7 empty] | Cooling Coil Type | 1722 | [6 empty] | 1722 | 0 = MicroChannel 1 = Tube and Fin |  | Attr | York RTU.Cooling Control | 4 | Evaporator Coil Type | EM Variable: 0 |  | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | MV:29600 | HR:406 | ADI:124 |  | Value |  |  | Views.Controller.FDD | Evaporator Coil Type | 1675 | 101 |  | Views.Controller.FDD | EvapCoil-Type | 1709 | 116
Prop | Templates.Cooling Control | Condenser Coil Type | 1675 | 103 | 7026 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Cooling Coil Type | 1722 | [7 empty] | Cooling Coil Type | 1722 | [6 empty] | 1722 | 0 = MicroChannel 1 = Tube and Fin |  | Attr | York RTU.Cooling Control | 4 | Condenser Coil Type | EM Variable: 0 |  | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | MV:29601 | HR:423 | ADI:136 |  | Value |  |  | Views.Controller.FDD | Condenser Coil Type | 1675 | 103 |  | Views.Controller.FDD | CondCoil-Type | 1709 | 117
Prop | Templates.Cooling Control | Indoor Metering Device Type | 1675 | 135 | 7027 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | SE RTU Expansion Device | 1684 | TxV | [6 empty] | SE RTU Expansion Device | 1684 | [6 empty] | 1684 | 0 = TxV 1 = FO 2 = TxV Or FO 3 = n |  | Attr | York RTU.Cooling Control | 4 | Indoor Metering Device Type | FDDApp.FDD.INDOOR_EXPANSION_DEVICE_TYPE | Relinquish Default | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | MV:29602 | HR:424 | ADI:137 |  | Value |  |  | Views.Controller.FDD | Indoor Metering Device Type | 1675 | 135 |  | Views.Controller.FDD | InMeterDev-Type | 1709 | 118
Prop | Templates.Cooling Control | Outdoor Metering Device Type | 1675 | 136 | 7028 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | SE RTU Expansion Device | 1684 | n | [6 empty] | SE RTU Expansion Device | 1684 | [6 empty] | 1684 | 0 = TxV 1 = FO 2 = TxV Or FO 3 = n |  | Attr | York RTU.Cooling Control | 4 | Outdoor Metering Device Type | FDDApp.FDD.OUTDOOR_EXPANSION_DEVICE_TYPE | Relinquish Default | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | MV:29603 | HR:425 | ADI:138 |  | Value |  |  | Views.Controller.FDD | Outdoor Metering Device Type | 1675 | 136 |  | Views.Controller.FDD | OutMeterDev-Type | 1709 | 445
Prop | Templates.Cooling Control | VAV Cooling Supply Air Temp Upper Setpoint | 1675 | 137 | 7029 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 60 | 41 | 70 |  |  | 1s | 0 | deg C | 507:62 | 5 | 21 | [7 empty] | Attr | York RTU.Cooling Control | 4 | VAV Cooling Supply Air Temp Upper Setpoint | UCBapp.newUCB.Upper_SAT_Clg_Setpoint | Relinquish Default | FALSE |  |  |  | AV:29604 | HR:26 | ADF:47 |  | Value |  |  | Views.Details.FanVFD.Setup | VAV Cooling Supply Air Temp Upper Setpoint | 1675 | 137 |  | Views.Details.FanVFD.Setup | SATUp-Sp | 1709 | 119
Prop | Templates.Cooling Control | VAV Cooling Supply Air Temp Upper Setpoint | 1675 | 137 | 7029 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 60 | 41 | 70 |  |  | 1s | 0 | deg C | 507:62 | 5 | 21 | [7 empty] | Attr | York RTU.Cooling Control | 4 | VAV Cooling Supply Air Temp Upper Setpoint | UCBapp.newUCB.Upper_SAT_Clg_Setpoint | Relinquish Default | FALSE |  |  |  | AV:29604 | HR:26 | ADF:47 |  | Value |  |  | Views.Details.Single Zone VAV.Setup | VAV Cooling Supply Air Temp Upper Setpoint | 1675 | 137 |  | Views.Details.SZ VAV.Setup | SATUp-Sp | 1709 | 119
Prop | Templates.Cooling Control | VAV Cooling Supply Air Temp Upper Setpoint | 1675 | 137 | 7029 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 60 | 41 | 70 |  |  | 1s | 0 | deg C | 507:62 | 5 | 21 | [7 empty] | Attr | York RTU.Cooling Control | 4 | VAV Cooling Supply Air Temp Upper Setpoint | UCBapp.newUCB.Upper_SAT_Clg_Setpoint | Relinquish Default | FALSE |  |  |  | AV:29604 | HR:26 | ADF:47 |  | Value |  |  | Views.Clone.Partial Clone 1 | VAV Cooling Supply Air Temp Upper Setpoint | 1675 | 137 |  |  | SATUp-Sp | 1709 | 119
Prop | Templates.Cooling Control | VAV Cooling Supply Air Temp Lower Setpoint | 1675 | 138 | 7030 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 55 | 40 | 69 |  |  | 1s | 0 | deg C | 507:62 | 4 | 20 | [7 empty] | Attr | York RTU.Cooling Control | 4 | VAV Cooling Supply Air Temp Lower Setpoint | UCBapp.newUCB.Lower_SAT_Clg_Setpoint | Relinquish Default | FALSE |  |  |  | AV:29605 | HR:27 | ADF:48 |  | Value |  |  | Views.Details.FanVFD.Setup | VAV Cooling Supply Air Temp Lower Setpoint | 1675 | 138 |  | Views.Details.FanVFD.Setup | SATLo-Sp | 1709 | 120
Prop | Templates.Cooling Control | VAV Cooling Supply Air Temp Lower Setpoint | 1675 | 138 | 7030 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 55 | 40 | 69 |  |  | 1s | 0 | deg C | 507:62 | 4 | 20 | [7 empty] | Attr | York RTU.Cooling Control | 4 | VAV Cooling Supply Air Temp Lower Setpoint | UCBapp.newUCB.Lower_SAT_Clg_Setpoint | Relinquish Default | FALSE |  |  |  | AV:29605 | HR:27 | ADF:48 |  | Value |  |  | Views.Details.Single Zone VAV.Setup | VAV Cooling Supply Air Temp Lower Setpoint | 1675 | 138 |  | Views.Details.SZ VAV.Setup | SATLo-Sp | 1709 | 120
Prop | Templates.Cooling Control | VAV Cooling Supply Air Temp Lower Setpoint | 1675 | 138 | 7030 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 55 | 40 | 69 |  |  | 1s | 0 | deg C | 507:62 | 4 | 20 | [7 empty] | Attr | York RTU.Cooling Control | 4 | VAV Cooling Supply Air Temp Lower Setpoint | UCBapp.newUCB.Lower_SAT_Clg_Setpoint | Relinquish Default | FALSE |  |  |  | AV:29605 | HR:27 | ADF:48 |  | Value |  |  | Views.Clone.Partial Clone 1 | VAV Cooling Supply Air Temp Lower Setpoint | 1675 | 138 |  |  | SATLo-Sp | 1709 | 120
Prop | Templates.Cooling Control | VAV Cooling Supply Air Temp Lower Setpoint | 1675 | 138 | 7030 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 55 | 40 | 69 |  |  | 1s | 0 | deg C | 507:62 | 4 | 20 | [7 empty] | Attr | York RTU.Cooling Control | 4 | VAV Cooling Supply Air Temp Lower Setpoint | UCBapp.newUCB.Lower_SAT_Clg_Setpoint | Relinquish Default | FALSE |  |  |  | AV:29605 | HR:27 | ADF:48 |  | Value |  |  | Views.Details.Verasys | VAV Cooling Supply Air Temp Lower Setpoint | 1675 | 138 |  | Views.Details.Verasys | SATLo-Sp | 1709 | 120
Prop | Templates.Cooling Control | VAV Supply Air Temp Reset Setpoint | 1675 | 139 | 7031 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 72 | 40 | 85 |  |  | 1s | 0 | deg C | 507:62 | 4 | 30 | [7 empty] | Attr | York RTU.Cooling Control | 4 | VAV Supply Air Temp Reset Setpoint | UCBapp.newUCB.VAV_Supply_Air_Temp_Reset_SP | Relinquish Default | FALSE |  |  | UCBapp.newUCB.Setpoint_Input_Presence:Present Value = Curve 2 | AV:29606 | HR:28 | ADF:49 |  | Value |  |  | Views.Details.FanVFD.Setup | VAV Supply Air Temp Reset Setpoint | 1675 | 139 |  | Views.Details.FanVFD.Setup | SATRst-Sp | 1709 | 121
Prop | Templates.Cooling Control | VAV Supply Air Temp Reset Setpoint | 1675 | 139 | 7031 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 72 | 40 | 85 |  |  | 1s | 0 | deg C | 507:62 | 4 | 30 | [7 empty] | Attr | York RTU.Cooling Control | 4 | VAV Supply Air Temp Reset Setpoint | UCBapp.newUCB.VAV_Supply_Air_Temp_Reset_SP | Relinquish Default | FALSE |  |  | UCBapp.newUCB.Setpoint_Input_Presence:Present Value = Curve 2 | AV:29606 | HR:28 | ADF:49 |  | Value |  |  | Views.Clone.Partial Clone 1 | VAV Supply Air Temp Reset Setpoint | 1675 | 139 |  |  | SATRst-Sp | 1709 | 121
Prop | Templates.Cooling Control | VAV Operating Cooling Setpoint | 1675 | 1679 | 7032 | TRUE | FALSE | FALSE | 4 | Float | 100ths | 4 | deg F | 507:64 | 72 |  |  |  |  | 100ths | 0 | deg C | 507:62 | [5 empty] | Alternate Cooling Setpoint |  |  |  | Attr | York RTU.Cooling Control | 4 | VAV Operating Cooling Setpoint | UCBapp.newUCB.Operating_Cooling_Setpoint | Present Value | FALSE |  |  | UCBapp.newUCB.Setpoint_Input_Presence:Present Value >= Curve 2 | AV:29607 | IR:160 | ADF:50 |  | Value |  |  | Views.Details.Cooling.Service.Unit | VAV Operating Cooling Setpoint | 1675 | 1679 |  | Views.Details.Clg.Service.Unit | OprVAVClg-Sp | 1709 | 122
Prop | Templates.Cooling Control | CV Occupied Cooling Setpoint | 1675 | 141 | 7033 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 72 | 45 | 98 |  |  | 1s | 0 | deg C | 507:62 | 7 | 36 |  |  |  | Occupied Cooling Setpoint |  |  |  | Attr | York RTU.Cooling Control | 4 | CV Occupied Cooling Setpoint | UCBapp.newUCB.Occ_Clg_Setpoint | Relinquish Default | FALSE |  |  | UCBapp.newUCB.Setpoint_Input_Presence:Present Value = Curve 1 | AV:29608 | HR:29 | ADF:51 |  | Value |  |  | Views.Details.Cooling.Setup | CV Occupied Cooling Setpoint | 1675 | 141 |  | Views.Details.Clg.Setup | ClgOcc-Sp | 1709 | 123
Prop | Templates.Cooling Control | CV Occupied Cooling Setpoint | 1675 | 141 | 7033 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 72 | 45 | 98 |  |  | 1s | 0 | deg C | 507:62 | 7 | 36 |  |  |  | Occupied Cooling Setpoint |  |  |  | Attr | York RTU.Cooling Control | 4 | CV Occupied Cooling Setpoint | UCBapp.newUCB.Occ_Clg_Setpoint | Relinquish Default | FALSE |  |  | UCBapp.newUCB.Setpoint_Input_Presence:Present Value = Curve 1 | AV:29608 | HR:29 | ADF:51 |  | Value |  |  | Views.Details.Cooling.Misc | CV Occupied Cooling Setpoint | 1675 | 141 |  | Views.Details.Clg.Misc | ClgOcc-Sp | 1709 | 123
Prop | Templates.Cooling Control | CV Occupied Cooling Setpoint | 1675 | 141 | 7033 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 72 | 45 | 98 |  |  | 1s | 0 | deg C | 507:62 | 7 | 36 |  |  |  | Occupied Cooling Setpoint |  |  |  | Attr | York RTU.Cooling Control | 4 | CV Occupied Cooling Setpoint | UCBapp.newUCB.Occ_Clg_Setpoint | Relinquish Default | FALSE |  |  | UCBapp.newUCB.Setpoint_Input_Presence:Present Value = Curve 1 | AV:29608 | HR:29 | ADF:51 |  | Value |  |  | Views.Clone.Partial Clone 1 | CV Occupied Cooling Setpoint | 1675 | 141 |  |  | ClgOcc-Sp | 1709 | 123
Prop | Templates.Cooling Control | CV Unoccupied Cooling Setpoint | 1675 | 142 | 7034 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 85 | 46 | 99 |  |  | 1s | 0 | deg C | 507:62 | 8 | 37 |  |  |  | Unoccupied Cooling Setpoint |  |  |  | Attr | York RTU.Cooling Control | 4 | CV Unoccupied Cooling Setpoint | UCBapp.newUCB.Unocc_Clg_Setpoint | Relinquish Default | FALSE |  |  | UCBapp.newUCB.Setpoint_Input_Presence:Present Value = Curve 1 | AV:29609 | HR:30 | ADF:52 |  | Value |  |  | Views.Details.Cooling.Setup | CV Unoccupied Cooling Setpoint | 1675 | 142 |  | Views.Details.Clg.Setup | ClgUnocc-Sp | 1709 | 124
Prop | Templates.Cooling Control | CV Unoccupied Cooling Setpoint | 1675 | 142 | 7034 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 85 | 46 | 99 |  |  | 1s | 0 | deg C | 507:62 | 8 | 37 |  |  |  | Unoccupied Cooling Setpoint |  |  |  | Attr | York RTU.Cooling Control | 4 | CV Unoccupied Cooling Setpoint | UCBapp.newUCB.Unocc_Clg_Setpoint | Relinquish Default | FALSE |  |  | UCBapp.newUCB.Setpoint_Input_Presence:Present Value = Curve 1 | AV:29609 | HR:30 | ADF:52 |  | Value |  |  | Views.Clone.Partial Clone 1 | CV Unoccupied Cooling Setpoint | 1675 | 142 |  |  | ClgUnocc-Sp | 1709 | 124
Prop | Templates.Cooling Control | CV Operating Cooling Setpoint | 1675 | 144 | 7035 | TRUE | FALSE | FALSE | 4 | Float | 100ths | 4 | deg F | 507:64 | 72 |  |  |  |  | 100ths | 0 | deg C | 507:62 | [5 empty] | Cooling Setpoint |  |  |  | Attr | York RTU.Cooling Control | 4 | CV Operating Cooling Setpoint | UCBapp.newUCB.Operating_Cooling_Setpoint | Present Value | FALSE |  |  | UCBapp.newUCB.Opr_Setpoint_Presence:Present Value = Curve 1 | AV:29610 | IR:161 | ADF:53 |  | Value |  |  | Views.Details.Cooling.Service.Unit | CV Operating Cooling Setpoint | 1675 | 144 |  | Views.Details.Clg.Service.Unit | OprCVClg-Sp | 1709 | 125
Prop | Templates.Cooling Control | CV Operating Cooling Setpoint | 1675 | 144 | 7035 | TRUE | FALSE | FALSE | 4 | Float | 100ths | 4 | deg F | 507:64 | 72 |  |  |  |  | 100ths | 0 | deg C | 507:62 | [5 empty] | Cooling Setpoint |  |  |  | Attr | York RTU.Cooling Control | 4 | CV Operating Cooling Setpoint | UCBapp.newUCB.Operating_Cooling_Setpoint | Present Value | FALSE |  |  | UCBapp.newUCB.Opr_Setpoint_Presence:Present Value = Curve 1 | AV:29610 | IR:161 | ADF:53 |  | Value |  |  | Views.Details.Cooling.Misc | CV Operating Cooling Setpoint | 1675 | 144 |  | Views.Details.Clg.Misc | OprCVClg-Sp | 1709 | 125
Prop | Templates.Cooling Control | CV Operating Cooling Setpoint | 1675 | 144 | 7035 | TRUE | FALSE | FALSE | 4 | Float | 100ths | 4 | deg F | 507:64 | 72 |  |  |  |  | 100ths | 0 | deg C | 507:62 | [5 empty] | Cooling Setpoint |  |  |  | Attr | York RTU.Cooling Control | 4 | CV Operating Cooling Setpoint | UCBapp.newUCB.Operating_Cooling_Setpoint | Present Value | FALSE |  |  | UCBapp.newUCB.Opr_Setpoint_Presence:Present Value = Curve 1 | AV:29610 | IR:161 | ADF:53 |  | Value |  |  | Views.Details.Hot Gas Reheat.Service | CV Operating Cooling Setpoint | 1675 | 144 |  | Views.Details.HGR.Service | OprCVClg-Sp | 1709 | 125
Prop | Templates.Cooling Control | CV Operating Cooling Setpoint | 1675 | 144 | 7035 | TRUE | FALSE | FALSE | 4 | Float | 100ths | 4 | deg F | 507:64 | 72 |  |  |  |  | 100ths | 0 | deg C | 507:62 | [5 empty] | Cooling Setpoint |  |  |  | Attr | York RTU.Cooling Control | 4 | CV Operating Cooling Setpoint | UCBapp.newUCB.Operating_Cooling_Setpoint | Present Value | FALSE |  |  | UCBapp.newUCB.Opr_Setpoint_Presence:Present Value = Curve 1 | AV:29610 | IR:161 | ADF:53 |  | Value |  |  | Views.Details.Mod Hot Gas Reheat.Service | CV Operating Cooling Setpoint | 1675 | 144 |  | Views.Details.ModHGR.Service | OprCVClg-Sp | 1709 | 125
Prop | Templates.Cooling Control | Excessive Supply Air Cooling Fault | 1675 | 345 | 7036 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | SE RTU Excessive SAT State | 1644 | Normal | [6 empty] | SE RTU Excessive SAT State | 1644 | [6 empty] | 1644 | 0 = Normal 1 = Drop Stage 2 = Wait 3 = SAT Unreliable |  | Attr | York RTU.Cooling Control | 4 | Excessive Supply Air Cooling Fault | UCBapp.newUCB.Excessive_SA_Cooling_Fault | Present Value | FALSE
Prop | Templates.Cooling Control | Cooling Lockout due to Low Outdoor Air Temp | 1675 | 346 | 7037 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | FALSE | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Cooling Control | 4 | Cooling Lockout due to Low Outdoor Air Temp | UCBapp.newUCB.OAT_Cooling_Cutout_En | Present Value | FALSE
Prop | Templates.Cooling Control | Unit Capacity | 1675 | 371 | 7038 | TRUE | TRUE | FALSE | 4 | Float | 10ths | 5 | tons refr | 507:52 | 0 | 0 | 130 |  |  | 10ths | 0 | kW | 507:48 | 0 | 460 | [7 empty] | Attr | York RTU.Cooling Control | 4 | Unit Capacity | FDDApp.FDD.UNIT_CAPACITY | Relinquish Default | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | AV:29886 | HR:407 | ADF:176 |  | Value |  |  | Views.Controller.FDD | Unit Capacity | 1675 | 371 |  | Views.Controller.FDD | UnitCap | 1709 | 482
Prop | Templates.Cooling Control | Fan Power | 1675 | 372 | 7039 | TRUE | TRUE | FALSE | 4 | Float | 10ths | 5 | kW | 507:48 | 0 | 0 | 19 |  |  | 10ths | 0 | kW | 507:48 | 0 | 19 | [7 empty] | Attr | York RTU.Cooling Control | 4 | Fan Power | FDDApp.FDD.FAN_POWER | Relinquish Default | FALSE |  |  | York RTU.System Controllers.FDD Manager Controller:Present Value = Not Present | AV:29887 | HR:426 | ADF:180 |  | Value |  |  | Views.Controller.FDD | Fan Power | 1675 | 372 |  | Views.Controller.FDD | FanPower | 1709 | 483
Prop | Templates.Cooling Control | Super Heat Goal | 1675 | 373 | 7040 | TRUE | TRUE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | 0 | 10 | 30 |  |  | 10ths | 0 | deg C | 507:62 | -12.2 | -1.1 | [7 empty] | Attr | York RTU.Cooling Control | 4 | Super Heat Goal | FDDApp.FDD.SUPER_HEAT_GOAL | Relinquish Default | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | AV:29888 | HR:427 | ADF:181 |  | Value |  |  | Views.Controller.FDD | Super Heat Goal | 1675 | 373 |  | Views.Controller.FDD | SuperHeatGoal | 1709 | 484
Prop | Templates.Cooling Control | Altitude | 1675 | 374 | 7041 | TRUE | TRUE | FALSE | 4 | Float | 10ths | 5 | ft | 507:33 | 0 | -1500 | 30000 |  |  | 10ths | 0 | m | 507:31 | -457.2 | 9144 | [7 empty] | Attr | York RTU.Cooling Control | 4 | Altitude | FDDApp.FDD.ALTITUDE | Relinquish Default | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | AV:29889 | HR:31 | ADF:54 |  | Value |  |  | Views.Controller.FDD | Altitude | 1675 | 374 |  | Views.Controller.FDD | Altitude | 1709 | 485
Prop | Templates.Cooling Control | Cooling Adaptive Tuning Enable | 1675 | 486 | 7043 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Disable | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Cooling Control | 4 | Cooling Adaptive Tuning Enable | UCBapp.newUCB.Cooling_Adaptive_Tuning_En | Relinquish Default | FALSE |  |  |  | MV:29882 | HR:100 | ADI:35 |  | Value |  |  | Views.Details.Cooling.Setup | Cooling Adaptive Tuning Enable | 1675 | 486 |  | Views.Details.Clg.Setup | ClgAdapTunEn | 1709 | 617
Prop | Templates.Cooling Control | Number of Refrig Systems Installed | 1675 | 495 | 7044 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 |  | 507:95 | 4 | 0 | 4 |  |  | 1s | 0 |  | 507:95 | 0 | 4 | [7 empty] | Attr | York RTU.Cooling Control | 4 | Number of Refrig Systems Installed | UCBapp.newUCB.Num_of_Refrigeration_Cycles | Relinquish Default | FALSE |  |  |  | AV:29890 | HR:32 | ADF:55 |  | Value |  |  | Views.Commissioning.Options | Number of Refrig Systems Installed | 1675 | 495 |  | Views.Commission.Options | #RefrigSys | 1709 | 627
Prop | Templates.Cooling Control | Number of Refrig Systems Installed | 1675 | 495 | 7044 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 |  | 507:95 | 4 | 0 | 4 |  |  | 1s | 0 |  | 507:95 | 0 | 4 | [7 empty] | Attr | York RTU.Cooling Control | 4 | Number of Refrig Systems Installed | UCBapp.newUCB.Num_of_Refrigeration_Cycles | Relinquish Default | FALSE |  |  |  | AV:29890 | HR:32 | ADF:55 |  | Value |  |  | Views.Commissioning.Quick Start | Number of Refrig Systems Installed | 1675 | 495 |  | Views.Commission.Quick Start | #RefrigSys | 1709 | 627
Prop | Templates.Cooling Control | DAT Cooling Min SP | 1675 | 494 | 7045 | TRUE | TRUE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | 54 | 50 | 60 |  |  | 10ths | 0 | deg C | 507:62 | 9.5 | 15.6 | [7 empty] | Attr | York RTU.Cooling Control | 4 | DAT Cooling Min SP | UCBapp.newUCB.DAT_Cooling_Min_SP | Relinquish Default | FALSE |  |  | York RTU.SZ VAV Enabled:Present Value = On | AV:29907 | HR:74 | ADF:160
Prop | Templates.Cooling Control | Pump Out Enable | 1675 | 619 | 7046 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Disable/Enable | 658 | Disable | [6 empty] | Disable/Enable | 658 | [6 empty] | 658 | 0 = Disable 1 = Enable |  | Attr | York RTU.Cooling Control | 4 | Pump Out Enable | UCBapp.newUCB.Pump_Out_Enable | Relinquish Default | FALSE |  |  |  | MV:29921 | HR:428 | ADI:139 |  | Value |  |  | Views.Details.Cooling.Setup | Pump Out Enable | 1675 | 619 |  | Views.Details.Clg.Setup | PmpOut-En | 1709 | 644
Prop | Templates.Cooling Control | Staged Cooling Command | 1675 | 628 | 7047 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 0 |  |  |  |  | 1s | 0 | % | 507:98 | [9 empty] | Attr | York RTU.Cooling Control | 4 | Staged Cooling Command | UCBapp.newUCB.Staged_Cooling_Command | Present Value | FALSE |  |  |  | AV:29922 | IR:263 | ADF:165 |  | Value |  |  | Views.Details.Cooling.Service.Unit | Staged Cooling Command | 1675 | 628 |  | Views.Details.Clg.Service.Unit | StgClgCmd | 1709 | 648
Prop | Templates.Cooling Control | Staged Cooling Command | 1675 | 628 | 7047 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 0 |  |  |  |  | 1s | 0 | % | 507:98 | [9 empty] | Attr | York RTU.Cooling Control | 4 | Staged Cooling Command | UCBapp.newUCB.Staged_Cooling_Command | Present Value | FALSE |  |  |  | AV:29922 | IR:263 | ADF:165 |  | Value |  |  | Views.Details.FanVFD.Service | Staged Cooling Command | 1675 | 628 |  | Views.Details.FanVFD.Service | StgClgCmd | 1709 | 648
Prop | Templates.Cooling Control | Staged Cooling Command | 1675 | 628 | 7047 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 0 |  |  |  |  | 1s | 0 | % | 507:98 | [9 empty] | Attr | York RTU.Cooling Control | 4 | Staged Cooling Command | UCBapp.newUCB.Staged_Cooling_Command | Present Value | FALSE |  |  |  | AV:29922 | IR:263 | ADF:165 |  | Value |  |  | Views.Details.Hot Gas Reheat.Service | Staged Cooling Command | 1675 | 628 |  | Views.Details.HGR.Service | StgClgCmd | 1709 | 648
Prop | Templates.Cooling Control | Staged Cooling Command | 1675 | 628 | 7047 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 0 |  |  |  |  | 1s | 0 | % | 507:98 | [9 empty] | Attr | York RTU.Cooling Control | 4 | Staged Cooling Command | UCBapp.newUCB.Staged_Cooling_Command | Present Value | FALSE |  |  |  | AV:29922 | IR:263 | ADF:165 |  | Value |  |  | Views.Details.Mod Hot Gas Reheat.Service | Staged Cooling Command | 1675 | 628 |  | Views.Details.ModHGR.Service | StgClgCmd | 1709 | 648
Prop | Templates.Cooling Control | SZ VAV Occupied Cooling Setpoint | 1675 | 644 | 7048 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 72 | 45 | 98 |  |  | 1s | 0 | deg C | 507:62 | 7 | 36 | [7 empty] | Attr | York RTU.Cooling Control | 4 | SZ VAV Occupied Cooling Setpoint | UCBapp.newUCB.Occ_Clg_Setpoint | Relinquish Default | FALSE |  |  | UCBapp.newUCB.Setpoint_Input_Presence:Present Value = Curve 3 | AV:29925 | HR:270 | ADF:169 |  | Value |  |  | Views.Details.Single Zone VAV.Setup | SZ VAV Occupied Cooling Setpoint | 1675 | 644 |  | Views.Details.SZ VAV.Setup | SZVAVClgOcc-Sp | 1709 | 656
Prop | Templates.Cooling Control | SZ VAV Occupied Cooling Setpoint | 1675 | 644 | 7048 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 72 | 45 | 98 |  |  | 1s | 0 | deg C | 507:62 | 7 | 36 | [7 empty] | Attr | York RTU.Cooling Control | 4 | SZ VAV Occupied Cooling Setpoint | UCBapp.newUCB.Occ_Clg_Setpoint | Relinquish Default | FALSE |  |  | UCBapp.newUCB.Setpoint_Input_Presence:Present Value = Curve 3 | AV:29925 | HR:270 | ADF:169 |  | Value |  |  | Views.Clone.Partial Clone 1 | SZ VAV Occupied Cooling Setpoint | 1675 | 644 |  |  | SZVAVClgOcc-Sp | 1709 | 656
Prop | Templates.Cooling Control | SZ VAV Occupied Cooling Setpoint | 1675 | 644 | 7048 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 72 | 45 | 98 |  |  | 1s | 0 | deg C | 507:62 | 7 | 36 | [7 empty] | Attr | York RTU.Cooling Control | 4 | SZ VAV Occupied Cooling Setpoint | UCBapp.newUCB.Occ_Clg_Setpoint | Relinquish Default | FALSE |  |  | UCBapp.newUCB.Setpoint_Input_Presence:Present Value = Curve 3 | AV:29925 | HR:270 | ADF:169 |  | Value |  |  | Views.Details.Cooling.Setup | SZ VAV Occupied Cooling Setpoint | 1675 | 644 |  | Views.Details.Clg.Setup | SZVAVClgOcc-Sp | 1709 | 656
Prop | Templates.Cooling Control | SZ VAV Occupied Cooling Setpoint | 1675 | 644 | 7048 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 72 | 45 | 98 |  |  | 1s | 0 | deg C | 507:62 | 7 | 36 | [7 empty] | Attr | York RTU.Cooling Control | 4 | SZ VAV Occupied Cooling Setpoint | UCBapp.newUCB.Occ_Clg_Setpoint | Relinquish Default | FALSE |  |  | UCBapp.newUCB.Setpoint_Input_Presence:Present Value = Curve 3 | AV:29925 | HR:270 | ADF:169 |  | Value |  |  | Views.Details.Cooling.Misc | SZ VAV Occupied Cooling Setpoint | 1675 | 644 |  | Views.Details.Clg.Misc | SZVAVClgOcc-Sp | 1709 | 656
Prop | Templates.Cooling Control | SZ VAV Unoccupied Cooling Setpoint | 1675 | 646 | 7049 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 85 | 45 | 98 |  |  | 1s | 0 | deg C | 507:62 | 7 | 36 | [7 empty] | Attr | York RTU.Cooling Control | 4 | SZ VAV Unoccupied Cooling Setpoint | UCBapp.newUCB.Unocc_Clg_Setpoint | Relinquish Default | FALSE |  |  | UCBapp.newUCB.Setpoint_Input_Presence:Present Value = Curve 3 | AV:29926 | HR:271 | ADF:170 |  | Value |  |  | Views.Details.Single Zone VAV.Setup | SZ VAV Unoccupied Cooling Setpoint | 1675 | 646 |  | Views.Details.SZ VAV.Setup | SZVAVClgUnocc-Sp | 1709 | 657
Prop | Templates.Cooling Control | SZ VAV Unoccupied Cooling Setpoint | 1675 | 646 | 7049 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 85 | 45 | 98 |  |  | 1s | 0 | deg C | 507:62 | 7 | 36 | [7 empty] | Attr | York RTU.Cooling Control | 4 | SZ VAV Unoccupied Cooling Setpoint | UCBapp.newUCB.Unocc_Clg_Setpoint | Relinquish Default | FALSE |  |  | UCBapp.newUCB.Setpoint_Input_Presence:Present Value = Curve 3 | AV:29926 | HR:271 | ADF:170 |  | Value |  |  | Views.Clone.Partial Clone 1 | SZ VAV Unoccupied Cooling Setpoint | 1675 | 646 |  |  | SZVAVClgUnocc-Sp | 1709 | 657
Prop | Templates.Cooling Control | SZ VAV Unoccupied Cooling Setpoint | 1675 | 646 | 7049 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 85 | 45 | 98 |  |  | 1s | 0 | deg C | 507:62 | 7 | 36 | [7 empty] | Attr | York RTU.Cooling Control | 4 | SZ VAV Unoccupied Cooling Setpoint | UCBapp.newUCB.Unocc_Clg_Setpoint | Relinquish Default | FALSE |  |  | UCBapp.newUCB.Setpoint_Input_Presence:Present Value = Curve 3 | AV:29926 | HR:271 | ADF:170 |  | Value |  |  | Views.Details.Cooling.Setup | SZ VAV Unoccupied Cooling Setpoint | 1675 | 646 |  | Views.Details.Clg.Setup | SZVAVClgUnocc-Sp | 1709 | 657
Prop | Templates.Cooling Control | SZ VAV Operating Cooling Setpoint | 1675 | 648 | 7050 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 55 |  |  |  |  | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control | 4 | SZ VAV Operating Cooling Setpoint | UCBapp.newUCB.SZVAV_Cascaded_DAT_Sp_Clg | Present Value | FALSE |  |  | UCBapp.newUCB.Opr_Setpoint_Presence:Present Value = Curve 3 | AV:30077 | IR:266 | ADF:197 | DAT setpoint | Value |  |  | Views.Details.Single Zone VAV.Service | VAV Operating Cooling Supply Air Temp Setpoint | 1675 | 140 |  | Views.Details.SZ VAV.Service | OprSZVAVClg-Sp | 1709 | 660
Prop | Templates.Cooling Control | SZ VAV Operating Cooling Setpoint | 1675 | 648 | 7050 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 55 |  |  |  |  | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control | 4 | SZ VAV Operating Cooling Setpoint | UCBapp.newUCB.SZVAV_Cascaded_DAT_Sp_Clg | Present Value | FALSE |  |  | UCBapp.newUCB.Opr_Setpoint_Presence:Present Value = Curve 3 | AV:30077 | IR:266 | ADF:197 | DAT setpoint | Value |  |  | Views.Details.Cooling.Misc | VAV Operating Cooling Supply Air Temp Setpoint | 1675 | 140 |  | Views.Details.Clg.Misc | OprSZVAVClg-Sp | 1709 | 660
Prop | Templates.Cooling Control | SZ VAV Operating Cooling Setpoint | 1675 | 648 | 7050 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 55 |  |  |  |  | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control | 4 | SZ VAV Operating Cooling Setpoint | UCBapp.newUCB.SZVAV_Cascaded_DAT_Sp_Clg | Present Value | FALSE |  |  | UCBapp.newUCB.Opr_Setpoint_Presence:Present Value = Curve 3 | AV:30077 | IR:266 | ADF:197 | DAT setpoint | Value |  |  | Views.Details.FanVFD.Service | VAV Operating Cooling Supply Air Temp Setpoint | 1675 | 140 |  | Views.Details.FanVFD.Service | OprVAVClg-Sp | 1709 | 122
Prop | Templates.Cooling Control | Low Ambient Enabled | 1675 | 649 | 7051 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Enable | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Cooling Control | 4 | Low Ambient Enabled | UCBapp.newUCB.Low_Ambient_Enabled | Relinquish Default | FALSE |  |  |  | MV:29928 | HR:429 | ADI:140 |  | Value |  |  | Views.Commissioning.Options | Low Ambient Enabled | 1675 | 649 |  | Views.Commission.Options | LowAmb-En | 1709 | 662
Prop | Templates.Cooling Control | Low Ambient Enabled | 1675 | 649 | 7051 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Enable | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Cooling Control | 4 | Low Ambient Enabled | UCBapp.newUCB.Low_Ambient_Enabled | Relinquish Default | FALSE |  |  |  | MV:29928 | HR:429 | ADI:140 |  | Value |  |  | Views.Details.Cooling.Setup | Low Ambient Enabled | 1675 | 649 |  | Views.Details.Clg.Setup | LowAmb-En | 1709 | 662
Prop | Templates.Cooling Control | VAV Unoccupied Cooling Setpoint | 1675 | 740 | 7052 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 85 | 46 | 99 |  |  | 1s | 0 | deg C | 507:62 | 8 | 37 | [7 empty] | Attr | York RTU.Cooling Control | 4 | VAV Unoccupied Cooling Setpoint | UCBapp.newUCB.Unocc_Clg_Setpoint | Relinquish Default | FALSE |  |  | York RTU.Fan Control.Fan Control Type:Present Value = Variable Speed | AV:29932 |  | ADF:168 |  | Value |  |  | Views.Details.FanVFD.Setup | VAV Unoccupied Cooling Setpoint | 1675 | 740 |  | Views.Details.FanVFD.Setup | VAVClgUnocc-Sp | 1709 | 663
Prop | Templates.Cooling Control | SZ VAV Cooling Load | 1675 | 744 | 7053 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | % | 507:98 | 0 |  |  |  |  | 10ths | 0 | % | 507:98 | [9 empty] | Attr | York RTU.Cooling Control | 4 | SZ VAV Cooling Load | UCBapp.newUCB.SZ_VAV_Cooling_Load | Present Value | FALSE |  |  | York RTU.SZ VAV Enabled:Present Value = On | AV:29935 | IR:438 | ADF:186 |  | Value |  |  | Views.Details.Single Zone VAV.Service | SZ VAV Cooling Load | 1675 | 744 |  | Views.Details.SZ VAV.Service | SZVAVClgLd | 1709 | 665
Prop | Templates.Cooling Control | Operational Error Sigma | 1675 | 1076 | 7054 | TRUE | TRUE | FALSE | 4 | Float | 10ths | 5 | delta deg F | 507:120 | 1.4 | 1 | 2.5 |  |  | 10ths | 0 | delta deg C | 507:359 | 0.6 | 1.5 | [7 empty] | Attr | York RTU.Cooling Control | 4 | Operational Error Sigma | UCBapp.newUCB.Clg_Min_Tune_Band | Relinquish Default | FALSE | [7 empty] | Value |  |  | Views.Details.Cooling.Setup | Cooling Manual Tuning | 1675 | 478 |  | Views.Details.Clg.Setup | ClgManualTune | 1709 | 690
Prop | Templates.Cooling Control | 4 Pipe Split Enable | 1675 | 1454 | 7055 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | FALSE | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Cooling Control | 4 | 4 Pipe Split Enable | UCBapp.newUCB.Four_Pipe_Split_Enable | Relinquish Default | FALSE | [7 empty] | Value |  |  | Views.Details.Cooling.Setup | 4 Pipe Split Enable | 1675 | 1454 |  | Views.Details.Clg.Setup | 4pipeEna | 1709 | 695
Prop | Templates.Cooling Control | Low Ambient Start | 1675 | 1457 | 7056 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Enable | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Cooling Control | 4 | Low Ambient Start | UCBapp.newUCB.Low_Amb_Freeze_Protect | Relinquish Default | FALSE | [7 empty] | Value |  |  | Views.Commissioning.Options | Low Ambient Start | 1675 | 1457 |  | Views.Commission.Options | LowAmbStart | 1709 | 697
Prop | Templates.Cooling Control | Low Ambient Start | 1675 | 1457 | 7056 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Enable | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Cooling Control | 4 | Low Ambient Start | UCBapp.newUCB.Low_Amb_Freeze_Protect | Relinquish Default | FALSE | [7 empty] | Value |  |  | Views.Details.Cooling.Setup | Low Ambient Start | 1675 | 1457 |  | Views.Details.Clg.Setup | LowAmbStart | 1709 | 697
Prop | Templates.Cooling Control | Alarm Delay | 1675 | 1461 | 7057 | TRUE | TRUE | FALSE | 18 | UnsignedInteger | 1s | 6 | hours | 507:71 |  | 0 | 1080 |  |  | 1s | 0 | hours | 507:71 | 0 | 1080 | [7 empty] | Attr | York RTU.Cooling Control | 4 | Alarm Delay | SE-FDD1001-05/FDSI FDD | Alarm Delay | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2
Prop | Templates.Cooling Control | Alarm Reporting | 1675 | 1369 | 7058 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Cooling Control | 4 | Alarm Reporting | UCBapp.newUCB.NO_FREEZE_PROTECT_ALARM | Present Value | FALSE
Prop | Templates.Cooling Control | Cooling Stages Available | 1675 | 68 | 7059 | TRUE | TRUE | FALSE | 16 | Byte | 1s | 6 |  | 507:95 | 4 | 1 | 4 |  |  | 1s | 0 |  | 507:95 | 1 | 4 | [7 empty] | Attr | York RTU.Cooling Control | 4 | Cooling Stages Available | UCBapp.newUCB.EFF_MAX_COOL_DISPLAY | Present Value | TRUE
Prop | Templates.Cooling Control | Cooling Allowed During Heat Limit | 1714 | 230 | 7060 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | No | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Cooling Control | 4 | Cooling Allowed During Heat Limit | UCBapp.newUCB.Cool_During_Heat_Limit | Relinquish Default | FALSE |  |  |  | MV:30071 | HR:845 | ADI:193 |  | Value |  |  | Views.Commissioning.Options | Cooling Allowed During Heat Limit | 1714 | 230 |  | Views.Commission.Options | CoolDuringHeatLimit | 1709 | 727
Prop | Templates.Cooling Control | Cooling Allowed During Heat Limit | 1714 | 230 | 7060 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | No | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Cooling Control | 4 | Cooling Allowed During Heat Limit | UCBapp.newUCB.Cool_During_Heat_Limit | Relinquish Default | FALSE |  |  |  | MV:30071 | HR:845 | ADI:193 |  | Value |  |  | Views.Details.Heating.Setup | Cooling Allowed During Heat Limit | 1714 | 230 |  | Views.Details.Htg.Setup | CoolDuringHeatLimit | 1709 | 727
Prop | Templates.Cooling Control | SZ VAV Operating Cooling Setpoint | 1675 | 648 | 7061 | TRUE | FALSE | FALSE | 4 | Float | 100ths | 4 | deg F | 507:64 | 72 |  |  |  |  | 100ths | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control | 4 | SZ VAV Operating Cooling Setpoint | UCBapp.newUCB.Operating_Cooling_Setpoint | Present Value | FALSE |  |  | UCBapp.newUCB.Setpoint_Input_Presence:Present Value = Curve 3 | AV:29927 | IR:850 | ADF:171
Prop | Templates.Cooling Control | FDD Alarm Enable | 1714 | 236 | 7062 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Disable/Enable | 658 | Disable | [6 empty] | Disable/Enable | 658 | [6 empty] | 658 | 0 = Disable 1 = Enable |  | Attr | York RTU.Cooling Control | 4 | FDD Alarm Enable | FDDApp.FDD.FDD_ALARM_ENABLE | Relinquish Default | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | MV:30076 | HR:848 | ADI:196 |  | Value |  |  | Views.Commissioning.Options | FDD Alarm Enable | 1714 | 236 |  | Views.Commission.Options | FDDAlarmEn | 1709 | 733
Prop | Templates.Cooling Control | Circuit 1 Modulating Condenser Fan Installed | 2644 | 323 | 7063 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | FALSE | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Cooling Control | 4 | Circuit 1 Modulating Condenser Fan Installed | UCBapp.newUCB.Cond1_Fan_Type | Relinquish Default | TRUE | [7 empty] | Value |  |  | Views.Commissioning.Options | Circuit 1 Modulating Condenser Fan Installed | 2644 | 323 |  | Views.Commission.Options | ModCondFanCir1En | 2645 | 342
Prop | Templates.Cooling Control | Circuit 2 Modulating Condenser Fan Installed | 2644 | 324 | 7064 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | FALSE | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Cooling Control | 4 | Circuit 2 Modulating Condenser Fan Installed | UCBapp.newUCB.Cond2_Fan_Type | Relinquish Default | TRUE | [7 empty] | Value |  |  | Views.Commissioning.Options | Circuit 2 Modulating Condenser Fan Installed | 2644 | 324 |  | Views.Commission.Options | ModCondFanCir2En | 2645 | 343
Prop | Templates.Cooling Control | Modulating Condenser Fan 1 Output | 2644 | 293 | 7065 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | % | 507:98 | N/A | 0 | 100 |  |  | 10ths | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Cooling Control | 4 | Modulating Condenser Fan 1 Output | FourStageApp.FourStage.CF1_MOD | Present Value | FALSE |  |  | York RTU.Cooling Control.Circuit 1 Modulating Condenser Fan Installed:Present Value = Yes | AV:30079 | IR:856 | AO:7 |  | Value |  |  | Views.Details.Cooling.Service.Unit | Modulating Condenser Fan 1 Output | 2644 | 293 |  | Views.Details.Clg.Service.Unit | ModCondFan1Out | 2645 | 312
Prop | Templates.Cooling Control | Modulating Condenser Fan 2 Output | 2644 | 294 | 7066 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | % | 507:98 | N/A | 0 | 100 |  |  | 10ths | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Cooling Control | 4 | Modulating Condenser Fan 2 Output | FourStageApp.FourStage.CF2_MOD | Present Value | FALSE |  |  | York RTU.Cooling Control.Circuit 2 Modulating Condenser Fan Installed:Present Value = Yes | AV:30080 | IR:857 | AO:8 |  | Value |  |  | Views.Details.Cooling.Service.Unit | Modulating Condenser Fan 2 Output | 2644 | 294 |  | Views.Details.Clg.Service.Unit | ModCondFan2Out | 2645 | 313
Prop | Templates.Cooling Control | Modulating Compressor Output | 2644 | 292 | 7067 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | % | 507:98 | N/A | 0 | 100 |  |  | 10ths | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Cooling Control | 4 | Modulating Compressor Output | FourStageApp.FourStage.C1_MOD | Present Value | FALSE |  |  | York RTU.Unique Equipment Identifier:Present Value > 5 | AV:30081 | IR:858 | AO:9 |  | Value |  |  | Views.Details.Cooling.Service.Stage 1 | Modulating Compressor Output | 2644 | 292 |  | Views.Details.Clg.Service.Stage 1 | ModCompOut | 2645 | 311
Prop | Templates.Cooling Control | Modulating Compressor Output | 2644 | 292 | 7067 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | % | 507:98 | N/A | 0 | 100 |  |  | 10ths | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Cooling Control | 4 | Modulating Compressor Output | FourStageApp.FourStage.C1_MOD | Present Value | FALSE |  |  | York RTU.Unique Equipment Identifier:Present Value > 5 | AV:30081 | IR:858 | AO:9 |  | Value |  |  | Views.Details.Hot Gas Reheat.Service | Modulating Compressor Output | 2644 | 292 |  | Views.Details.HGR.Service | ModCompOut | 2645 | 311
Prop | Templates.Cooling Control | Modulating Compressor Output | 2644 | 292 | 7067 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | % | 507:98 | N/A | 0 | 100 |  |  | 10ths | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Cooling Control | 4 | Modulating Compressor Output | FourStageApp.FourStage.C1_MOD | Present Value | FALSE |  |  | York RTU.Unique Equipment Identifier:Present Value > 5 | AV:30081 | IR:858 | AO:9 |  | Value |  |  | Views.Details.Mod Hot Gas Reheat.Service | Modulating Compressor Output | 2644 | 292 |  | Views.Details.ModHGR.Service | ModCompOut | 2645 | 311
Prop | Templates.Cooling Control | Circuit 1 OAT Cooling Cutout | 2644 | 442 | 7068 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 45 |  | 100 | 7070 |  | 1s | 0 | deg C | 507:62 |  | 38 | 7070 | [6 empty] | Attr | York RTU.Cooling Control | 4 | Circuit 1 OAT Cooling Cutout | UCBapp.newUCB.OA_Cooling_Lockout_SP | Relinquish Default | FALSE |  |  | York RTU.Unique Equipment Identifier:Present Value > 0 | AV:30082 | HR:859 | ADF:198 |  | Value |  |  | Views.Commissioning.Standard | Circuit 1 OAT Cooling Cutout | 2644 | 442 |  | Views.Commission.Standard | Circ1ClgOATCutout | 2645 | 425
Prop | Templates.Cooling Control | Circuit 2 OAT Cooling Cutout | 2644 | 443 | 7069 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 45 |  | 100 | 7071 |  | 1s | 0 | deg C | 507:62 |  | 38 | 7071 | [6 empty] | Attr | York RTU.Cooling Control | 4 | Circuit 2 OAT Cooling Cutout | UCBapp.newUCB.OA_Cooling_Lockout_SP_2 | Relinquish Default | FALSE |  |  | York RTU.Unique Equipment Identifier:Present Value > 0 | AV:30083 | HR:860 | ADF:199 |  | Value |  |  | Views.Commissioning.Standard | Circuit 2 OAT Cooling Cutout | 2644 | 443 |  | Views.Commission.Standard | Circ2ClgOATCutout | 2645 | 426
Prop | Templates.Cooling Control | Min Cooling Setpoint | 1675 | 515 | 7070 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | 0 |  |  |  |  | 10ths | 0 | deg C | 507:62 | [8 empty] | circuit 1 cooling OAT lockout minimum value | Attr | York RTU.Cooling Control | 4 | Min Cooling Setpoint | UCBapp.newUCB.Low_OA_Cutout_SP_Min_1 | Present Value | FALSE | [6 empty] | circuit 1 cooling OAT lockout minimum value
Prop | Templates.Cooling Control | Min Cooling Setpoint | 1675 | 515 | 7071 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | 0 |  |  |  |  | 10ths | 0 | deg C | 507:62 | [8 empty] | circuit 2 cooling OAT lockout minimum value | Attr | York RTU.Cooling Control | 4 | Min Cooling Setpoint | UCBapp.newUCB.Low_OA_Cutout_SP_Min_2 | Present Value | FALSE | [6 empty] | circuit 2 cooling OAT lockout minimum value
Prop | Templates.Cooling Control | Alarm Points | 1712 | 159 | 7072 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Alarm/Normal | 1696 | Enable | [6 empty] | Alarm/Normal | 1696 | [6 empty] | 1696 | 0 = Alarm 1 = Normal | This is the Envelope Alarm | Attr | York RTU.Cooling Control | 4 | Alarm Points | FDDApp.FDD.Mod_Comp_Env_En_Alarm | Present Value | FALSE |  |  | York RTU.Unique Equipment Identifier:Present Value > 5 |  |  |  | Envelope Alarm
Prop | Templates.Cooling Control | Compressor 1 Lockout | 1675 | 973 | 7073 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal Lockout | 1604 | Normal | [6 empty] | Normal Lockout | 1604 | [6 empty] | 1604 | 0 = Normal 1 = Lockout | Envelope Lockout | Attr | York RTU.Cooling Control | 4 | Compressor 1 Lockout | FDDApp.FDD.Mod_Comp_Env_Lockout | Present Value | FALSE |  |  | York RTU.Unique Equipment Identifier:Present Value > 5 |  |  |  | Envelope Lockout
Prop | Templates.Cooling Control | Compressor Stage 1 Lockout | 1675 | 1282 | 7074 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal Lockout | 1604 | Normal | [6 empty] | Normal Lockout | 1604 | [6 empty] | 1604 | 0 = Normal 1 = Lockout | Oil Management Lockout | Attr | York RTU.Cooling Control | 4 | Compressor Stage 1 Lockout | FDDApp.FDD.Mod_Comp_Oil_Lockout | Present Value | FALSE |  |  | York RTU.Unique Equipment Identifier:Present Value > 5 |  |  |  | Oil Management Lockout
Prop | Templates.Cooling Control | Compressor VFD Alarm | 2644 | 484 | 7075 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Cooling Control | 4 | Compressor VFD Alarm | FDDApp.FDD.Eff_VS_Comp_Alm | Present Value | FALSE |  |  | York RTU.Unique Equipment Identifier:Present Value > 5 | MV:30084 | IR:861 | ADI:198
Prop | Templates.Cooling Control | Oil Level Switch | 2644 | 507 | 7076 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Off | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Cooling Control | 4 | Oil Level Switch | FourStageApp.FourStage.Oil_Level_Alarm_Src | Present Value | FALSE |  |  | York RTU.Cooling Control.Oil Switch Installed:Present Value = TRUE |  |  |  |  | Value |  |  | Views.Details.Cooling.Service.Stage 1 | Oil Level Switch | 2644 | 507 |  | Views.Details.Clg.Service.Stage 1 | OIL-A | 2645 | 467
Prop | Templates.Cooling Control | Oil Switch Installed | 2644 | 418 | 7077 | TRUE | TRUE | FALSE | 1 | Boolean |  |  |  |  | FALSE | [17 empty] | Attr | York RTU.Cooling Control | 4 | Oil Switch Installed | FDDApp.FDD.Oil_Alarm_Installed | Relinquish Default | TRUE |  |  | York RTU.Unique Equipment Identifier:Present Value > 5 |  |  |  |  | Value |  |  | Views.Commissioning.Options | Oil Switch Installed | 2644 | 418 |  | Views.Commission.Options | Oil Switch Installed | 2644 | 418
Prop | Templates.Cooling Control | Saturated Suction Temperature 1 | 2644 | 374 | 7078 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | 0 |  |  |  |  | 10ths | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control | 4 | Saturated Suction Temperature 1 | FDDApp.FDD.Sat_Suction_Temp_Circ1 | Present Value | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 1 | AV:30085 | IR:862 | ADF:200 |  | Value |  |  | Views.Details.Cooling.Misc | Saturated Suction Temperature 1 | 2644 | 374 |  | Views.Details.Clg.Misc | SatSucTemp1 | 2645 | 382
Prop | Templates.Cooling Control | Saturated Discharge Temperature 1 | 2644 | 370 | 7079 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | 0 |  |  |  |  | 10ths | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control | 4 | Saturated Discharge Temperature 1 | FDDApp.FDD.Sat_Discharge_Temp_Circ1 | Present Value | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 1 | AV:30086 | IR:863 | ADF:201 |  | Value |  |  | Views.Details.Cooling.Misc | Saturated Discharge Temperature 1 | 2644 | 370 |  | Views.Details.Clg.Misc | SatDischTemp1 | 2645 | 378
Prop | Templates.Cooling Control | Saturated Discharge Temperature 2 | 2644 | 371 | 7080 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | 0 |  |  |  |  | 10ths | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control | 4 | Saturated Discharge Temperature 2 | FDDApp.FDD.Sat_Discharge_Temp_Circ2 | Present Value | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 1 | AV:30087 | IR:864 | ADF:202 |  | Value |  |  | Views.Details.Cooling.Misc | Saturated Discharge Temperature 2 | 2644 | 371 |  | Views.Details.Clg.Misc | SatDischTemp2 | 2645 | 379
Prop | Templates.Cooling Control | Saturated Suction Temperature 2 | 2644 | 375 | 7081 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | 0 |  |  |  |  | 10ths | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control | 4 | Saturated Suction Temperature 2 | FDDApp.FDD.Sat_Suction_Temp_Circ2 | Present Value | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 1 | AV:30088 | IR:865 | ADF:203 |  | Value |  |  | Views.Details.Cooling.Misc | Saturated Suction Temperature 2 | 2644 | 375 |  | Views.Details.Clg.Misc | SatSucTemp2 | 2645 | 383
Prop | Templates.Cooling Control | Suction Superheat 1 | 2644 | 366 | 7082 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | 0 |  |  |  |  | 10ths | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control | 4 | Suction Superheat 1 | FDDApp.FDD.Suction_Superheat_Circ1 | Present Value | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 1 | AV:30093 | IR:870 | ADF:204 |  | Value |  |  | Views.Details.Cooling.Misc | Suction Superheat 1 | 2644 | 366 |  | Views.Details.Clg.Misc | SucSuperheat1 | 2645 | 374
Prop | Templates.Cooling Control | Modulating Compressor Max Speed | 1714 | 245 | 7083 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 42 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Cooling Control | 4 | Modulating Compressor Max Speed | FDDApp.FDD.Modulating_Equip_Max | Relinquish Default | FALSE |  |  | York RTU.Unique Equipment Identifier:Present Value > 5
Prop | Templates.Cooling Control | Modulating Compressor Min Speed | 1714 | 246 | 7084 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 17 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Cooling Control | 4 | Modulating Compressor Min Speed | FDDApp.FDD.Modulating_Equip_Min | Relinquish Default | FALSE |  |  | York RTU.Unique Equipment Identifier:Present Value > 5
Prop | Templates.Cooling Control | Modulating Cond Fan Max Speed | 1714 | 247 | 7085 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 67 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Cooling Control | 4 | Modulating Cond Fan Max Speed | UCBapp.newUCB.CF_Mod_Max_Speed_Cir1 | Relinquish Default | FALSE |  |  | York RTU.Cooling Control.Circuit 1 Modulating Condenser Fan Installed:Present Value = Yes
Prop | Templates.Cooling Control | Modulating Cond Fan Min Speed | 1714 | 248 | 7086 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 0 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Cooling Control | 4 | Modulating Cond Fan Min Speed | UCBapp.newUCB.CF_Mod_Min_Speed_Cir1 | Relinquish Default | FALSE |  |  | York RTU.Cooling Control.Circuit 1 Modulating Condenser Fan Installed:Present Value = Yes
Prop | Templates.Cooling Control | Modulating Cond Fan SDT High Limit | 1714 | 250 | 7087 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 80 | 0 | 200 |  |  | 1s | 0 | deg C | 507:62 | -18 | 93 | [7 empty] | Attr | York RTU.Cooling Control | 4 | Modulating Cond Fan SDT High Limit | UCBapp.newUCB.CF_Mod_Max_Speed_Setpoint_Cir1 | Relinquish Default | FALSE |  |  | York RTU.Cooling Control.Circuit 1 Modulating Condenser Fan Installed:Present Value = Yes
Prop | Templates.Cooling Control | Modulating Cond Fan SDT Low Limit | 1714 | 249 | 7088 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 70 | 0 | 200 |  |  | 1s | 0 | deg C | 507:62 | -18 | 93 | [7 empty] | Attr | York RTU.Cooling Control | 4 | Modulating Cond Fan SDT Low Limit | UCBapp.newUCB.CF_Mod_Min_Speed_Setpoint_Cir1 | Relinquish Default | FALSE |  |  | York RTU.Cooling Control.Circuit 1 Modulating Condenser Fan Installed:Present Value = Yes
Prop | Templates.Cooling Control | Circuit 1 High Pressure Unload Enable | 1714 | 254 | 7089 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Disable/Enable | 658 | Enable | [6 empty] | Disable/Enable | 658 | [6 empty] | 658 | 0 = Disable 1 = Enable |  | Attr | York RTU.Cooling Control | 4 | Circuit 1 High Pressure Unload Enable | FDDApp.FDD.Cir1_High_Pres_Unload_En | Relinquish Default | FALSE |  |  | York RTU.Unique Equipment Identifier:Present Value > 5 |  |  |  |  | Value |  |  | Views.Details.Cooling.Misc | Circuit 1 High Pressure Unload Enable | 1714 | 254 |  | Views.Details.Clg.Misc | Cir1HighPresUnloadEn | 1709 | 754
Prop | Templates.Cooling Control | Circuit 1 Low Pressure Unload Enable | 1714 | 255 | 7090 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Disable/Enable | 658 | Enable | [6 empty] | Disable/Enable | 658 | [6 empty] | 658 | 0 = Disable 1 = Enable |  | Attr | York RTU.Cooling Control | 4 | Circuit 1 Low Pressure Unload Enable | FDDApp.FDD.Cir1_Low_Pres_Unload_En | Relinquish Default | FALSE |  |  | York RTU.Unique Equipment Identifier:Present Value > 5 |  |  |  |  | Value |  |  | Views.Details.Cooling.Misc | Circuit 1 Low Pressure Unload Enable | 1714 | 255 |  | Views.Details.Clg.Misc | Cir1LowPresUnloadEn | 1709 | 755
Prop | Templates.Cooling Control | Circuit 2 High Pressure Unload Enable | 1714 | 256 | 7091 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Disable/Enable | 658 | Disable | [6 empty] | Disable/Enable | 658 | [6 empty] | 658 | 0 = Disable 1 = Enable |  | Attr | York RTU.Cooling Control | 4 | Circuit 2 High Pressure Unload Enable | FDDApp.FDD.Cir2_High_Pres_Unload_En | Relinquish Default | FALSE |  |  | York RTU.Unique Equipment Identifier:Present Value > 5 |  |  |  |  | Value |  |  | Views.Details.Cooling.Misc | Circuit 2 High Pressure Unload Enable | 1714 | 256 |  | Views.Details.Clg.Misc | Cir2HighPresUnloadEn | 1709 | 756
Prop | Templates.Cooling Control | Circuit 2 Low Pressure Unload Enable | 1714 | 257 | 7092 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Disable/Enable | 658 | Disable | [6 empty] | Disable/Enable | 658 | [6 empty] | 658 | 0 = Disable 1 = Enable |  | Attr | York RTU.Cooling Control | 4 | Circuit 2 Low Pressure Unload Enable | FDDApp.FDD.Cir2_Low_Pres_Unload_En | Relinquish Default | FALSE |  |  | York RTU.Unique Equipment Identifier:Present Value > 5 |  |  |  |  | Value |  |  | Views.Details.Cooling.Misc | Circuit 2 Low Pressure Unload Enable | 1714 | 257 |  | Views.Details.Clg.Misc | Cir2LowPresUnloadEn | 1709 | 757
Prop | Templates.Cooling Control | Modulating Cond Fan 2 Min Speed | 1714 | 258 | 7093 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 0 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Cooling Control | 4 | Modulating Cond Fan 2 Min Speed | UCBapp.newUCB.CF_Mod_Min_Speed_Cir2 | Relinquish Default | FALSE |  |  | York RTU.Cooling Control.Circuit 2 Modulating Condenser Fan Installed:Present Value = Yes
Prop | Templates.Cooling Control | Modulating Cond Fan 2 Max Speed | 1714 | 259 | 7094 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 66 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Cooling Control | 4 | Modulating Cond Fan 2 Max Speed | UCBapp.newUCB.CF_Mod_Max_Speed_Cir2 | Relinquish Default | FALSE |  |  | York RTU.Cooling Control.Circuit 2 Modulating Condenser Fan Installed:Present Value = Yes
Prop | Templates.Cooling Control | Modulating Cond Fan 2 SDT Low Limit | 1714 | 260 | 7095 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 70 | 0 | 200 |  |  | 1s | 0 | deg C | 507:62 | -18 | 93 | [7 empty] | Attr | York RTU.Cooling Control | 4 | Modulating Cond Fan 2 SDT Low Limit | UCBapp.newUCB.CF_Mod_Min_Speed_Setpoint_Cir2 | Relinquish Default | FALSE |  |  | York RTU.Cooling Control.Circuit 2 Modulating Condenser Fan Installed:Present Value = Yes
Prop | Templates.Cooling Control | Modulating Cond Fan 2 SDT High Limit | 1714 | 261 | 7096 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 80 | 0 | 200 |  |  | 1s | 0 | deg C | 507:62 | -18 | 93 | [7 empty] | Attr | York RTU.Cooling Control | 4 | Modulating Cond Fan 2 SDT High Limit | UCBapp.newUCB.CF_Mod_Max_Speed_Setpoint_Cir2 | Relinquish Default | FALSE |  |  | York RTU.Cooling Control.Circuit 2 Modulating Condenser Fan Installed:Present Value = Yes
Prop | Templates.Cooling Control | Modulating Cond Fan SDT Off Setpoint | 1714 | 262 | 7097 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 60 | 0 | 200 |  |  | 1s | 0 | deg C | 507:62 | -18 | 93 | [7 empty] | Attr | York RTU.Cooling Control | 4 | Modulating Cond Fan SDT Off Setpoint | UCBapp.newUCB.CF_Mod_Off_Setpoint_Cir1 | Relinquish Default | FALSE |  |  | York RTU.Cooling Control.Circuit 1 Modulating Condenser Fan Installed:Present Value = Yes
Prop | Templates.Cooling Control | Modulating Cond Fan 2 SDT Off Setpoint | 1714 | 263 | 7098 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 60 | 0 | 200 |  |  | 1s | 0 | deg C | 507:62 | -18 | 93 | [7 empty] | Attr | York RTU.Cooling Control | 4 | Modulating Cond Fan 2 SDT Off Setpoint | UCBapp.newUCB.CF_Mod_Off_Setpoint_Cir2 | Relinquish Default | FALSE |  |  | York RTU.Cooling Control.Circuit 2 Modulating Condenser Fan Installed:Present Value = Yes
Prop | Templates.Cooling Control | DLT Protection Enable | 1714 | 264 | 7099 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Disable/Enable | 658 | Enable | [6 empty] | Disable/Enable | 658 | [6 empty] | 658 | 0 = Disable 1 = Enable |  | Attr | York RTU.Cooling Control | 4 | DLT Protection Enable | FDDApp.FDD.DLT_Protection_En | Relinquish Default | FALSE |  |  | York RTU.Unique Equipment Identifier:Present Value > 5
Prop | Templates.Cooling Control | High Discharge Line Temp Lockout | 1714 | 265 | 7100 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Cooling Control | 4 | High Discharge Line Temp Lockout | FDDApp.FDD.High_DLT_Shutdown | Present Value | FALSE |  |  | York RTU.Unique Equipment Identifier:Present Value > 5
Prop | Templates.Cooling Control | Cooling Rapid Start Enable | 1714 | 267 | 7101 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Disable/Enable | 658 | Disable | [6 empty] | Disable/Enable | 658 | [6 empty] | 658 | 0 = Disable 1 = Enable |  | Attr | York RTU.Cooling Control | 4 | Cooling Rapid Start Enable | UCBapp.newUCB.Cooling_Rapid_Start_Enable | Relinquish Default | TRUE |  |  | York RTU.Thermostat Control.Thermostat Only Control Enabled:Present Value = No | MV:30103 | HR:878 | ADI:212 |  | Value |  |  | Views.Details.Cooling.Setup | Cooling Rapid Start Enable | 1714 | 267 |  | Views.Details.Clg.Setup | ClgRapidStartEn | 1709 | 767
Prop | Templates.Cooling Control | Cooling Rapid Start Time | 1714 | 269 | 7102 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | minutes | 507:72 | 300 | 2 | 30 |  |  | 1s | 0 | minutes | 507:72 | 2 | 30 | [7 empty] | Attr | York RTU.Cooling Control | 4 | Cooling Rapid Start Time | UCBapp.newUCB.Cooling_Rapid_Start_Time | Relinquish Default | FALSE |  |  | York RTU.Cooling Control.Cooling Rapid Start Enable:Present Value = Enable | AV:30140 | HR:889 | ADF:223 |  | Value |  |  | Views.Details.Cooling.Setup | Cooling Rapid Start Time | 1714 | 269 |  | Views.Details.Clg.Setup | ClgRapidStartTime | 1709 | 769
Prop | Templates.Cooling Control | A2L Leak Detector Alarm | 1714 | 276 | 7103 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Cooling Control | 4 | A2L Leak Detector Alarm | UCBapp.newUCB.A2L_Leak_Detector_Alarm | Present Value | FALSE |  |  |  | MV:30134 | IR:891 | ADI:225 |  | Value |  |  | Views.Details.Cooling.Safeties | A2L Leak Detector Alarm | 1714 | 276 |  | Views.Details.Clg.Safeties | A2LLeakAlarm | 1709 | 787
Prop | Templates.Cooling Control | A2L Lockout Option | 1714 | 278 | 7104 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | SE RTU Lockout Option | 3452 | Three_Strikes | [6 empty] | SE RTU Lockout Option | 3452 | [6 empty] | 3452 | 0 = No Lockout 1 = Three Strikes 2 = Always Lockout | A2L Lockout Option | Attr | York RTU.Cooling Control | 4 | A2L Lockout Option | UCBapp.newUCB.A2L_Lockout_Option | Relinquish Default | TRUE
Prop | Templates.Cooling Control | A2L Lockout Time Interval | 1714 | 279 | 7105 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | hours | 507:71 | 2 | 1 | 24 |  |  | 1s | 0 | hours | 507:71 | 1 | 24 | [6 empty] | A2L Lockout Time Interval | Attr | York RTU.Cooling Control | 4 | A2L Lockout Time Interval | UCBapp.newUCB.A2L_Lockout_Time_Interval | Relinquish Default | FALSE
Prop | Templates.Cooling Control | A2L Leak Detector Alarm-Lockout | 1714 | 280 | 7106 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal Lockout | 1604 | Normal | [6 empty] | Normal Lockout | 1604 | [6 empty] | 1604 | 0 = Normal 1 = Lockout | A2L Leak Detector Alarm-Lockout | Attr | York RTU.Cooling Control | 4 | A2L Leak Detector Alarm-Lockout | UCBapp.newUCB.A2L_Leak_Detector_Lockout | Present Value | FALSE |  |  | York RTU.Cooling Control.A2L Lockout Option:Present Value <> No Lockout | MV:30135 | IR:892 | ADI:226 |  | Value |  |  | Views.Details.Cooling.Safeties | A2L Leak Detector Alarm-Lockout | 1714 | 280 |  | Views.Details.Clg.Safeties | A2LLeakAlarm-LO | 1709 | 791
Prop | Templates.Cooling Control | Condensate Alarm Enable | 2644 | 383 | 7107 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Disable/Enable | 658 | Disable | [6 empty] | Disable/Enable | 658 | [6 empty] | 658 | 0 = Disable 1 = Enable | Condensate_Alarm_Enable | Attr | York RTU.Cooling Control | 4 | Condensate Alarm Enable | UCBapp.newUCB.Condensate_Alarm_Enable | Relinquish Default | FALSE |  |  |  | MV:30156 | HR:897 | ADI:229 |  | Value |  |  | Views.Details.Cooling.Safeties | Condensate Alarm Enable | 2644 | 383 |  | Views.Details.Clg.Safeties | COS-En | 1709 | 797
Prop | Templates.Cooling Control | Condensate Overflow Switch | 1714 | 277 | 7108 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Alarm/Normal | 1696 | Enable | [6 empty] | Alarm/Normal | 1696 | [6 empty] | 1696 | 0 = Alarm 1 = Normal | Condensate Overflow Switch | Attr | York RTU.Cooling Control | 4 | Condensate Overflow Switch | UCBapp.newUCB.Condensate_Alarm_State | Present Value | FALSE |  |  |  | MV:30136 | IR:893 | ADI:227 |  | Value |  |  | Views.Details.Cooling.Safeties | Condensate Overflow Switch | 1714 | 277 |  | Views.Details.Clg.Safeties | COS | 1709 | 788
Tmpl | Templates.DX Cooling Circuit | [31 empty] | Model | York RTU.Cooling Control.DX Cooling Circuit 1 | 5
Prop | Templates.DX Cooling Circuit | Compressor Stage Number | 1675 | 83 | 7000 | TRUE | FALSE | FALSE | 17 | SignedInteger | 1s | 6 |  | 507:95 |  | 0 | 100 |  |  | 1s | 0 |  | 507:95 | 0 | 100 | [7 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 1 | 5 | Compressor Stage Number | EM Variable: 1 |  | FALSE
Prop | Templates.DX Cooling Circuit | Compressor Stage Command | 1675 | 84 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [5 empty] | Cooling Stage 1 ; Heat Pump Stage 1 Cooling Mode ; Heat Pump Stage 1 Heating Mode | 647 | 0 = Off 1 = On |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 1 | 5 | Compressor Stage Command | UCBapp.newUCB.COMP1_C | Present Value | FALSE |  |  |  | MV:29611 | IR:311 | BO:5 |  | Value |  |  | Views.Details.Cooling.Service.Stage 1 | Compressor Stage Command 1 | 1714 | 145 |  | Views.Details.Clg.Service.Stage 1 | C1 | 1709 | 127
Prop | Templates.DX Cooling Circuit | Compressor Stage Command | 1675 | 84 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [5 empty] | Cooling Stage 1 ; Heat Pump Stage 1 Cooling Mode ; Heat Pump Stage 1 Heating Mode | 647 | 0 = Off 1 = On |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 1 | 5 | Compressor Stage Command | UCBapp.newUCB.COMP1_C | Present Value | FALSE |  |  |  | MV:29611 | IR:311 | BO:5 |  | Value |  |  | Views.Details.FanVFD.Service | Compressor Stage Command 1 | 1714 | 145 |  | Views.Details.FanVFD.Service | C1 | 1709 | 127
Prop | Templates.DX Cooling Circuit | Compressor Stage Command | 1675 | 84 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [5 empty] | Cooling Stage 1 ; Heat Pump Stage 1 Cooling Mode ; Heat Pump Stage 1 Heating Mode | 647 | 0 = Off 1 = On |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 1 | 5 | Compressor Stage Command | UCBapp.newUCB.COMP1_C | Present Value | FALSE |  |  |  | MV:29611 | IR:311 | BO:5 |  | Value |  |  | Views.Details.Single Zone VAV.Service | Compressor Stage Command 1 | 1714 | 145 |  | Views.Details.SZ VAV.Service | C1 | 1709 | 127
Prop | Templates.DX Cooling Circuit | Compressor Stage Command | 1675 | 84 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [5 empty] | Cooling Stage 1 ; Heat Pump Stage 1 Cooling Mode ; Heat Pump Stage 1 Heating Mode | 647 | 0 = Off 1 = On |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 1 | 5 | Compressor Stage Command | UCBapp.newUCB.COMP1_C | Present Value | FALSE |  |  |  | MV:29611 | IR:311 | BO:5 |  | Value |  |  | Views.Details.Hot Gas Reheat.Service | Compressor Stage Command 1 | 1714 | 145 |  | Views.Details.HGR.Service | C1 | 1709 | 127
Prop | Templates.DX Cooling Circuit | Compressor Stage Command | 1675 | 84 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [5 empty] | Cooling Stage 1 ; Heat Pump Stage 1 Cooling Mode ; Heat Pump Stage 1 Heating Mode | 647 | 0 = Off 1 = On |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 1 | 5 | Compressor Stage Command | UCBapp.newUCB.COMP1_C | Present Value | FALSE |  |  |  | MV:29611 | IR:311 | BO:5 |  | Value |  |  | Views.Details.Mod Hot Gas Reheat.Service | Compressor Stage Command 1 | 1714 | 145 |  | Views.Details.ModHGR.Service | C1 | 1709 | 127
Prop | Templates.DX Cooling Circuit | Compressor Stage Status | 1675 | 85 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | SE RTU DX Cooling Circuit 1 Status | 1741 | Off_Idle | [6 empty] | SE RTU DX Cooling Circuit 1 Status | 1741 | [6 empty] | 1741 | 0 = Off-Idle 1 = On-Minimum On Time 2 = On-Normal Command 3 = Off-Cooling Is Disabled ... |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 1 | 5 | Compressor Stage Status | UCBapp.newUCB.Compressor_1_Stage_Status | Present Value | FALSE |  |  |  | MV:29615 | IR:312 | BI:14 |  | Value |  |  | Views.Details.Cooling.Service.Stage 1 | Compressor Stage 1 Status | 1714 | 39 |  | Views.Details.Clg.Service.Stage 1 | C1-S | 1709 | 131
Prop | Templates.DX Cooling Circuit | Compressor Stage Enabled | 1675 | 86 | 7003 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Yes/No | 1698 | Enable | [6 empty] | Yes/No | 1698 | [6 empty] | 1698 | 0 = Yes 1 = No |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 1 | 5 | Compressor Stage Enabled | UCBapp.newUCB.Compressor_Stage_1_Enabled | Relinquish Default | FALSE |  |  |  | MV:29619 | HR:101 | ADI:36 |  | Value |  |  | Views.Details.Cooling.Setup | Compressor Stage 1 Enabled | 1714 | 40 |  | Views.Details.Clg.Setup | C1-En | 1709 | 135
Prop | Templates.DX Cooling Circuit | Hot Gas Bypass Present | 1675 | 89 | 7004 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Off | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 1 | 5 | Hot Gas Bypass Present | UCBapp.newUCB.Hot_Gas_Bypass_Present | Relinquish Default | FALSE |  |  |  | MV:29623 | HR:408 | ADI:125 |  | Value |  |  | Views.Commissioning.Options | Hot Gas Bypass Present | 1675 | 89 |  | Views.Commission.Options | HGP-Inst | 1709 | 139
Prop | Templates.DX Cooling Circuit | Hot Gas Bypass Present | 1675 | 89 | 7004 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Off | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 1 | 5 | Hot Gas Bypass Present | UCBapp.newUCB.Hot_Gas_Bypass_Present | Relinquish Default | FALSE |  |  |  | MV:29623 | HR:408 | ADI:125 |  | Value |  |  | Views.Details.Cooling.Setup | Hot Gas Bypass Present | 1675 | 89 |  | Views.Details.Clg.Setup | HGP-Inst | 1709 | 139
Prop | Templates.DX Cooling Circuit | Compressor Stage Accumulated Runtime | 1675 | 90 | 7005 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | hours | 507:71 |  | 0 | 10000 |  |  | 1s | 0 | hours | 507:71 | 0 | 10000 | [7 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 1 | 5 | Compressor Stage Accumulated Runtime | 8-1/UCBApp.Clg_Runtime_1 | Present Value | FALSE |  |  |  | AV:29627 | IR:33 | ADF:56 |  | Value |  |  | Views.Details.Cooling.Service.Stage 1 | Compressor Stage Accumulated Runtime 1 | 1714 | 43 |  | Views.Details.Clg.Service.Stage 1 | C1RunTim | 1709 | 140
Prop | Templates.DX Cooling Circuit | Compressor Stage Accumulated Runtime | 1675 | 90 | 7005 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | hours | 507:71 |  | 0 | 10000 |  |  | 1s | 0 | hours | 507:71 | 0 | 10000 | [7 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 1 | 5 | Compressor Stage Accumulated Runtime | 8-1/UCBApp.Clg_Runtime_1 | Present Value | FALSE |  |  |  | AV:29627 | IR:33 | ADF:56 |  | Value |  |  | Views.Clone.Full Clone | Compressor Stage Accumulated Runtime 1 | 1714 | 43 |  |  | C1RunTim | 1709 | 140
Prop | Templates.DX Cooling Circuit | Compressor Stage Number Times On | 1675 | 91 | 7006 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 |  | 507:95 |  | 0 | 2000000 |  |  | 1s | 0 |  | 507:95 | 0 | 2000000 | [7 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 1 | 5 | Compressor Stage Number Times On | 8-1/UCBApp.Clg_Starts_1 | Relinquish Default | FALSE
Prop | Templates.DX Cooling Circuit | Min On Time Remaining | 1675 | 92 | 7007 | TRUE | FALSE | FALSE | 17 | SignedInteger | 1s | 6 | seconds | 507:73 | 0 |  |  |  |  | 1s | 0 | seconds | 507:73 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 1 | 5 | Min On Time Remaining | UCBapp.newUCB.Cool_Min_On_Time_Remaining_1 | Present Value | FALSE |  |  |  | AV:29631 | IR:162 | ADI:37 |  | Value |  |  | Views.Details.Cooling.Service.Stage 1 | Min On Time Remaining 1 | 1714 | 41 |  | Views.Details.Clg.Service.Stage 1 | C1OnTmr | 1709 | 148
Prop | Templates.DX Cooling Circuit | Anti-Short Cycle Delay Time Remaining | 1675 | 145 | 7008 | TRUE | FALSE | FALSE | 17 | SignedInteger | 1s | 6 | seconds | 507:73 | 0 |  |  |  |  | 1s | 0 | seconds | 507:73 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 1 | 5 | Anti-Short Cycle Delay Time Remaining | UCBapp.newUCB.Cool_Min_Off_Time_Remaining_1 | Present Value | FALSE |  |  |  | AV:29635 | IR:163 | ADI:38 |  | Value |  |  | Views.Details.Cooling.Service.Stage 1 | Anti-Short Cycle Delay Time Remaining 1 | 1714 | 42 |  | Views.Details.Clg.Service.Stage 1 | C1ASCDTmr | 1709 | 152
Prop | Templates.DX Cooling Circuit | High Pressure Limit | 1675 | 93 | 7009 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 1 | 5 | High Pressure Limit | UCBapp.newUCB.High_Pressure_Limit_1 | Present Value | FALSE |  |  |  | MV:29639 | IR:313 | BI:15 |  | Value |  |  | Views.Details.Cooling.Safeties | High Pressure Limit 1 | 1714 | 121 |  | Views.Details.Clg.Safeties | HPS1 | 1709 | 156
Prop | Templates.DX Cooling Circuit | High Pressure Lockout | 1675 | 94 | 7010 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal Lockout | 1604 | Normal | [6 empty] | Normal Lockout | 1604 | [6 empty] | 1604 | 0 = Normal 1 = Lockout |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 1 | 5 | High Pressure Lockout | UCBapp.newUCB.High_Pressure_Lockout_1 | Present Value | FALSE |  |  |  | MV:29643 | IR:314 | ADI:39 |  | Value |  |  | Views.Details.Cooling.Safeties | High Pressure Lockout 1 | 1714 | 129 |  | Views.Details.Clg.Safeties | HPS1-LO | 1709 | 160
Prop | Templates.DX Cooling Circuit | Low Pressure Limit | 1675 | 95 | 7011 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 1 | 5 | Low Pressure Limit | UCBapp.newUCB.Low_Pressure_Limit_1 | Present Value | FALSE |  |  |  | MV:29647 | IR:315 | BI:16 |  | Value |  |  | Views.Details.Cooling.Safeties | Low Pressure Limit 1 | 1714 | 122 |  | Views.Details.Clg.Safeties | LPS1 | 1709 | 164
Prop | Templates.DX Cooling Circuit | Low Pressure Lockout | 1675 | 96 | 7012 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal Lockout | 1604 | Normal | [6 empty] | Normal Lockout | 1604 | [6 empty] | 1604 | 0 = Normal 1 = Lockout |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 1 | 5 | Low Pressure Lockout | UCBapp.newUCB.Low_Pressure_Lockout_1 | Present Value | FALSE |  |  |  | MV:29651 | IR:316 | ADI:40 |  | Value |  |  | Views.Details.Cooling.Safeties | Low Pressure Lockout 1 | 1714 | 130 |  | Views.Details.Clg.Safeties | LPS1-LO | 1709 | 168
Prop | Templates.DX Cooling Circuit | Freeze Condition | 1675 | 97 | 7013 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 1 | 5 | Freeze Condition | UCBapp.newUCB.Freeze_Condition_1 | Present Value | FALSE |  |  |  | MV:29655 | IR:317 | BI:17 |  | Value |  |  | Views.Details.Cooling.Safeties | Freeze Condition 1 | 1714 | 131 |  | Views.Details.Clg.Safeties | FS1 | 1709 | 172
Prop | Templates.DX Cooling Circuit | Freeze Condition Lockout | 1675 | 98 | 7014 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal Lockout | 1604 | Normal | [6 empty] | Normal Lockout | 1604 | [6 empty] | 1604 | 0 = Normal 1 = Lockout |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 1 | 5 | Freeze Condition Lockout | UCBapp.newUCB.Freeze_Condition_Lockout_1 | Present Value | FALSE |  |  |  | MV:29659 | IR:318 | ADI:41 |  | Value |  |  | Views.Details.Cooling.Safeties | Freeze Condition Lockout 1 | 1714 | 132 |  | Views.Details.Clg.Safeties | FS1-LO | 1709 | 176
Prop | Templates.DX Cooling Circuit | Evaporator Coil Temp | 1675 | 100 | 7015 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | N/A |  |  |  |  | 10ths | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 1 | 5 | Evaporator Coil Temp | UCBapp.newUCB.EVAP1_T | Present Value | FALSE |  |  |  | AV:29663 | IR:164 | AI:5 |  | Value |  |  | Views.Details.Cooling.Sensors | Evaporator Coil Temp 1 | 1714 | 44 |  | Views.Details.Clg.Sensors | EC1 | 1709 | 180
Prop | Templates.DX Cooling Circuit | Condenser Coil Temp | 1675 | 102 | 7016 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | N/A |  |  |  |  | 10ths | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 1 | 5 | Condenser Coil Temp | UCBapp.newUCB.COND1_T | Present Value | FALSE |  |  |  | AV:29667 | IR:165 | AI:6 |  | Value |  |  | Views.Details.Cooling.Sensors | Condenser Coil Temp 1 | 1714 | 45 |  | Views.Details.Clg.Sensors | CC1 | 1709 | 184
Prop | Templates.DX Cooling Circuit | Condenser Coil Temp | 1675 | 102 | 7016 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | N/A |  |  |  |  | 10ths | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 1 | 5 | Condenser Coil Temp | UCBapp.newUCB.COND1_T | Present Value | FALSE |  |  |  | AV:29667 | IR:165 | AI:6 |  | Value |  |  | Views.Details.Heat Pump | Condenser Coil Temp 1 | 1714 | 45 |  | Views.Details.HeatPmp | CC1 | 1709 | 184
Prop | Templates.DX Cooling Circuit | Evaporator Coil Temp Sensor Fault | 1675 | 308 | 7017 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 1 | 5 | Evaporator Coil Temp Sensor Fault | UCBapp.newUCB.Evap_Coil_1_Temp_Sensor_Fault | Present Value | FALSE
Prop | Templates.DX Cooling Circuit | Condenser Coil Temp Sensor Fault | 1675 | 309 | 7018 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 1 | 5 | Condenser Coil Temp Sensor Fault | UCBapp.newUCB.Cond_Coil_1_Temp_Sensor_Fault | Present Value | FALSE
Prop | Templates.DX Cooling Circuit | Low Pressure Limit | 1675 | 95 | 7019 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 1 | 5 | Low Pressure Limit | UCBapp.newUCB.Low_Pressure_Alarm_1 | Present Value | FALSE
Tmpl | Templates.Cooling Circuit Diagnostics | [31 empty] | Model | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | 6 | [6 empty] | York RTU.System Controllers.FDD Manager Controller:Present Value <> Not Present
Prop | Templates.Cooling Circuit Diagnostics | Cooling Circuit Test Status | 1675 | 193 | 7000 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | SE FDD Codes | 1694 | [7 empty] | SE FDD Codes | 1694 | [6 empty] | 1694 | 0 = Unknown Status 1 = Basic Data Not Available Manual Entry 2 = Basic Data Not Available 3 = Return Wet Bulb Temp Not Available ... |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | 6 | Cooling Circuit Test Status | SE-FDD1001-05/FDSI FDD | Diagnostic Code Circuit 1 | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | MV:29829 | IR:343 | ADI:60 |  | Value |  |  | Views.Details.Cooling.Service.Stage 1 | Cooling Circuit Test Status | 1675 | 193 |  | Views.Details.Clg.Service.Stage 1 | ClgCktTestS-1 | 1709 | 478
Prop | Templates.Cooling Circuit Diagnostics | Suction Pressure | 1675 | 194 | 7001 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 6 | psi | 507:56 | N/A |  |  |  |  | 1s | 0 | kPa | 507:54 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | 6 | Suction Pressure | FDDApp.FDD.SLA_P | Present Value | FALSE |  |  |  | AV:29671 | IR:178 | AI:13 |  | Value |  |  | Views.Details.Cooling.Sensors | Suction Pressure 1 | 1714 | 46 |  | Views.Details.Clg.Sensors | SLP-1 | 1709 | 188
Prop | Templates.Cooling Circuit Diagnostics | Liquid Pressure | 1675 | 195 | 7002 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 6 | psi | 507:56 | N/A |  |  |  |  | 1s | 0 | kPa | 507:54 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | 6 | Liquid Pressure | FDDApp.FDD.DLA_P | Present Value | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | AV:29675 | IR:179 | AI:14 |  | Value |  |  | Views.Details.Cooling.Sensors | Liquid Pressure 1 | 1714 | 47 |  | Views.Details.Clg.Sensors | LLP-1 | 1709 | 192
Prop | Templates.Cooling Circuit Diagnostics | Suction Temperature | 1675 | 196 | 7003 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | N/A |  |  |  |  | 10ths | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | 6 | Suction Temperature | FDDApp.FDD.SLA_T | Present Value | FALSE |  |  |  | AV:29679 | IR:180 | AI:15 |  | Value |  |  | Views.Details.Cooling.Sensors | Suction Temperature 1 | 1714 | 48 |  | Views.Details.Clg.Sensors | SLT-1 | 1709 | 196
Prop | Templates.Cooling Circuit Diagnostics | Liquid Temperature | 1675 | 197 | 7004 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | N/A |  |  |  |  | 10ths | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | 6 | Liquid Temperature | FDDApp.FDD.DLA_T | Present Value | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | AV:29683 | IR:181 | AI:16 |  | Value |  |  | Views.Details.Cooling.Sensors | Liquid Temperature 1 | 1714 | 49 |  | Views.Details.Clg.Sensors | LLT-1 | 1709 | 200
Prop | Templates.Cooling Circuit Diagnostics | Superheat | 1675 | 198 | 7005 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | 6 | Superheat | SE-FDD1001-05/FDSI FDD | Superheat Value Circuit 1 | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | AV:29687 | IR:182 | ADF:60 |  | Value |  |  | Views.Details.Cooling.Service.Stage 1 | Superheat | 1675 | 198 |  | Views.Details.Clg.Service.Stage 1 | C1-SuperHeat | 1709 | 204
Prop | Templates.Cooling Circuit Diagnostics | Subcooling | 1675 | 199 | 7006 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | 6 | Subcooling | SE-FDD1001-05/FDSI FDD | Subcool Value Circuit 1 | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | AV:29691 | IR:183 | ADF:61 |  | Value |  |  | Views.Details.Cooling.Service.Stage 1 | Subcooling | 1675 | 199 |  | Views.Details.Clg.Service.Stage 1 | C1-SubCool | 1709 | 208
Prop | Templates.Cooling Circuit Diagnostics | Condensing Temperature over Ambient | 1675 | 200 | 7007 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | 6 | Condensing Temperature over Ambient | SE-FDD1001-05/FDSI FDD | Condense Temp Over Ambient Value Circuit 1 | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | AV:29695 | IR:184 | ADF:62 |  | Value |  |  | Views.Details.Cooling.Service.Stage 1 | Condensing Temperature over Ambient 1 | 1714 | 54 |  | Views.Details.Clg.Service.Stage 1 | C1-CondTempOvrAmb | 1709 | 212
Prop | Templates.Cooling Circuit Diagnostics | Efficiency Index | 1675 | 201 | 7008 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | [5 empty] | 1s | 0 | % | 507:98 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | 6 | Efficiency Index | SE-FDD1001-05/FDSI FDD | Efficiency Index Circuit 1 | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | AV:29699 | IR:185 | ADF:63 |  | Value |  |  | Views.Details.Cooling.Service.Stage 1 | Efficiency Index 1 | 1714 | 52 |  | Views.Details.Clg.Service.Stage 1 | C1-EI | 1709 | 216
Prop | Templates.Cooling Circuit Diagnostics | Capacity Index | 1675 | 202 | 7009 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | [5 empty] | 1s | 0 | % | 507:98 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | 6 | Capacity Index | SE-FDD1001-05/FDSI FDD | Capacity Index Circuit 1 | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | AV:29703 | IR:186 | ADF:64 |  | Value |  |  | Views.Details.Cooling.Service.Stage 1 | Capacity Index 1 | 1714 | 53 |  | Views.Details.Clg.Service.Stage 1 | C1-CI | 1709 | 220
Prop | Templates.Cooling Circuit Diagnostics | Suction Pressure Sensor Fault | 1675 | 331 | 7010 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | 6 | Suction Pressure Sensor Fault | FDDApp.FDD.SLP_Alarm_1_Src | Present Value | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 1
Prop | Templates.Cooling Circuit Diagnostics | Suction Temperature Sensor Fault | 1675 | 332 | 7011 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | 6 | Suction Temperature Sensor Fault | FDDApp.FDD.SLT_Alarm_1_Src | Present Value | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 1
Prop | Templates.Cooling Circuit Diagnostics | Discharge Pressure Sensor Fault | 1675 | 1681 | 7012 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm | Discharge Pressure Sensor Fault | Attr | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | 6 | Discharge Pressure Sensor Fault | FDDApp.FDD.DLP_Alarm_1_Src | Present Value | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 1 |  |  |  | Discharge Pressure cir1 Sensor Fault
Prop | Templates.Cooling Circuit Diagnostics | Discharge Temperature Sensor Fault | 1675 | 1682 | 7013 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm | Discharge Temperature Sensor Fault | Attr | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | 6 | Discharge Temperature Sensor Fault | FDDApp.FDD.DLT_Alarm_1_Src | Present Value | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 1 |  |  |  | Discharge Temperature cir1 Sensor Fault
Prop | Templates.Cooling Circuit Diagnostics | Evaporating Temp Value | 1675 | 424 | 7014 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | 6 | Evaporating Temp Value | SE-FDD1001-05/FDSI FDD | Evaporating Temperature Value Circuit 1 | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | AV:29833 | IR:187 | ADF:65 |  | Value |  |  | Views.Details.Cooling.Service.Stage 1 | Evaporating Temperature Value Circuit 1 | 1714 | 164 |  | Views.Details.Clg.Service.Stage 1 | C1-EvapTempValue | 1709 | 534
Prop | Templates.Cooling Circuit Diagnostics | Condenser Temperature Over Ambient High | 1675 | 440 | 7015 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | 6 | Condenser Temperature Over Ambient High | SE-FDD1001-05/FDSI FDD | Condense Temp Over Ambient High Limit Circuit 1 | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | AV:29849 | IR:188 | ADF:66
Prop | Templates.Cooling Circuit Diagnostics | Condenser Temperature Over Ambient Low | 1675 | 441 | 7016 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | 6 | Condenser Temperature Over Ambient Low | SE-FDD1001-05/FDSI FDD | Condense Temp Over Ambient Low Limit Circuit 1 | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | AV:29853 | IR:189 | ADF:67
Prop | Templates.Cooling Circuit Diagnostics | Superheat High | 1675 | 442 | 7017 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | 6 | Superheat High | SE-FDD1001-05/FDSI FDD | Superheat High Limit Circuit 1 | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | AV:29857 | IR:190 | ADF:68
Prop | Templates.Cooling Circuit Diagnostics | Superheat Low | 1675 | 443 | 7018 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | 6 | Superheat Low | SE-FDD1001-05/FDSI FDD | Superheat Low Limit Circuit 1 | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | AV:29861 | IR:191 | ADF:69
Prop | Templates.Cooling Circuit Diagnostics | Subcool High | 1675 | 444 | 7019 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | 6 | Subcool High | SE-FDD1001-05/FDSI FDD | Subcool High Limit Circuit 1 | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | AV:29865 | IR:192 | ADF:70
Prop | Templates.Cooling Circuit Diagnostics | Subcool Low | 1675 | 445 | 7020 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | 6 | Subcool Low | SE-FDD1001-05/FDSI FDD | Subcool Low Limit Circuit 1 | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | AV:29869 | IR:193 | ADF:71
Prop | Templates.Cooling Circuit Diagnostics | Evaporating Temperature High | 1675 | 446 | 7021 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | 6 | Evaporating Temperature High | SE-FDD1001-05/FDSI FDD | Evaporating Temperature High Limit Circuit 1 | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | AV:29873 | IR:194 | ADF:72
Prop | Templates.Cooling Circuit Diagnostics | Evaporating Temperature Low | 1675 | 447 | 7022 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | 6 | Evaporating Temperature Low | SE-FDD1001-05/FDSI FDD | Evaporating Temperature Low Limit Circuit 1 | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | AV:29877 | IR:195 | ADF:73
Prop | Templates.Cooling Circuit Diagnostics | Service Alarm | 1675 | 588 | 7023 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | CPO5 Alarms | 2594 | None | [6 empty] | CPO5 Alarms | 2594 | [6 empty] | 2594 | 0 = None 1 = Chiller 1 Interlock Alarm 2 = Chiller 2 Interlock Alarm 3 = Chiller 3 Interlock Alarm ... |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | 6 | Service Alarm | FDDApp.FDD.DIAGNOSTIC_CODE_CIRCUIT_1o | Present Value | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2
Prop | Templates.Cooling Circuit Diagnostics | Discharge Line Pressure | 2644 | 482 | 7024 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 6 | psi | 507:56 | N/A | 0 | 750 |  |  | 1s | 0 | kPa | 507:54 | 0 | 5172 | [7 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | 6 | Discharge Line Pressure | FDDApp.FDD.DLA_P | Present Value | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 1 | AV:30089 | IR:866 | AI:34 |  | Value |  |  | Views.Details.Cooling.Sensors | Discharge Line Pressure 1 | 2644 | 378 |  | Views.Details.Clg.Sensors | DLP1 | 2645 | 386
Prop | Templates.Cooling Circuit Diagnostics | Discharge Line Temperature | 2644 | 483 | 7025 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | N/A | -50 | 250 |  |  | 10ths | 0 | deg C | 507:62 | -45.6 | 121.1 | [7 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | 6 | Discharge Line Temperature | FDDApp.FDD.DLA_T | Present Value | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 1 | AV:30090 | IR:867 | AI:35 |  | Value |  |  | Views.Details.Cooling.Sensors | Discharge Line Temperature 1 | 2644 | 380 |  | Views.Details.Clg.Sensors | DLT1 | 2645 | 388
Prop | Templates.Cooling Circuit Diagnostics | High Pressure Limit | 1675 | 93 | 7026 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Alarm/Normal | 1696 | Enable | [6 empty] | Alarm/Normal | 1696 | [6 empty] | 1696 | 0 = Alarm 1 = Normal | High Pressure Unload Alarm | Attr | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | 6 | High Pressure Limit | FDDApp.FDD.Clg_En_1_HP_Unload_Src | Present Value | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 1 |  |  |  | C1 High Pressure Unload Alarm
Prop | Templates.Cooling Circuit Diagnostics | High Pressure Lockout | 1675 | 94 | 7027 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal Lockout | 1604 | Normal | [6 empty] | Normal Lockout | 1604 | [6 empty] | 1604 | 0 = Normal 1 = Lockout | High Pressure Unload Lockout | Attr | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | 6 | High Pressure Lockout | FDDApp.FDD.Clg_LO_1_HP_Unload_Src | Present Value | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 1 |  |  |  | C1 High Pressure Unload Lockout
Prop | Templates.Cooling Circuit Diagnostics | Low Pressure Limit | 1675 | 95 | 7028 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Alarm/Normal | 1696 | Enable | [6 empty] | Alarm/Normal | 1696 | [6 empty] | 1696 | 0 = Alarm 1 = Normal | Low Pressure Unload Alarm | Attr | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | 6 | Low Pressure Limit | FDDApp.FDD.Clg_En_1_LP_Unload_Src | Present Value | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 1 |  |  |  | C1 Low Pressure Unload Alarm
Prop | Templates.Cooling Circuit Diagnostics | Low Pressure Lockout | 1675 | 96 | 7029 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal Lockout | 1604 | Normal | [6 empty] | Normal Lockout | 1604 | [6 empty] | 1604 | 0 = Normal 1 = Lockout | Low Pressure Unload Lockout | Attr | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | 6 | Low Pressure Lockout | FDDApp.FDD.Clg_LO_1_LP_Unload_Src | Present Value | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 1 |  |  |  | C1 Low Pressure Unload Lockout
Tmpl | Templates.DX Cooling Circuit | [31 empty] | Model | York RTU.Cooling Control.DX Cooling Circuit 2 | 7 | [6 empty] | York RTU.Cooling Control.Cooling Stages Available:Present Value > 1
Prop | Templates.DX Cooling Circuit | Compressor Stage Number | 1675 | 83 | 7000 | TRUE | FALSE | FALSE | 17 | SignedInteger | 1s | 6 |  | 507:95 |  | 0 | 100 |  |  | 1s | 0 |  | 507:95 | 0 | 100 | [7 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 2 | 7 | Compressor Stage Number | EM Variable: 2 |  | FALSE
Prop | Templates.DX Cooling Circuit | Compressor Stage Command | 1675 | 84 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [5 empty] | Cooling Stage 1 ; Heat Pump Stage 1 Cooling Mode ; Heat Pump Stage 1 Heating Mode | 647 | 0 = Off 1 = On |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 2 | 7 | Compressor Stage Command | UCBapp.newUCB.COMP2_C | Present Value | FALSE |  |  |  | MV:29612 | IR:319 | BO:6 |  | Value |  |  | Views.Details.Cooling.Service.Stage 2 | Compressor Stage Command 2 | 1714 | 146 |  | Views.Details.Clg.Service.Stage 2 | C2 | 1709 | 128
Prop | Templates.DX Cooling Circuit | Compressor Stage Command | 1675 | 84 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [5 empty] | Cooling Stage 1 ; Heat Pump Stage 1 Cooling Mode ; Heat Pump Stage 1 Heating Mode | 647 | 0 = Off 1 = On |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 2 | 7 | Compressor Stage Command | UCBapp.newUCB.COMP2_C | Present Value | FALSE |  |  |  | MV:29612 | IR:319 | BO:6 |  | Value |  |  | Views.Details.FanVFD.Service | Compressor Stage Command 2 | 1714 | 146 |  | Views.Details.FanVFD.Service | C2 | 1709 | 128
Prop | Templates.DX Cooling Circuit | Compressor Stage Command | 1675 | 84 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [5 empty] | Cooling Stage 1 ; Heat Pump Stage 1 Cooling Mode ; Heat Pump Stage 1 Heating Mode | 647 | 0 = Off 1 = On |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 2 | 7 | Compressor Stage Command | UCBapp.newUCB.COMP2_C | Present Value | FALSE |  |  |  | MV:29612 | IR:319 | BO:6 |  | Value |  |  | Views.Details.Single Zone VAV.Service | Compressor Stage Command 2 | 1714 | 146 |  | Views.Details.SZ VAV.Service | C2 | 1709 | 128
Prop | Templates.DX Cooling Circuit | Compressor Stage Command | 1675 | 84 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [5 empty] | Cooling Stage 1 ; Heat Pump Stage 1 Cooling Mode ; Heat Pump Stage 1 Heating Mode | 647 | 0 = Off 1 = On |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 2 | 7 | Compressor Stage Command | UCBapp.newUCB.COMP2_C | Present Value | FALSE |  |  |  | MV:29612 | IR:319 | BO:6 |  | Value |  |  | Views.Details.Hot Gas Reheat.Service | Compressor Stage Command 2 | 1714 | 146 |  | Views.Details.HGR.Service | C2 | 1709 | 128
Prop | Templates.DX Cooling Circuit | Compressor Stage Command | 1675 | 84 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [5 empty] | Cooling Stage 1 ; Heat Pump Stage 1 Cooling Mode ; Heat Pump Stage 1 Heating Mode | 647 | 0 = Off 1 = On |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 2 | 7 | Compressor Stage Command | UCBapp.newUCB.COMP2_C | Present Value | FALSE |  |  |  | MV:29612 | IR:319 | BO:6 |  | Value |  |  | Views.Details.Mod Hot Gas Reheat.Service | Compressor Stage Command 2 | 1714 | 146 |  | Views.Details.ModHGR.Service | C2 | 1709 | 128
Prop | Templates.DX Cooling Circuit | Compressor Stage Status | 1675 | 85 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | SE RTU DX Cooling Circuit 1 Status | 1741 | Off_Idle | [6 empty] | SE RTU DX Cooling Circuit 1 Status | 1741 | [6 empty] | 1741 | 0 = Off-Idle 1 = On-Minimum On Time 2 = On-Normal Command 3 = Off-Cooling Is Disabled ... |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 2 | 7 | Compressor Stage Status | UCBapp.newUCB.Compressor_2_Stage_Status | Present Value | FALSE |  |  |  | MV:29616 | IR:320 | BI:18 |  | Value |  |  | Views.Details.Cooling.Service.Stage 2 | Compressor Stage 2 Status | 1714 | 55 |  | Views.Details.Clg.Service.Stage 2 | C2-S | 1709 | 132
Prop | Templates.DX Cooling Circuit | Compressor Stage Enabled | 1675 | 86 | 7003 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Yes/No | 1698 | Enable | [6 empty] | Yes/No | 1698 | [6 empty] | 1698 | 0 = Yes 1 = No |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 2 | 7 | Compressor Stage Enabled | UCBapp.newUCB.Compressor_Stage_2_Enabled | Relinquish Default | FALSE |  |  |  | MV:29620 | HR:102 | ADI:42 |  | Value |  |  | Views.Details.Cooling.Setup | Compressor Stage 2 Enabled | 1714 | 56 |  | Views.Details.Clg.Setup | C2-En | 1709 | 136
Prop | Templates.DX Cooling Circuit | Hot Gas Bypass Present | 1675 | 89 | 7004 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | [7 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 2 | 7 | Hot Gas Bypass Present | EM Variable: 0 |  | FALSE
Prop | Templates.DX Cooling Circuit | Compressor Stage Accumulated Runtime | 1675 | 90 | 7005 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | hours | 507:71 |  | 0 | 10000 |  |  | 1s | 0 | hours | 507:71 | 0 | 10000 | [7 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 2 | 7 | Compressor Stage Accumulated Runtime | 8-1/UCBApp.Clg_Runtime_2 | Present Value | FALSE |  |  |  | AV:29628 | IR:34 | ADF:57 |  | Value |  |  | Views.Details.Cooling.Service.Stage 2 | Compressor Stage Accumulated Runtime 2 | 1714 | 59 |  | Views.Details.Clg.Service.Stage 2 | C2RunTim | 1709 | 141
Prop | Templates.DX Cooling Circuit | Compressor Stage Accumulated Runtime | 1675 | 90 | 7005 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | hours | 507:71 |  | 0 | 10000 |  |  | 1s | 0 | hours | 507:71 | 0 | 10000 | [7 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 2 | 7 | Compressor Stage Accumulated Runtime | 8-1/UCBApp.Clg_Runtime_2 | Present Value | FALSE |  |  |  | AV:29628 | IR:34 | ADF:57 |  | Value |  |  | Views.Clone.Full Clone | Compressor Stage Accumulated Runtime 2 | 1714 | 59 |  |  | C2RunTim | 1709 | 141
Prop | Templates.DX Cooling Circuit | Compressor Stage Number Times On | 1675 | 91 | 7006 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 |  | 507:95 |  | 0 | 2000000 |  |  | 1s | 0 |  | 507:95 | 0 | 2000000 | [7 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 2 | 7 | Compressor Stage Number Times On | 8-1/UCBApp.Clg_Starts_2 | Relinquish Default | FALSE
Prop | Templates.DX Cooling Circuit | Min On Time Remaining | 1675 | 92 | 7007 | TRUE | FALSE | FALSE | 17 | SignedInteger | 1s | 6 | seconds | 507:73 | 0 |  |  |  |  | 1s | 0 | seconds | 507:73 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 2 | 7 | Min On Time Remaining | UCBapp.newUCB.Cool_Min_On_Time_Remaining_2 | Present Value | FALSE |  |  |  | AV:29632 | IR:166 | ADI:43 |  | Value |  |  | Views.Details.Cooling.Service.Stage 2 | Min On Time Remaining 2 | 1714 | 57 |  | Views.Details.Clg.Service.Stage 2 | C2OnTmr | 1709 | 149
Prop | Templates.DX Cooling Circuit | Anti-Short Cycle Delay Time Remaining | 1675 | 145 | 7008 | TRUE | FALSE | FALSE | 17 | SignedInteger | 1s | 6 | seconds | 507:73 | 0 |  |  |  |  | 1s | 0 | seconds | 507:73 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 2 | 7 | Anti-Short Cycle Delay Time Remaining | UCBapp.newUCB.Cool_Min_Off_Time_Remaining_2 | Present Value | FALSE |  |  |  | AV:29636 | IR:167 | ADI:44 |  | Value |  |  | Views.Details.Cooling.Service.Stage 2 | Anti-Short Cycle Delay Time Remaining 2 | 1714 | 58 |  | Views.Details.Clg.Service.Stage 2 | C2ASCDTmr | 1709 | 153
Prop | Templates.DX Cooling Circuit | High Pressure Limit | 1675 | 93 | 7009 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 2 | 7 | High Pressure Limit | UCBapp.newUCB.High_Pressure_Limit_2 | Present Value | FALSE |  |  |  | MV:29640 | IR:321 | BI:19 |  | Value |  |  | Views.Details.Cooling.Safeties | High Pressure Limit 2 | 1714 | 123 |  | Views.Details.Clg.Safeties | HPS2 | 1709 | 157
Prop | Templates.DX Cooling Circuit | High Pressure Lockout | 1675 | 94 | 7010 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal Lockout | 1604 | Normal | [6 empty] | Normal Lockout | 1604 | [6 empty] | 1604 | 0 = Normal 1 = Lockout |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 2 | 7 | High Pressure Lockout | UCBapp.newUCB.High_Pressure_Lockout_2 | Present Value | FALSE |  |  |  | MV:29644 | IR:322 | ADI:45 |  | Value |  |  | Views.Details.Cooling.Safeties | High Pressure Lockout 2 | 1714 | 133 |  | Views.Details.Clg.Safeties | HPS2-LO | 1709 | 161
Prop | Templates.DX Cooling Circuit | Low Pressure Limit | 1675 | 95 | 7011 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 2 | 7 | Low Pressure Limit | UCBapp.newUCB.Low_Pressure_Limit_2 | Present Value | FALSE |  |  |  | MV:29648 | IR:323 | BI:20 |  | Value |  |  | Views.Details.Cooling.Safeties | Low Pressure Limit 2 | 1714 | 124 |  | Views.Details.Clg.Safeties | LPS2 | 1709 | 165
Prop | Templates.DX Cooling Circuit | Low Pressure Lockout | 1675 | 96 | 7012 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal Lockout | 1604 | Normal | [6 empty] | Normal Lockout | 1604 | [6 empty] | 1604 | 0 = Normal 1 = Lockout |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 2 | 7 | Low Pressure Lockout | UCBapp.newUCB.Low_Pressure_Lockout_2 | Present Value | FALSE |  |  |  | MV:29652 | IR:324 | ADI:46 |  | Value |  |  | Views.Details.Cooling.Safeties | Low Pressure Lockout 2 | 1714 | 134 |  | Views.Details.Clg.Safeties | LPS2-LO | 1709 | 169
Prop | Templates.DX Cooling Circuit | Freeze Condition | 1675 | 97 | 7013 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 2 | 7 | Freeze Condition | UCBapp.newUCB.Freeze_Condition_2 | Present Value | FALSE |  |  |  | MV:29656 | IR:325 | BI:21 |  | Value |  |  | Views.Details.Cooling.Safeties | Freeze Condition 2 | 1714 | 135 |  | Views.Details.Clg.Safeties | FS2 | 1709 | 173
Prop | Templates.DX Cooling Circuit | Freeze Condition Lockout | 1675 | 98 | 7014 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal Lockout | 1604 | Normal | [6 empty] | Normal Lockout | 1604 | [6 empty] | 1604 | 0 = Normal 1 = Lockout |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 2 | 7 | Freeze Condition Lockout | UCBapp.newUCB.Freeze_Condition_Lockout_2 | Present Value | FALSE |  |  |  | MV:29660 | IR:326 | ADI:47 |  | Value |  |  | Views.Details.Cooling.Safeties | Freeze Condition Lockout 2 | 1714 | 136 |  | Views.Details.Clg.Safeties | FS2-LO | 1709 | 177
Prop | Templates.DX Cooling Circuit | Evaporator Coil Temp | 1675 | 100 | 7015 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | N/A |  |  |  |  | 10ths | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 2 | 7 | Evaporator Coil Temp | UCBapp.newUCB.EVAP2_T | Present Value | FALSE |  |  |  | AV:29664 | IR:168 | AI:7 |  | Value |  |  | Views.Details.Cooling.Sensors | Evaporator Coil Temp 2 | 1714 | 60 |  | Views.Details.Clg.Sensors | EC2 | 1709 | 181
Prop | Templates.DX Cooling Circuit | Condenser Coil Temp | 1675 | 102 | 7016 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | N/A |  |  |  |  | 10ths | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 2 | 7 | Condenser Coil Temp | UCBapp.newUCB.COND2_T | Present Value | FALSE |  |  |  | AV:29668 | IR:169 | AI:8 |  | Value |  |  | Views.Details.Cooling.Sensors | Condenser Coil Temp 2 | 1714 | 61 |  | Views.Details.Clg.Sensors | CC2 | 1709 | 185
Prop | Templates.DX Cooling Circuit | Condenser Coil Temp | 1675 | 102 | 7016 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | N/A |  |  |  |  | 10ths | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 2 | 7 | Condenser Coil Temp | UCBapp.newUCB.COND2_T | Present Value | FALSE |  |  |  | AV:29668 | IR:169 | AI:8 |  | Value |  |  | Views.Details.Heat Pump | Condenser Coil Temp 2 | 1714 | 61 |  | Views.Details.HeatPmp | CC2 | 1709 | 185
Prop | Templates.DX Cooling Circuit | Evaporator Coil Temp Sensor Fault | 1675 | 308 | 7017 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 2 | 7 | Evaporator Coil Temp Sensor Fault | UCBapp.newUCB.Evap_Coil_2_Temp_Sensor_Fault | Present Value | FALSE
Prop | Templates.DX Cooling Circuit | Condenser Coil Temp Sensor Fault | 1675 | 309 | 7018 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 2 | 7 | Condenser Coil Temp Sensor Fault | UCBapp.newUCB.Cond_Coil_2_Temp_Sensor_Fault | Present Value | FALSE
Prop | Templates.DX Cooling Circuit | Low Pressure Limit | 1675 | 95 | 7019 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 2 | 7 | Low Pressure Limit | UCBapp.newUCB.Low_Pressure_Alarm_2 | Present Value | FALSE
Tmpl | Templates.Cooling Circuit Diagnostics | [31 empty] | Model | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | 8 | [6 empty] | York RTU.System Controllers.FDD Manager Controller:Present Value <> Not Present
Prop | Templates.Cooling Circuit Diagnostics | Cooling Circuit Test Status | 1675 | 193 | 7000 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | SE FDD Codes | 1694 | [7 empty] | SE FDD Codes | 1694 | [6 empty] | 1694 | 0 = Unknown Status 1 = Basic Data Not Available Manual Entry 2 = Basic Data Not Available 3 = Return Wet Bulb Temp Not Available ... |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | 8 | Cooling Circuit Test Status | SE-FDD1001-05/FDSI FDD | Diagnostic Code Circuit 2 | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | MV:29830 | IR:344 | ADI:61 |  | Value |  |  | Views.Details.Cooling.Service.Stage 2 | Cooling Circuit Test Status | 1675 | 193 |  | Views.Details.Clg.Service.Stage 2 | ClgCktTestS-2 | 1709 | 479
Prop | Templates.Cooling Circuit Diagnostics | Suction Pressure | 1675 | 194 | 7001 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 6 | psi | 507:56 | N/A |  |  |  |  | 1s | 0 | kPa | 507:54 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | 8 | Suction Pressure | FDDApp.FDD.SLB_P | Present Value | FALSE |  |  |  | AV:29672 | IR:196 | AI:17 |  | Value |  |  | Views.Details.Cooling.Sensors | Suction Pressure 2 | 1714 | 62 |  | Views.Details.Clg.Sensors | SLP-2 | 1709 | 189
Prop | Templates.Cooling Circuit Diagnostics | Liquid Pressure | 1675 | 195 | 7002 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 6 | psi | 507:56 | N/A |  |  |  |  | 1s | 0 | kPa | 507:54 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | 8 | Liquid Pressure | FDDApp.FDD.DLB_P | Present Value | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | AV:29676 | IR:197 | AI:18 |  | Value |  |  | Views.Details.Cooling.Sensors | Liquid Pressure 2 | 1714 | 63 |  | Views.Details.Clg.Sensors | LLP-2 | 1709 | 193
Prop | Templates.Cooling Circuit Diagnostics | Suction Temperature | 1675 | 196 | 7003 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | N/A |  |  |  |  | 10ths | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | 8 | Suction Temperature | FDDApp.FDD.SLB_T | Present Value | FALSE |  |  |  | AV:29680 | IR:198 | AI:19 |  | Value |  |  | Views.Details.Cooling.Sensors | Suction Temperature 2 | 1714 | 64 |  | Views.Details.Clg.Sensors | SLT-2 | 1709 | 197
Prop | Templates.Cooling Circuit Diagnostics | Liquid Temperature | 1675 | 197 | 7004 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | N/A |  |  |  |  | 10ths | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | 8 | Liquid Temperature | FDDApp.FDD.DLB_T | Present Value | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | AV:29684 | IR:199 | AI:20 |  | Value |  |  | Views.Details.Cooling.Sensors | Liquid Temperature 2 | 1714 | 65 |  | Views.Details.Clg.Sensors | LLT-2 | 1709 | 201
Prop | Templates.Cooling Circuit Diagnostics | Superheat | 1675 | 198 | 7005 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | 8 | Superheat | SE-FDD1001-05/FDSI FDD | Superheat Value Circuit 2 | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | AV:29688 | IR:200 | ADF:74 |  | Value |  |  | Views.Details.Cooling.Service.Stage 2 | Superheat | 1675 | 198 |  | Views.Details.Clg.Service.Stage 2 | C2-SuperHeat | 1709 | 205
Prop | Templates.Cooling Circuit Diagnostics | Subcooling | 1675 | 199 | 7006 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | 8 | Subcooling | SE-FDD1001-05/FDSI FDD | Subcool Value Circuit 2 | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | AV:29692 | IR:201 | ADF:75 |  | Value |  |  | Views.Details.Cooling.Service.Stage 2 | Subcooling | 1675 | 199 |  | Views.Details.Clg.Service.Stage 2 | C2-SubCool | 1709 | 209
Prop | Templates.Cooling Circuit Diagnostics | Condensing Temperature over Ambient | 1675 | 200 | 7007 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | 8 | Condensing Temperature over Ambient | SE-FDD1001-05/FDSI FDD | Condense Temp Over Ambient Value Circuit 2 | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | AV:29696 | IR:202 | ADF:76 |  | Value |  |  | Views.Details.Cooling.Service.Stage 2 | Condensing Temperature over Ambient 2 | 1714 | 70 |  | Views.Details.Clg.Service.Stage 2 | C2-CondTempOvrAmb | 1709 | 213
Prop | Templates.Cooling Circuit Diagnostics | Efficiency Index | 1675 | 201 | 7008 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | [5 empty] | 1s | 0 | % | 507:98 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | 8 | Efficiency Index | SE-FDD1001-05/FDSI FDD | Efficiency Index Circuit 2 | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | AV:29700 | IR:203 | ADF:77 |  | Value |  |  | Views.Details.Cooling.Service.Stage 2 | Efficiency Index 2 | 1714 | 68 |  | Views.Details.Clg.Service.Stage 2 | C2-EI | 1709 | 217
Prop | Templates.Cooling Circuit Diagnostics | Capacity Index | 1675 | 202 | 7009 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | [5 empty] | 1s | 0 | % | 507:98 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | 8 | Capacity Index | SE-FDD1001-05/FDSI FDD | Capacity Index Circuit 2 | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | AV:29704 | IR:204 | ADF:78 |  | Value |  |  | Views.Details.Cooling.Service.Stage 2 | Capacity Index 2 | 1714 | 69 |  | Views.Details.Clg.Service.Stage 2 | C2-CI | 1709 | 221
Prop | Templates.Cooling Circuit Diagnostics | Suction Pressure Sensor Fault | 1675 | 331 | 7010 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | 8 | Suction Pressure Sensor Fault | FDDApp.FDD.SLP_Alarm_2_Src | Present Value | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 1
Prop | Templates.Cooling Circuit Diagnostics | Suction Temperature Sensor Fault | 1675 | 332 | 7011 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | 8 | Suction Temperature Sensor Fault | FDDApp.FDD.SLT_Alarm_2_Src | Present Value | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 1
Prop | Templates.Cooling Circuit Diagnostics | Discharge Pressure Sensor Fault | 1675 | 1681 | 7012 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm | Discharge Pressure Sensor Fault | Attr | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | 8 | Discharge Pressure Sensor Fault | FDDApp.FDD.DLP_Alarm_2_Src | Present Value | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 1 |  |  |  | Discharge Pressure circ2 Sensor Fault
Prop | Templates.Cooling Circuit Diagnostics | Discharge Temperature Sensor Fault | 1675 | 1682 | 7013 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm | Discharge Temperature Sensor Fault | Attr | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | 8 | Discharge Temperature Sensor Fault | FDDApp.FDD.DLT_Alarm_2_Src | Present Value | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 1 |  |  |  | Discharge Temperature cir2 Sensor Fault
Prop | Templates.Cooling Circuit Diagnostics | Evaporating Temp Value | 1675 | 424 | 7014 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | 8 | Evaporating Temp Value | SE-FDD1001-05/FDSI FDD | Evaporating Temperature Value Circuit 2 | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | AV:29834 | IR:205 | ADF:79 |  | Value |  |  | Views.Details.Cooling.Service.Stage 2 | Evaporating Temperature Value Circuit 2 | 1714 | 165 |  | Views.Details.Clg.Service.Stage 2 | C2-EvapTempValue | 1709 | 535
Prop | Templates.Cooling Circuit Diagnostics | Condenser Temperature Over Ambient High | 1675 | 440 | 7015 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | 8 | Condenser Temperature Over Ambient High | SE-FDD1001-05/FDSI FDD | Condense Temp Over Ambient High Limit Circuit 2 | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | AV:29850 | IR:206 | ADF:80
Prop | Templates.Cooling Circuit Diagnostics | Condenser Temperature Over Ambient Low | 1675 | 441 | 7016 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | 8 | Condenser Temperature Over Ambient Low | SE-FDD1001-05/FDSI FDD | Condense Temp Over Ambient Low Limit Circuit 2 | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | AV:29854 | IR:207 | ADF:81
Prop | Templates.Cooling Circuit Diagnostics | Superheat High | 1675 | 442 | 7017 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | 8 | Superheat High | SE-FDD1001-05/FDSI FDD | Superheat High Limit Circuit 2 | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | AV:29858 | IR:208 | ADF:82
Prop | Templates.Cooling Circuit Diagnostics | Superheat Low | 1675 | 443 | 7018 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | 8 | Superheat Low | SE-FDD1001-05/FDSI FDD | Superheat Low Limit Circuit 2 | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | AV:29862 | IR:209 | ADF:83
Prop | Templates.Cooling Circuit Diagnostics | Subcool High | 1675 | 444 | 7019 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | 8 | Subcool High | SE-FDD1001-05/FDSI FDD | Subcool High Limit Circuit 2 | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | AV:29866 | IR:210 | ADF:84
Prop | Templates.Cooling Circuit Diagnostics | Subcool Low | 1675 | 445 | 7020 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | 8 | Subcool Low | SE-FDD1001-05/FDSI FDD | Subcool Low Limit Circuit 2 | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | AV:29870 | IR:211 | ADF:85
Prop | Templates.Cooling Circuit Diagnostics | Evaporating Temperature High | 1675 | 446 | 7021 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | 8 | Evaporating Temperature High | SE-FDD1001-05/FDSI FDD | Evaporating Temperature High Limit Circuit 2 | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | AV:29874 | IR:212 | ADF:86
Prop | Templates.Cooling Circuit Diagnostics | Evaporating Temperature Low | 1675 | 447 | 7022 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | 8 | Evaporating Temperature Low | SE-FDD1001-05/FDSI FDD | Evaporating Temperature Low Limit Circuit 2 | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2 | AV:29878 | IR:213 | ADF:87
Prop | Templates.Cooling Circuit Diagnostics | Service Alarm | 1675 | 588 | 7023 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | CPO5 Alarms | 2594 | None | [6 empty] | CPO5 Alarms | 2594 | [6 empty] | 2594 | 0 = None 1 = Chiller 1 Interlock Alarm 2 = Chiller 2 Interlock Alarm 3 = Chiller 3 Interlock Alarm ... |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | 8 | Service Alarm | FDDApp.FDD.DIAGNOSTIC_CODE_CIRCUIT_2o | Present Value | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 2
Prop | Templates.Cooling Circuit Diagnostics | Discharge Line Pressure | 2644 | 482 | 7024 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 6 | psi | 507:56 | N/A | 0 | 750 |  |  | 1s | 0 | kPa | 507:54 | 0 | 5172 | [7 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | 8 | Discharge Line Pressure | FDDApp.FDD.DLB_P | Present Value | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 1 | AV:30091 | IR:868 | AI:36 |  | Value |  |  | Views.Details.Cooling.Sensors | Discharge Line Pressure 2 | 2644 | 379 |  | Views.Details.Clg.Sensors | DLP2 | 2645 | 387
Prop | Templates.Cooling Circuit Diagnostics | Discharge Line Temperature | 2644 | 483 | 7025 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | N/A | -50 | 250 |  |  | 10ths | 0 | deg C | 507:62 | -45.6 | 121.1 | [7 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | 8 | Discharge Line Temperature | FDDApp.FDD.DLB_T | Present Value | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 1 | AV:30092 | IR:869 | AI:37 |  | Value |  |  | Views.Details.Cooling.Sensors | Discharge Line Temperature 2 | 2644 | 381 |  | Views.Details.Clg.Sensors | DLT2 | 2645 | 389
Prop | Templates.Cooling Circuit Diagnostics | High Pressure Limit | 1675 | 93 | 7026 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Alarm/Normal | 1696 | Enable | [6 empty] | Alarm/Normal | 1696 | [6 empty] | 1696 | 0 = Alarm 1 = Normal | High Pressure Unload Alarm | Attr | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | 8 | High Pressure Limit | FDDApp.FDD.Clg_En_2_HP_Unload_Src | Present Value | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 1 |  |  |  | C2 High Pressure Unload Alarm
Prop | Templates.Cooling Circuit Diagnostics | High Pressure Lockout | 1675 | 94 | 7027 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal Lockout | 1604 | Normal | [6 empty] | Normal Lockout | 1604 | [6 empty] | 1604 | 0 = Normal 1 = Lockout | High Pressure Unload Lockout | Attr | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | 8 | High Pressure Lockout | FDDApp.FDD.Clg_LO_2_HP_Unload_Src | Present Value | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 1 |  |  |  | C2 High Pressure Unload Lockout
Prop | Templates.Cooling Circuit Diagnostics | Low Pressure Limit | 1675 | 95 | 7028 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Alarm/Normal | 1696 | Enable | [6 empty] | Alarm/Normal | 1696 | [6 empty] | 1696 | 0 = Alarm 1 = Normal | Low Pressure Unload Alarm | Attr | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | 8 | Low Pressure Limit | FDDApp.FDD.Clg_En_2_LP_Unload_Src | Present Value | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 1 |  |  |  | C2 Low Pressure Unload Alarm
Prop | Templates.Cooling Circuit Diagnostics | Low Pressure Lockout | 1675 | 96 | 7029 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal Lockout | 1604 | Normal | [6 empty] | Normal Lockout | 1604 | [6 empty] | 1604 | 0 = Normal 1 = Lockout | Low Pressure Unload Lockout | Attr | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | 8 | Low Pressure Lockout | FDDApp.FDD.Clg_LO_2_LP_Unload_Src | Present Value | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 1 |  |  |  | C2 Low Pressure Unload Lockout
Tmpl | Templates.DX Cooling Circuit | [31 empty] | Model | York RTU.Cooling Control.DX Cooling Circuit 3 | 9 | [6 empty] | UCBapp.newUCB.EFF_MAX_COOL_DISPLAY:Present Value > 2
Prop | Templates.DX Cooling Circuit | Compressor Stage Number | 1675 | 83 | 7000 | TRUE | FALSE | FALSE | 17 | SignedInteger | 1s | 6 |  | 507:95 |  | 0 | 100 |  |  | 1s | 0 |  | 507:95 | 0 | 100 | [7 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 3 | 9 | Compressor Stage Number | EM Variable: 3 |  | FALSE
Prop | Templates.DX Cooling Circuit | Compressor Stage Command | 1675 | 84 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [5 empty] | Cooling Stage 1 ; Heat Pump Stage 1 Cooling Mode ; Heat Pump Stage 1 Heating Mode | 647 | 0 = Off 1 = On |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 3 | 9 | Compressor Stage Command | FourStageApp.FourStage.CLG3_C | Present Value | FALSE |  |  |  | MV:29613 | IR:327 | BO:7 |  | Value |  |  | Views.Details.Cooling.Service.Stage 3 | Compressor Stage Command 3 | 1714 | 147 |  | Views.Details.Clg.Service.Stage 3 | C3 | 1709 | 129
Prop | Templates.DX Cooling Circuit | Compressor Stage Command | 1675 | 84 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [5 empty] | Cooling Stage 1 ; Heat Pump Stage 1 Cooling Mode ; Heat Pump Stage 1 Heating Mode | 647 | 0 = Off 1 = On |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 3 | 9 | Compressor Stage Command | FourStageApp.FourStage.CLG3_C | Present Value | FALSE |  |  |  | MV:29613 | IR:327 | BO:7 |  | Value |  |  | Views.Details.FanVFD.Service | Compressor Stage Command 3 | 1714 | 147 |  | Views.Details.FanVFD.Service | C3 | 1709 | 129
Prop | Templates.DX Cooling Circuit | Compressor Stage Command | 1675 | 84 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [5 empty] | Cooling Stage 1 ; Heat Pump Stage 1 Cooling Mode ; Heat Pump Stage 1 Heating Mode | 647 | 0 = Off 1 = On |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 3 | 9 | Compressor Stage Command | FourStageApp.FourStage.CLG3_C | Present Value | FALSE |  |  |  | MV:29613 | IR:327 | BO:7 |  | Value |  |  | Views.Details.Single Zone VAV.Service | Compressor Stage Command 3 | 1714 | 147 |  | Views.Details.SZ VAV.Service | C3 | 1709 | 129
Prop | Templates.DX Cooling Circuit | Compressor Stage Command | 1675 | 84 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [5 empty] | Cooling Stage 1 ; Heat Pump Stage 1 Cooling Mode ; Heat Pump Stage 1 Heating Mode | 647 | 0 = Off 1 = On |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 3 | 9 | Compressor Stage Command | FourStageApp.FourStage.CLG3_C | Present Value | FALSE |  |  |  | MV:29613 | IR:327 | BO:7 |  | Value |  |  | Views.Details.Hot Gas Reheat.Service | Compressor Stage Command 3 | 1714 | 147 |  | Views.Details.HGR.Service | C3 | 1709 | 129
Prop | Templates.DX Cooling Circuit | Compressor Stage Command | 1675 | 84 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [5 empty] | Cooling Stage 1 ; Heat Pump Stage 1 Cooling Mode ; Heat Pump Stage 1 Heating Mode | 647 | 0 = Off 1 = On |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 3 | 9 | Compressor Stage Command | FourStageApp.FourStage.CLG3_C | Present Value | FALSE |  |  |  | MV:29613 | IR:327 | BO:7 |  | Value |  |  | Views.Details.Mod Hot Gas Reheat.Service | Compressor Stage Command 3 | 1714 | 147 |  | Views.Details.ModHGR.Service | C3 | 1709 | 129
Prop | Templates.DX Cooling Circuit | Compressor Stage Status | 1675 | 85 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | SE RTU DX Cooling Circuit 1 Status | 1741 | Off_Idle | [6 empty] | SE RTU DX Cooling Circuit 1 Status | 1741 | [6 empty] | 1741 | 0 = Off-Idle 1 = On-Minimum On Time 2 = On-Normal Command 3 = Off-Cooling Is Disabled ... |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 3 | 9 | Compressor Stage Status | UCBapp.newUCB.Compressor_3_Stage_Status | Present Value | FALSE |  |  |  | MV:29617 | IR:328 | BI:22 |  | Value |  |  | Views.Details.Cooling.Service.Stage 3 | Compressor Stage 3 Status | 1714 | 71 |  | Views.Details.Clg.Service.Stage 3 | C3-S | 1709 | 133
Prop | Templates.DX Cooling Circuit | Compressor Stage Enabled | 1675 | 86 | 7003 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Yes/No | 1698 | Enable | [6 empty] | Yes/No | 1698 | [6 empty] | 1698 | 0 = Yes 1 = No |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 3 | 9 | Compressor Stage Enabled | UCBapp.newUCB.Compressor_Stage_3_Enabled | Relinquish Default | FALSE |  |  |  | MV:29621 | HR:103 | ADI:48 |  | Value |  |  | Views.Details.Cooling.Setup | Compressor Stage 3 Enabled | 1714 | 72 |  | Views.Details.Clg.Setup | C3-En | 1709 | 137
Prop | Templates.DX Cooling Circuit | Hot Gas Bypass Present | 1675 | 89 | 7004 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | [7 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 3 | 9 | Hot Gas Bypass Present | EM Variable: 0 |  | FALSE
Prop | Templates.DX Cooling Circuit | Compressor Stage Accumulated Runtime | 1675 | 90 | 7005 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | hours | 507:71 |  | 0 | 10000 |  |  | 1s | 0 | hours | 507:71 | 0 | 10000 | [7 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 3 | 9 | Compressor Stage Accumulated Runtime | 8-1/UCBApp.Clg_Runtime_3 | Present Value | FALSE |  |  |  | AV:29629 | IR:35 | ADF:58 |  | Value |  |  | Views.Details.Cooling.Service.Stage 3 | Compressor Stage Accumulated Runtime 3 | 1714 | 75 |  | Views.Details.Clg.Service.Stage 3 | C3RunTim | 1709 | 142
Prop | Templates.DX Cooling Circuit | Compressor Stage Accumulated Runtime | 1675 | 90 | 7005 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | hours | 507:71 |  | 0 | 10000 |  |  | 1s | 0 | hours | 507:71 | 0 | 10000 | [7 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 3 | 9 | Compressor Stage Accumulated Runtime | 8-1/UCBApp.Clg_Runtime_3 | Present Value | FALSE |  |  |  | AV:29629 | IR:35 | ADF:58 |  | Value |  |  | Views.Clone.Full Clone | Compressor Stage Accumulated Runtime 3 | 1714 | 75 |  |  | C3RunTim | 1709 | 142
Prop | Templates.DX Cooling Circuit | Compressor Stage Number Times On | 1675 | 91 | 7006 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 |  | 507:95 |  | 0 | 2000000 |  |  | 1s | 0 |  | 507:95 | 0 | 2000000 | [7 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 3 | 9 | Compressor Stage Number Times On | 8-1/UCBApp.Clg_Starts_3 | Relinquish Default | FALSE
Prop | Templates.DX Cooling Circuit | Min On Time Remaining | 1675 | 92 | 7007 | TRUE | FALSE | FALSE | 17 | SignedInteger | 1s | 6 | seconds | 507:73 | 0 |  |  |  |  | 1s | 0 | seconds | 507:73 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 3 | 9 | Min On Time Remaining | UCBapp.newUCB.Cool_Min_On_Time_Remaining_3 | Present Value | FALSE |  |  |  | AV:29633 | IR:170 | ADI:49 |  | Value |  |  | Views.Details.Cooling.Service.Stage 3 | Min On Time Remaining 3 | 1714 | 73 |  | Views.Details.Clg.Service.Stage 3 | C3OnTmr | 1709 | 150
Prop | Templates.DX Cooling Circuit | Anti-Short Cycle Delay Time Remaining | 1675 | 145 | 7008 | TRUE | FALSE | FALSE | 17 | SignedInteger | 1s | 6 | seconds | 507:73 | 0 |  |  |  |  | 1s | 0 | seconds | 507:73 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 3 | 9 | Anti-Short Cycle Delay Time Remaining | UCBapp.newUCB.Cool_Min_Off_Time_Remaining_3 | Present Value | FALSE |  |  |  | AV:29637 | IR:171 | ADI:50 |  | Value |  |  | Views.Details.Cooling.Service.Stage 3 | Anti-Short Cycle Delay Time Remaining 3 | 1714 | 74 |  | Views.Details.Clg.Service.Stage 3 | C3ASCDTmr | 1709 | 154
Prop | Templates.DX Cooling Circuit | High Pressure Limit | 1675 | 93 | 7009 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 3 | 9 | High Pressure Limit | UCBapp.newUCB.High_Pressure_Limit_3 | Present Value | FALSE |  |  | UCBapp.newUCB.Equipment_Configuration:Present Value < Tandem Cir1 With 2 Stage Cir2 | MV:29641 | IR:329 | BI:23 |  | Value |  |  | Views.Details.Cooling.Safeties | High Pressure Limit 3 | 1714 | 125 |  | Views.Details.Clg.Safeties | HPS3 | 1709 | 158
Prop | Templates.DX Cooling Circuit | High Pressure Lockout | 1675 | 94 | 7010 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal Lockout | 1604 | Normal | [6 empty] | Normal Lockout | 1604 | [6 empty] | 1604 | 0 = Normal 1 = Lockout |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 3 | 9 | High Pressure Lockout | UCBapp.newUCB.High_Pressure_Lockout_3 | Present Value | FALSE |  |  | UCBapp.newUCB.Equipment_Configuration:Present Value < Tandem Cir1 With 2 Stage Cir2 | MV:29645 | IR:330 | ADI:51 |  | Value |  |  | Views.Details.Cooling.Safeties | High Pressure Lockout 3 | 1714 | 137 |  | Views.Details.Clg.Safeties | HPS3-LO | 1709 | 162
Prop | Templates.DX Cooling Circuit | Low Pressure Limit | 1675 | 95 | 7011 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 3 | 9 | Low Pressure Limit | UCBapp.newUCB.Low_Pressure_Limit_3 | Present Value | FALSE |  |  | UCBapp.newUCB.Equipment_Configuration:Present Value < Tandem Cir1 With 2 Stage Cir2 | MV:29649 | IR:331 | BI:24 |  | Value |  |  | Views.Details.Cooling.Safeties | Low Pressure Limit 3 | 1714 | 126 |  | Views.Details.Clg.Safeties | LPS3 | 1709 | 166
Prop | Templates.DX Cooling Circuit | Low Pressure Lockout | 1675 | 96 | 7012 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal Lockout | 1604 | Normal | [6 empty] | Normal Lockout | 1604 | [6 empty] | 1604 | 0 = Normal 1 = Lockout |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 3 | 9 | Low Pressure Lockout | UCBapp.newUCB.Low_Pressure_Lockout_3 | Present Value | FALSE |  |  | UCBapp.newUCB.Equipment_Configuration:Present Value < Tandem Cir1 With 2 Stage Cir2 | MV:29653 | IR:332 | ADI:52 |  | Value |  |  | Views.Details.Cooling.Safeties | Low Pressure Lockout 3 | 1714 | 138 |  | Views.Details.Clg.Safeties | LPS3-LO | 1709 | 170
Prop | Templates.DX Cooling Circuit | Freeze Condition | 1675 | 97 | 7013 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 3 | 9 | Freeze Condition | UCBapp.newUCB.Freeze_Condition_3 | Present Value | FALSE |  |  | UCBapp.newUCB.Equipment_Configuration:Present Value < Tandem Cir1 With 2 Stage Cir2 | MV:29657 | IR:333 | BI:25 |  | Value |  |  | Views.Details.Cooling.Safeties | Freeze Condition 3 | 1714 | 139 |  | Views.Details.Clg.Safeties | FS3 | 1709 | 174
Prop | Templates.DX Cooling Circuit | Freeze Condition Lockout | 1675 | 98 | 7014 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal Lockout | 1604 | Normal | [6 empty] | Normal Lockout | 1604 | [6 empty] | 1604 | 0 = Normal 1 = Lockout |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 3 | 9 | Freeze Condition Lockout | UCBapp.newUCB.Freeze_Condition_Lockout_3 | Present Value | FALSE |  |  | UCBapp.newUCB.Equipment_Configuration:Present Value < Tandem Cir1 With 2 Stage Cir2 | MV:29661 | IR:334 | ADI:53 |  | Value |  |  | Views.Details.Cooling.Safeties | Freeze Condition Lockout 3 | 1714 | 140 |  | Views.Details.Clg.Safeties | FS3-LO | 1709 | 178
Prop | Templates.DX Cooling Circuit | Evaporator Coil Temp | 1675 | 100 | 7015 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | N/A |  |  |  |  | 10ths | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 3 | 9 | Evaporator Coil Temp | FourStageApp.FourStage.EVAP3_T | Present Value | FALSE |  |  | UCBapp.newUCB.Equipment_Configuration:Present Value < Tandem Cir1 With 2 Stage Cir2 | AV:29665 | IR:172 | AI:9 |  | Value |  |  | Views.Details.Cooling.Sensors | Evaporator Coil Temp 3 | 1714 | 76 |  | Views.Details.Clg.Sensors | EC3 | 1709 | 182
Prop | Templates.DX Cooling Circuit | Condenser Coil Temp | 1675 | 102 | 7016 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | N/A |  |  |  |  | 10ths | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 3 | 9 | Condenser Coil Temp | FourStageApp.FourStage.COND3_T | Present Value | FALSE |  |  | UCBapp.newUCB.Equipment_Configuration:Present Value < Tandem Cir1 With 2 Stage Cir2 | AV:29669 | IR:173 | AI:10 |  | Value |  |  | Views.Details.Cooling.Sensors | Condenser Coil Temp 3 | 1714 | 77 |  | Views.Details.Clg.Sensors | CC3 | 1709 | 186
Prop | Templates.DX Cooling Circuit | Evaporator Coil Temp Sensor Fault | 1675 | 308 | 7017 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 3 | 9 | Evaporator Coil Temp Sensor Fault | UCBapp.newUCB.Evap_Coil_3_Temp_Sensor_Fault | Present Value | FALSE |  |  | UCBapp.newUCB.Equipment_Configuration:Present Value < Tandem Cir1 With 2 Stage Cir2
Prop | Templates.DX Cooling Circuit | Condenser Coil Temp Sensor Fault | 1675 | 309 | 7018 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 3 | 9 | Condenser Coil Temp Sensor Fault | UCBapp.newUCB.Cond_Coil_3_Temp_Sensor_Fault | Present Value | FALSE |  |  | UCBapp.newUCB.Equipment_Configuration:Present Value < Tandem Cir1 With 2 Stage Cir2
Prop | Templates.DX Cooling Circuit | Low Pressure Limit | 1675 | 95 | 7019 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 3 | 9 | Low Pressure Limit | UCBapp.newUCB.Low_Pressure_Alarm_3 | Present Value | FALSE |  |  | UCBapp.newUCB.Equipment_Configuration:Present Value < Tandem Cir1 With 2 Stage Cir2
Tmpl | Templates.Cooling Circuit Diagnostics | [31 empty] | Model | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | 10 | [6 empty] | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value >= 1
Prop | Templates.Cooling Circuit Diagnostics | Cooling Circuit Test Status | 1675 | 193 | 7000 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | SE FDD Codes | 1694 | [7 empty] | SE FDD Codes | 1694 | [6 empty] | 1694 | 0 = Unknown Status 1 = Basic Data Not Available Manual Entry 2 = Basic Data Not Available 3 = Return Wet Bulb Temp Not Available ... |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | 10 | Cooling Circuit Test Status | SE-FDD1001-05/FDSI FDD | Diagnostic Code Circuit 3 | FALSE |  |  | York RTU.System Controllers.FDD Subordinate Controller:Present Value <> Not Present | MV:29831 | IR:345 | ADI:62 |  | Value |  |  | Views.Details.Cooling.Service.Stage 3 | Cooling Circuit Test Status | 1675 | 193 |  | Views.Details.Clg.Service.Stage 3 | ClgCktTestS-3 | 1709 | 480
Prop | Templates.Cooling Circuit Diagnostics | Suction Pressure | 1675 | 194 | 7001 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 6 | psi | 507:56 | [5 empty] | 1s | 0 | kPa | 507:54 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | 10 | Suction Pressure | FDDsApp.FDD.SLA_P | Present Value | FALSE |  |  | York RTU.System Controllers.FDD Subordinate Controller:Present Value <> Not Present | AV:29673 | IR:214 | AI:21 |  | Value |  |  | Views.Details.Cooling.Sensors | Suction Pressure 3 | 1714 | 78 |  | Views.Details.Clg.Sensors | SLP-3 | 1709 | 190
Prop | Templates.Cooling Circuit Diagnostics | Liquid Pressure | 1675 | 195 | 7002 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 6 | psi | 507:56 | [5 empty] | 1s | 0 | kPa | 507:54 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | 10 | Liquid Pressure | FDDsApp.FDD.DLA_P | Present Value | FALSE |  |  | York RTU.System Controllers.FDD Subordinate Controller:Present Value <> Not Present | AV:29677 | IR:215 | AI:22 |  | Value |  |  | Views.Details.Cooling.Sensors | Liquid Pressure 3 | 1714 | 79 |  | Views.Details.Clg.Sensors | LLP-3 | 1709 | 194
Prop | Templates.Cooling Circuit Diagnostics | Suction Temperature | 1675 | 196 | 7003 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | [5 empty] | 10ths | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | 10 | Suction Temperature | FDDsApp.FDD.SLA_T | Present Value | FALSE |  |  | York RTU.System Controllers.FDD Subordinate Controller:Present Value <> Not Present | AV:29681 | IR:216 | AI:23 |  | Value |  |  | Views.Details.Cooling.Sensors | Suction Temperature 3 | 1714 | 80 |  | Views.Details.Clg.Sensors | SLT-3 | 1709 | 198
Prop | Templates.Cooling Circuit Diagnostics | Liquid Temperature | 1675 | 197 | 7004 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | [5 empty] | 10ths | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | 10 | Liquid Temperature | FDDsApp.FDD.DLA_T | Present Value | FALSE |  |  | York RTU.System Controllers.FDD Subordinate Controller:Present Value <> Not Present | AV:29685 | IR:217 | AI:24 |  | Value |  |  | Views.Details.Cooling.Sensors | Liquid Temperature 3 | 1714 | 81 |  | Views.Details.Clg.Sensors | LLT-3 | 1709 | 202
Prop | Templates.Cooling Circuit Diagnostics | Superheat | 1675 | 198 | 7005 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | 10 | Superheat | SE-FDD1001-05/FDSI FDD | Superheat Value Circuit 3 | FALSE |  |  | York RTU.System Controllers.FDD Subordinate Controller:Present Value <> Not Present | AV:29689 | IR:218 | ADF:88 |  | Value |  |  | Views.Details.Cooling.Service.Stage 3 | Superheat | 1675 | 198 |  | Views.Details.Clg.Service.Stage 3 | C3-SuperHeat | 1709 | 206
Prop | Templates.Cooling Circuit Diagnostics | Subcooling | 1675 | 199 | 7006 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | 10 | Subcooling | SE-FDD1001-05/FDSI FDD | Subcool Value Circuit 3 | FALSE |  |  | York RTU.System Controllers.FDD Subordinate Controller:Present Value <> Not Present | AV:29693 | IR:219 | ADF:89 |  | Value |  |  | Views.Details.Cooling.Service.Stage 3 | Subcooling | 1675 | 199 |  | Views.Details.Clg.Service.Stage 3 | C3-SubCool | 1709 | 210
Prop | Templates.Cooling Circuit Diagnostics | Condensing Temperature over Ambient | 1675 | 200 | 7007 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | 10 | Condensing Temperature over Ambient | SE-FDD1001-05/FDSI FDD | Condense Temp Over Ambient Value Circuit 3 | FALSE |  |  | York RTU.System Controllers.FDD Subordinate Controller:Present Value <> Not Present | AV:29697 | IR:220 | ADF:90 |  | Value |  |  | Views.Details.Cooling.Service.Stage 3 | Condensing Temperature over Ambient 3 | 1714 | 86 |  | Views.Details.Clg.Service.Stage 3 | C3-CondTempOvrAmb | 1709 | 214
Prop | Templates.Cooling Circuit Diagnostics | Efficiency Index | 1675 | 201 | 7008 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | [5 empty] | 1s | 0 | % | 507:98 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | 10 | Efficiency Index | SE-FDD1001-05/FDSI FDD | Efficiency Index Circuit 3 | FALSE |  |  | York RTU.System Controllers.FDD Subordinate Controller:Present Value <> Not Present | AV:29701 | IR:221 | ADF:91 |  | Value |  |  | Views.Details.Cooling.Service.Stage 3 | Efficiency Index 3 | 1714 | 84 |  | Views.Details.Clg.Service.Stage 3 | C3-EI | 1709 | 218
Prop | Templates.Cooling Circuit Diagnostics | Capacity Index | 1675 | 202 | 7009 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | [5 empty] | 1s | 0 | % | 507:98 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | 10 | Capacity Index | SE-FDD1001-05/FDSI FDD | Capacity Index Circuit 3 | FALSE |  |  | York RTU.System Controllers.FDD Subordinate Controller:Present Value <> Not Present | AV:29705 | IR:222 | ADF:92 |  | Value |  |  | Views.Details.Cooling.Service.Stage 3 | Capacity Index 3 | 1714 | 85 |  | Views.Details.Clg.Service.Stage 3 | C3-CI | 1709 | 222
Prop | Templates.Cooling Circuit Diagnostics | Suction Pressure Sensor Fault | 1675 | 331 | 7010 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | [7 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | 10 | Suction Pressure Sensor Fault | EM Variable: 0 |  | FALSE
Prop | Templates.Cooling Circuit Diagnostics | Suction Temperature Sensor Fault | 1675 | 332 | 7011 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | [7 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | 10 | Suction Temperature Sensor Fault | EM Variable: 0 |  | FALSE
Prop | Templates.Cooling Circuit Diagnostics | Discharge Pressure Sensor Fault | 1675 | 1681 | 7012 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | [7 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm | Discharge Pressure Sensor Fault | Attr | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | 10 | Discharge Pressure Sensor Fault | EM Variable: 0 |  | FALSE
Prop | Templates.Cooling Circuit Diagnostics | Discharge Temperature Sensor Fault | 1675 | 1682 | 7013 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | [7 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm | Discharge Temperature Sensor Fault | Attr | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | 10 | Discharge Temperature Sensor Fault | EM Variable: 0 |  | FALSE
Prop | Templates.Cooling Circuit Diagnostics | Evaporating Temp Value | 1675 | 424 | 7014 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | 10 | Evaporating Temp Value | SE-FDD1001-05/FDSI FDD | Evaporating Temperature Value Circuit 3 | FALSE |  |  | York RTU.System Controllers.FDD Subordinate Controller:Present Value <> Not Present | AV:29835 | IR:223 | ADF:93 |  | Value |  |  | Views.Details.Cooling.Service.Stage 3 | Evaporating Temperature Value Circuit 3 | 1714 | 166 |  | Views.Details.Clg.Service.Stage 3 | C3-EvapTempValue | 1709 | 536
Prop | Templates.Cooling Circuit Diagnostics | Condenser Temperature Over Ambient High | 1675 | 440 | 7015 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | 10 | Condenser Temperature Over Ambient High | SE-FDD1001-05/FDSI FDD | Condense Temp Over Ambient High Limit Circuit 3 | FALSE |  |  | York RTU.System Controllers.FDD Subordinate Controller:Present Value <> Not Present | AV:29851 | IR:224 | ADF:94
Prop | Templates.Cooling Circuit Diagnostics | Condenser Temperature Over Ambient Low | 1675 | 441 | 7016 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | 10 | Condenser Temperature Over Ambient Low | SE-FDD1001-05/FDSI FDD | Condense Temp Over Ambient Low Limit Circuit 3 | FALSE |  |  | York RTU.System Controllers.FDD Subordinate Controller:Present Value <> Not Present | AV:29855 | IR:225 | ADF:95
Prop | Templates.Cooling Circuit Diagnostics | Superheat High | 1675 | 442 | 7017 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | 10 | Superheat High | SE-FDD1001-05/FDSI FDD | Superheat High Limit Circuit 3 | FALSE |  |  | York RTU.System Controllers.FDD Subordinate Controller:Present Value <> Not Present | AV:29859 | IR:226 | ADF:96
Prop | Templates.Cooling Circuit Diagnostics | Superheat Low | 1675 | 443 | 7018 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | 10 | Superheat Low | SE-FDD1001-05/FDSI FDD | Superheat Low Limit Circuit 3 | FALSE |  |  | York RTU.System Controllers.FDD Subordinate Controller:Present Value <> Not Present | AV:29863 | IR:227 | ADF:97
Prop | Templates.Cooling Circuit Diagnostics | Subcool High | 1675 | 444 | 7019 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | 10 | Subcool High | SE-FDD1001-05/FDSI FDD | Subcool High Limit Circuit 3 | FALSE |  |  | York RTU.System Controllers.FDD Subordinate Controller:Present Value <> Not Present | AV:29867 | IR:228 | ADF:98
Prop | Templates.Cooling Circuit Diagnostics | Subcool Low | 1675 | 445 | 7020 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | 10 | Subcool Low | SE-FDD1001-05/FDSI FDD | Subcool Low Limit Circuit 3 | FALSE |  |  | York RTU.System Controllers.FDD Subordinate Controller:Present Value <> Not Present | AV:29871 | IR:229 | ADF:99
Prop | Templates.Cooling Circuit Diagnostics | Evaporating Temperature High | 1675 | 446 | 7021 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | 10 | Evaporating Temperature High | SE-FDD1001-05/FDSI FDD | Evaporating Temperature High Limit Circuit 3 | FALSE |  |  | York RTU.System Controllers.FDD Subordinate Controller:Present Value <> Not Present | AV:29875 | IR:230 | ADF:100
Prop | Templates.Cooling Circuit Diagnostics | Evaporating Temperature Low | 1675 | 447 | 7022 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | 10 | Evaporating Temperature Low | SE-FDD1001-05/FDSI FDD | Evaporating Temperature Low Limit Circuit 3 | FALSE |  |  | York RTU.System Controllers.FDD Subordinate Controller:Present Value <> Not Present | AV:29879 | IR:231 | ADF:101
Prop | Templates.Cooling Circuit Diagnostics | Service Alarm | 1675 | 588 | 7023 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | CPO5 Alarms | 2594 | None | [6 empty] | CPO5 Alarms | 2594 | [6 empty] | 2594 | 0 = None 1 = Chiller 1 Interlock Alarm 2 = Chiller 2 Interlock Alarm 3 = Chiller 3 Interlock Alarm ... |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | 10 | Service Alarm | FDDApp.FDD.DIAGNOSTIC_CODE_CIRCUIT_3o | Present Value | FALSE |  |  | York RTU.System Controllers.FDD Subordinate Controller:Present Value <> Not Present
Prop | Templates.Cooling Circuit Diagnostics | Discharge Line Pressure | 2644 | 482 | 7024 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 6 | psi | 507:56 |  | 0 | 750 |  |  | 1s | 0 | kPa | 507:54 | 0 | 5172 | [7 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | 10 | Discharge Line Pressure | EM Variable: 0 |  | FALSE
Prop | Templates.Cooling Circuit Diagnostics | Discharge Line Temperature | 2644 | 483 | 7025 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 |  | -50 | 250 |  |  | 10ths | 0 | deg C | 507:62 | -45.6 | 121.1 | [7 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | 10 | Discharge Line Temperature | EM Variable: 0 |  | FALSE
Prop | Templates.Cooling Circuit Diagnostics | High Pressure Limit | 1675 | 93 | 7026 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Alarm/Normal | 1696 | Enable | [6 empty] | Alarm/Normal | 1696 | [6 empty] | 1696 | 0 = Alarm 1 = Normal | High Pressure Unload Alarm | Attr | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | 10 | High Pressure Limit | FDDApp.FDD.Clg_En_3_HP_Unload_Src | Present Value | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 1 |  |  |  | C3 High Pressure Unload Alarm
Prop | Templates.Cooling Circuit Diagnostics | High Pressure Lockout | 1675 | 94 | 7027 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal Lockout | 1604 | Normal | [6 empty] | Normal Lockout | 1604 | [6 empty] | 1604 | 0 = Normal 1 = Lockout | High Pressure Unload Lockout | Attr | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | 10 | High Pressure Lockout | FDDApp.FDD.Clg_LO_3_HP_Unload_Src | Present Value | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 1 |  |  |  | C3 High Pressure Unload Lockout
Prop | Templates.Cooling Circuit Diagnostics | Low Pressure Limit | 1675 | 95 | 7028 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Alarm/Normal | 1696 | Enable | [6 empty] | Alarm/Normal | 1696 | [6 empty] | 1696 | 0 = Alarm 1 = Normal | Low Pressure Unload Alarm | Attr | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | 10 | Low Pressure Limit | FDDApp.FDD.Clg_En_3_LP_Unload_Src | Present Value | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 1 |  |  |  | C3 Low Pressure Unload Alarm
Prop | Templates.Cooling Circuit Diagnostics | Low Pressure Lockout | 1675 | 96 | 7029 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal Lockout | 1604 | Normal | [6 empty] | Normal Lockout | 1604 | [6 empty] | 1604 | 0 = Normal 1 = Lockout | Low Pressure Unload Lockout | Attr | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | 10 | Low Pressure Lockout | FDDApp.FDD.Clg_LO_3_LP_Unload_Src | Present Value | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 1 |  |  |  | C3 Low Pressure Unload Lockout
Tmpl | Templates.DX Cooling Circuit | [31 empty] | Model | York RTU.Cooling Control.DX Cooling Circuit 4 | 11 | [6 empty] | UCBapp.newUCB.EFF_MAX_COOL_DISPLAY:Present Value > 3
Prop | Templates.DX Cooling Circuit | Compressor Stage Number | 1675 | 83 | 7000 | TRUE | FALSE | FALSE | 17 | SignedInteger | 1s | 6 |  | 507:95 |  | 0 | 100 |  |  | 1s | 0 |  | 507:95 | 0 | 100 | [7 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 4 | 11 | Compressor Stage Number | EM Variable: 4 |  | FALSE
Prop | Templates.DX Cooling Circuit | Compressor Stage Command | 1675 | 84 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [5 empty] | Cooling Stage 1 ; Heat Pump Stage 1 Cooling Mode ; Heat Pump Stage 1 Heating Mode | 647 | 0 = Off 1 = On |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 4 | 11 | Compressor Stage Command | FourStageApp.FourStage.CLG4_C | Present Value | FALSE |  |  |  | MV:29614 | IR:335 | BO:8 |  | Value |  |  | Views.Details.Cooling.Service.Stage 4 | Compressor Stage Command 4 | 1714 | 148 |  | Views.Details.Clg.Service.Stage 4 | C4 | 1709 | 130
Prop | Templates.DX Cooling Circuit | Compressor Stage Command | 1675 | 84 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [5 empty] | Cooling Stage 1 ; Heat Pump Stage 1 Cooling Mode ; Heat Pump Stage 1 Heating Mode | 647 | 0 = Off 1 = On |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 4 | 11 | Compressor Stage Command | FourStageApp.FourStage.CLG4_C | Present Value | FALSE |  |  |  | MV:29614 | IR:335 | BO:8 |  | Value |  |  | Views.Details.FanVFD.Service | Compressor Stage Command 4 | 1714 | 148 |  | Views.Details.FanVFD.Service | C4 | 1709 | 130
Prop | Templates.DX Cooling Circuit | Compressor Stage Command | 1675 | 84 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [5 empty] | Cooling Stage 1 ; Heat Pump Stage 1 Cooling Mode ; Heat Pump Stage 1 Heating Mode | 647 | 0 = Off 1 = On |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 4 | 11 | Compressor Stage Command | FourStageApp.FourStage.CLG4_C | Present Value | FALSE |  |  |  | MV:29614 | IR:335 | BO:8 |  | Value |  |  | Views.Details.Single Zone VAV.Service | Compressor Stage Command 4 | 1714 | 148 |  | Views.Details.SZ VAV.Service | C4 | 1709 | 130
Prop | Templates.DX Cooling Circuit | Compressor Stage Command | 1675 | 84 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [5 empty] | Cooling Stage 1 ; Heat Pump Stage 1 Cooling Mode ; Heat Pump Stage 1 Heating Mode | 647 | 0 = Off 1 = On |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 4 | 11 | Compressor Stage Command | FourStageApp.FourStage.CLG4_C | Present Value | FALSE |  |  |  | MV:29614 | IR:335 | BO:8 |  | Value |  |  | Views.Details.Hot Gas Reheat.Service | Compressor Stage Command 4 | 1714 | 148 |  | Views.Details.HGR.Service | C4 | 1709 | 130
Prop | Templates.DX Cooling Circuit | Compressor Stage Command | 1675 | 84 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [5 empty] | Cooling Stage 1 ; Heat Pump Stage 1 Cooling Mode ; Heat Pump Stage 1 Heating Mode | 647 | 0 = Off 1 = On |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 4 | 11 | Compressor Stage Command | FourStageApp.FourStage.CLG4_C | Present Value | FALSE |  |  |  | MV:29614 | IR:335 | BO:8 |  | Value |  |  | Views.Details.Mod Hot Gas Reheat.Service | Compressor Stage Command 4 | 1714 | 148 |  | Views.Details.ModHGR.Service | C4 | 1709 | 130
Prop | Templates.DX Cooling Circuit | Compressor Stage Status | 1675 | 85 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | SE RTU DX Cooling Circuit 1 Status | 1741 | Off_Idle | [6 empty] | SE RTU DX Cooling Circuit 1 Status | 1741 | [6 empty] | 1741 | 0 = Off-Idle 1 = On-Minimum On Time 2 = On-Normal Command 3 = Off-Cooling Is Disabled ... |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 4 | 11 | Compressor Stage Status | UCBapp.newUCB.Compressor_4_Stage_Status | Present Value | FALSE |  |  |  | MV:29618 | IR:336 | BI:26 |  | Value |  |  | Views.Details.Cooling.Service.Stage 4 | Compressor Stage 4 Status | 1714 | 87 |  | Views.Details.Clg.Service.Stage 4 | C4-S | 1709 | 134
Prop | Templates.DX Cooling Circuit | Compressor Stage Enabled | 1675 | 86 | 7003 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Yes/No | 1698 | Enable | [6 empty] | Yes/No | 1698 | [6 empty] | 1698 | 0 = Yes 1 = No |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 4 | 11 | Compressor Stage Enabled | UCBapp.newUCB.Compressor_Stage_4_Enabled | Relinquish Default | FALSE |  |  |  | MV:29622 | HR:104 | ADI:54 |  | Value |  |  | Views.Details.Cooling.Setup | Compressor Stage 4 Enabled | 1714 | 88 |  | Views.Details.Clg.Setup | C4-En | 1709 | 138
Prop | Templates.DX Cooling Circuit | Hot Gas Bypass Present | 1675 | 89 | 7004 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | [7 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 4 | 11 | Hot Gas Bypass Present | EM Variable: 0 |  | FALSE
Prop | Templates.DX Cooling Circuit | Compressor Stage Accumulated Runtime | 1675 | 90 | 7005 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | hours | 507:71 |  | 0 | 10000 |  |  | 1s | 0 | hours | 507:71 | 0 | 10000 | [7 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 4 | 11 | Compressor Stage Accumulated Runtime | 8-1/UCBApp.Clg_Runtime_4 | Present Value | FALSE |  |  |  | AV:29630 | IR:36 | ADF:59 |  | Value |  |  | Views.Details.Cooling.Service.Stage 4 | Compressor Stage Accumulated Runtime 4 | 1714 | 91 |  | Views.Details.Clg.Service.Stage 4 | C4RunTim | 1709 | 143
Prop | Templates.DX Cooling Circuit | Compressor Stage Accumulated Runtime | 1675 | 90 | 7005 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | hours | 507:71 |  | 0 | 10000 |  |  | 1s | 0 | hours | 507:71 | 0 | 10000 | [7 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 4 | 11 | Compressor Stage Accumulated Runtime | 8-1/UCBApp.Clg_Runtime_4 | Present Value | FALSE |  |  |  | AV:29630 | IR:36 | ADF:59 |  | Value |  |  | Views.Clone.Full Clone | Compressor Stage Accumulated Runtime 4 | 1714 | 91 |  |  | C4RunTim | 1709 | 143
Prop | Templates.DX Cooling Circuit | Compressor Stage Number Times On | 1675 | 91 | 7006 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 |  | 507:95 |  | 0 | 2000000 |  |  | 1s | 0 |  | 507:95 | 0 | 2000000 | [7 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 4 | 11 | Compressor Stage Number Times On | 8-1/UCBApp.Clg_Starts_4 | Relinquish Default | FALSE
Prop | Templates.DX Cooling Circuit | Min On Time Remaining | 1675 | 92 | 7007 | TRUE | FALSE | FALSE | 17 | SignedInteger | 1s | 6 | seconds | 507:73 | 0 |  |  |  |  | 1s | 0 | seconds | 507:73 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 4 | 11 | Min On Time Remaining | UCBapp.newUCB.Cool_Min_On_Time_Remaining_4 | Present Value | FALSE |  |  |  | AV:29634 | IR:174 | ADI:55 |  | Value |  |  | Views.Details.Cooling.Service.Stage 4 | Min On Time Remaining 4 | 1714 | 89 |  | Views.Details.Clg.Service.Stage 4 | C4OnTmr | 1709 | 151
Prop | Templates.DX Cooling Circuit | Anti-Short Cycle Delay Time Remaining | 1675 | 145 | 7008 | TRUE | FALSE | FALSE | 17 | SignedInteger | 1s | 6 | seconds | 507:73 | 0 |  |  |  |  | 1s | 0 | seconds | 507:73 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 4 | 11 | Anti-Short Cycle Delay Time Remaining | UCBapp.newUCB.Cool_Min_Off_Time_Remaining_4 | Present Value | FALSE |  |  |  | AV:29638 | IR:175 | ADI:56 |  | Value |  |  | Views.Details.Cooling.Service.Stage 4 | Anti-Short Cycle Delay Time Remaining 4 | 1714 | 90 |  | Views.Details.Clg.Service.Stage 4 | C4ASCDTmr | 1709 | 155
Prop | Templates.DX Cooling Circuit | High Pressure Limit | 1675 | 93 | 7009 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 4 | 11 | High Pressure Limit | UCBapp.newUCB.High_Pressure_Limit_4 | Present Value | FALSE |  |  | UCBapp.newUCB.Equipment_Configuration:Present Value < Tandem Cir1 With 2 Stage Cir2 | MV:29642 | IR:337 | BI:27 |  | Value |  |  | Views.Details.Cooling.Safeties | High Pressure Limit 4 | 1714 | 127 |  | Views.Details.Clg.Safeties | HPS4 | 1709 | 159
Prop | Templates.DX Cooling Circuit | High Pressure Lockout | 1675 | 94 | 7010 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal Lockout | 1604 | Normal | [6 empty] | Normal Lockout | 1604 | [6 empty] | 1604 | 0 = Normal 1 = Lockout |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 4 | 11 | High Pressure Lockout | UCBapp.newUCB.High_Pressure_Lockout_4 | Present Value | FALSE |  |  | UCBapp.newUCB.Equipment_Configuration:Present Value < Tandem Cir1 With 2 Stage Cir2 | MV:29646 | IR:338 | ADI:57 |  | Value |  |  | Views.Details.Cooling.Safeties | High Pressure Lockout 4 | 1714 | 141 |  | Views.Details.Clg.Safeties | HPS4-LO | 1709 | 163
Prop | Templates.DX Cooling Circuit | Low Pressure Limit | 1675 | 95 | 7011 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 4 | 11 | Low Pressure Limit | UCBapp.newUCB.Low_Pressure_Limit_4 | Present Value | FALSE |  |  | UCBapp.newUCB.Equipment_Configuration:Present Value < Tandem Cir1 With 2 Stage Cir2 | MV:29650 | IR:339 | BI:28 |  | Value |  |  | Views.Details.Cooling.Safeties | Low Pressure Limit 4 | 1714 | 128 |  | Views.Details.Clg.Safeties | LPS4 | 1709 | 167
Prop | Templates.DX Cooling Circuit | Low Pressure Lockout | 1675 | 96 | 7012 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal Lockout | 1604 | Normal | [6 empty] | Normal Lockout | 1604 | [6 empty] | 1604 | 0 = Normal 1 = Lockout |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 4 | 11 | Low Pressure Lockout | UCBapp.newUCB.Low_Pressure_Lockout_4 | Present Value | FALSE |  |  | UCBapp.newUCB.Equipment_Configuration:Present Value < Tandem Cir1 With 2 Stage Cir2 | MV:29654 | IR:340 | ADI:58 |  | Value |  |  | Views.Details.Cooling.Safeties | Low Pressure Lockout 4 | 1714 | 142 |  | Views.Details.Clg.Safeties | LPS4-LO | 1709 | 171
Prop | Templates.DX Cooling Circuit | Freeze Condition | 1675 | 97 | 7013 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 4 | 11 | Freeze Condition | UCBapp.newUCB.Freeze_Condition_4 | Present Value | FALSE |  |  | UCBapp.newUCB.Equipment_Configuration:Present Value < Tandem Cir1 With 2 Stage Cir2 | MV:29658 | IR:341 | BI:29 |  | Value |  |  | Views.Details.Cooling.Safeties | Freeze Condition 4 | 1714 | 143 |  | Views.Details.Clg.Safeties | FS4 | 1709 | 175
Prop | Templates.DX Cooling Circuit | Freeze Condition Lockout | 1675 | 98 | 7014 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal Lockout | 1604 | Normal | [6 empty] | Normal Lockout | 1604 | [6 empty] | 1604 | 0 = Normal 1 = Lockout |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 4 | 11 | Freeze Condition Lockout | UCBapp.newUCB.Freeze_Condition_Lockout_4 | Present Value | FALSE |  |  | UCBapp.newUCB.Equipment_Configuration:Present Value < Tandem Cir1 With 2 Stage Cir2 | MV:29662 | IR:342 | ADI:59 |  | Value |  |  | Views.Details.Cooling.Safeties | Freeze Condition Lockout 4 | 1714 | 144 |  | Views.Details.Clg.Safeties | FS4-LO | 1709 | 179
Prop | Templates.DX Cooling Circuit | Evaporator Coil Temp | 1675 | 100 | 7015 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | N/A |  |  |  |  | 10ths | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 4 | 11 | Evaporator Coil Temp | FourStageApp.FourStage.EVAP4_T | Present Value | FALSE |  |  | UCBapp.newUCB.Equipment_Configuration:Present Value < Tandem Cir1 With 2 Stage Cir2 | AV:29666 | IR:176 | AI:11 |  | Value |  |  | Views.Details.Cooling.Sensors | Evaporator Coil Temp 4 | 1714 | 92 |  | Views.Details.Clg.Sensors | EC4 | 1709 | 183
Prop | Templates.DX Cooling Circuit | Condenser Coil Temp | 1675 | 102 | 7016 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | N/A |  |  |  |  | 10ths | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 4 | 11 | Condenser Coil Temp | FourStageApp.FourStage.COND4_T | Present Value | FALSE |  |  | UCBapp.newUCB.Equipment_Configuration:Present Value < Tandem Cir1 With 2 Stage Cir2 | AV:29670 | IR:177 | AI:12 |  | Value |  |  | Views.Details.Cooling.Sensors | Condenser Coil Temp 4 | 1714 | 93 |  | Views.Details.Clg.Sensors | CC4 | 1709 | 187
Prop | Templates.DX Cooling Circuit | Evaporator Coil Temp Sensor Fault | 1675 | 308 | 7017 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 4 | 11 | Evaporator Coil Temp Sensor Fault | UCBapp.newUCB.Evap_Coil_4_Temp_Sensor_Fault | Present Value | FALSE |  |  | UCBapp.newUCB.Equipment_Configuration:Present Value = Tandem Cir1 With 2 Stage Cir2
Prop | Templates.DX Cooling Circuit | Condenser Coil Temp Sensor Fault | 1675 | 309 | 7018 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 4 | 11 | Condenser Coil Temp Sensor Fault | UCBapp.newUCB.Cond_Coil_4_Temp_Sensor_Fault | Present Value | FALSE |  |  | UCBapp.newUCB.Equipment_Configuration:Present Value < Tandem Cir1 With 2 Stage Cir2
Prop | Templates.DX Cooling Circuit | Low Pressure Limit | 1675 | 95 | 7019 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 4 | 11 | Low Pressure Limit | UCBapp.newUCB.Low_Pressure_Alarm_4 | Present Value | FALSE |  |  | UCBapp.newUCB.Equipment_Configuration:Present Value < Tandem Cir1 With 2 Stage Cir2
Tmpl | Templates.Cooling Circuit Diagnostics | [31 empty] | Model | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | 12 | [6 empty] | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value >= 1
Prop | Templates.Cooling Circuit Diagnostics | Cooling Circuit Test Status | 1675 | 193 | 7000 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | SE FDD Codes | 1694 | [7 empty] | SE FDD Codes | 1694 | [6 empty] | 1694 | 0 = Unknown Status 1 = Basic Data Not Available Manual Entry 2 = Basic Data Not Available 3 = Return Wet Bulb Temp Not Available ... |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | 12 | Cooling Circuit Test Status | SE-FDD1001-05/FDSI FDD | Diagnostic Code Circuit 4 | FALSE |  |  | York RTU.System Controllers.FDD Subordinate Controller:Present Value <> Not Present | MV:29832 | IR:346 | ADI:63 |  | Value |  |  | Views.Details.Cooling.Service.Stage 4 | Cooling Circuit Test Status | 1675 | 193 |  | Views.Details.Clg.Service.Stage 4 | ClgCktTestS-4 | 1709 | 481
Prop | Templates.Cooling Circuit Diagnostics | Suction Pressure | 1675 | 194 | 7001 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 6 | psi | 507:56 | [5 empty] | 1s | 0 | kPa | 507:54 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | 12 | Suction Pressure | FDDsApp.FDD.SLB_P | Present Value | FALSE |  |  | York RTU.System Controllers.FDD Subordinate Controller:Present Value <> Not Present | AV:29674 | IR:232 | AI:25 |  | Value |  |  | Views.Details.Cooling.Sensors | Suction Pressure 4 | 1714 | 94 |  | Views.Details.Clg.Sensors | SLP-4 | 1709 | 191
Prop | Templates.Cooling Circuit Diagnostics | Liquid Pressure | 1675 | 195 | 7002 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 6 | psi | 507:56 | [5 empty] | 1s | 0 | kPa | 507:54 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | 12 | Liquid Pressure | FDDsApp.FDD.DLB_P | Present Value | FALSE |  |  | York RTU.System Controllers.FDD Subordinate Controller:Present Value <> Not Present | AV:29678 | IR:233 | AI:26 |  | Value |  |  | Views.Details.Cooling.Sensors | Liquid Pressure 4 | 1714 | 95 |  | Views.Details.Clg.Sensors | LLP-4 | 1709 | 195
Prop | Templates.Cooling Circuit Diagnostics | Suction Temperature | 1675 | 196 | 7003 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | [5 empty] | 10ths | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | 12 | Suction Temperature | FDDsApp.FDD.SLB_T | Present Value | FALSE |  |  | York RTU.System Controllers.FDD Subordinate Controller:Present Value <> Not Present | AV:29682 | IR:234 | AI:27 |  | Value |  |  | Views.Details.Cooling.Sensors | Suction Temperature 4 | 1714 | 96 |  | Views.Details.Clg.Sensors | SLT-4 | 1709 | 199
Prop | Templates.Cooling Circuit Diagnostics | Liquid Temperature | 1675 | 197 | 7004 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | [5 empty] | 10ths | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | 12 | Liquid Temperature | FDDsApp.FDD.DLB_T | Present Value | FALSE |  |  | York RTU.System Controllers.FDD Subordinate Controller:Present Value <> Not Present | AV:29686 | IR:235 | AI:28 |  | Value |  |  | Views.Details.Cooling.Sensors | Liquid Temperature 4 | 1714 | 97 |  | Views.Details.Clg.Sensors | LLT-4 | 1709 | 203
Prop | Templates.Cooling Circuit Diagnostics | Superheat | 1675 | 198 | 7005 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | 12 | Superheat | SE-FDD1001-05/FDSI FDD | Superheat Value Circuit 4 | FALSE |  |  | York RTU.System Controllers.FDD Subordinate Controller:Present Value <> Not Present | AV:29690 | IR:236 | ADF:102 |  | Value |  |  | Views.Details.Cooling.Service.Stage 4 | Superheat | 1675 | 198 |  | Views.Details.Clg.Service.Stage 4 | C4-SuperHeat | 1709 | 207
Prop | Templates.Cooling Circuit Diagnostics | Subcooling | 1675 | 199 | 7006 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | 12 | Subcooling | SE-FDD1001-05/FDSI FDD | Subcool Value Circuit 4 | FALSE |  |  | York RTU.System Controllers.FDD Subordinate Controller:Present Value <> Not Present | AV:29694 | IR:237 | ADF:103 |  | Value |  |  | Views.Details.Cooling.Service.Stage 4 | Subcooling | 1675 | 199 |  | Views.Details.Clg.Service.Stage 4 | C4-SubCool | 1709 | 211
Prop | Templates.Cooling Circuit Diagnostics | Condensing Temperature over Ambient | 1675 | 200 | 7007 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | 12 | Condensing Temperature over Ambient | SE-FDD1001-05/FDSI FDD | Condense Temp Over Ambient Value Circuit 4 | FALSE |  |  | York RTU.System Controllers.FDD Subordinate Controller:Present Value <> Not Present | AV:29698 | IR:238 | ADF:104 |  | Value |  |  | Views.Details.Cooling.Service.Stage 4 | Condensing Temperature over Ambient 4 | 1714 | 102 |  | Views.Details.Clg.Service.Stage 4 | C4-CondTempOvrAmb | 1709 | 215
Prop | Templates.Cooling Circuit Diagnostics | Efficiency Index | 1675 | 201 | 7008 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | [5 empty] | 1s | 0 | % | 507:98 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | 12 | Efficiency Index | SE-FDD1001-05/FDSI FDD | Efficiency Index Circuit 4 | FALSE |  |  | York RTU.System Controllers.FDD Subordinate Controller:Present Value <> Not Present | AV:29702 | IR:239 | ADF:105 |  | Value |  |  | Views.Details.Cooling.Service.Stage 4 | Efficiency Index 4 | 1714 | 100 |  | Views.Details.Clg.Service.Stage 4 | C4-EI | 1709 | 219
Prop | Templates.Cooling Circuit Diagnostics | Capacity Index | 1675 | 202 | 7009 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | [5 empty] | 1s | 0 | % | 507:98 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | 12 | Capacity Index | SE-FDD1001-05/FDSI FDD | Capacity Index Circuit 4 | FALSE |  |  | York RTU.System Controllers.FDD Subordinate Controller:Present Value <> Not Present | AV:29706 | IR:240 | ADF:106 |  | Value |  |  | Views.Details.Cooling.Service.Stage 4 | Capacity Index 4 | 1714 | 101 |  | Views.Details.Clg.Service.Stage 4 | C4-CI | 1709 | 223
Prop | Templates.Cooling Circuit Diagnostics | Suction Pressure Sensor Fault | 1675 | 331 | 7010 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | [7 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | 12 | Suction Pressure Sensor Fault | EM Variable: 0 |  | FALSE
Prop | Templates.Cooling Circuit Diagnostics | Suction Temperature Sensor Fault | 1675 | 332 | 7011 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | [7 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | 12 | Suction Temperature Sensor Fault | EM Variable: 0 |  | FALSE
Prop | Templates.Cooling Circuit Diagnostics | Discharge Pressure Sensor Fault | 1675 | 1681 | 7012 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | [7 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm | Discharge Pressure Sensor Fault | Attr | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | 12 | Discharge Pressure Sensor Fault | EM Variable: 0 |  | FALSE
Prop | Templates.Cooling Circuit Diagnostics | Discharge Temperature Sensor Fault | 1675 | 1682 | 7013 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | [7 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm | Discharge Temperature Sensor Fault | Attr | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | 12 | Discharge Temperature Sensor Fault | EM Variable: 0 |  | FALSE
Prop | Templates.Cooling Circuit Diagnostics | Evaporating Temp Value | 1675 | 424 | 7014 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | 12 | Evaporating Temp Value | SE-FDD1001-05/FDSI FDD | Evaporating Temperature Value Circuit 4 | FALSE |  |  | York RTU.System Controllers.FDD Subordinate Controller:Present Value <> Not Present | AV:29836 | IR:241 | ADF:107 |  | Value |  |  | Views.Details.Cooling.Service.Stage 4 | Evaporating Temperature Value Circuit 4 | 1714 | 167 |  | Views.Details.Clg.Service.Stage 4 | C4-EvapTempValue | 1709 | 537
Prop | Templates.Cooling Circuit Diagnostics | Condenser Temperature Over Ambient High | 1675 | 440 | 7015 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | 12 | Condenser Temperature Over Ambient High | SE-FDD1001-05/FDSI FDD | Condense Temp Over Ambient High Limit Circuit 4 | FALSE |  |  | York RTU.System Controllers.FDD Subordinate Controller:Present Value <> Not Present | AV:29852 | IR:242 | ADF:108
Prop | Templates.Cooling Circuit Diagnostics | Condenser Temperature Over Ambient Low | 1675 | 441 | 7016 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | 12 | Condenser Temperature Over Ambient Low | SE-FDD1001-05/FDSI FDD | Condense Temp Over Ambient Low Limit Circuit 4 | FALSE |  |  | York RTU.System Controllers.FDD Subordinate Controller:Present Value <> Not Present | AV:29856 | IR:243 | ADF:109
Prop | Templates.Cooling Circuit Diagnostics | Superheat High | 1675 | 442 | 7017 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | 12 | Superheat High | SE-FDD1001-05/FDSI FDD | Superheat High Limit Circuit 4 | FALSE |  |  | York RTU.System Controllers.FDD Subordinate Controller:Present Value <> Not Present | AV:29860 | IR:244 | ADF:110
Prop | Templates.Cooling Circuit Diagnostics | Superheat Low | 1675 | 443 | 7018 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | 12 | Superheat Low | SE-FDD1001-05/FDSI FDD | Superheat Low Limit Circuit 4 | FALSE |  |  | York RTU.System Controllers.FDD Subordinate Controller:Present Value <> Not Present | AV:29864 | IR:245 | ADF:111
Prop | Templates.Cooling Circuit Diagnostics | Subcool High | 1675 | 444 | 7019 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | 12 | Subcool High | SE-FDD1001-05/FDSI FDD | Subcool High Limit Circuit 4 | FALSE |  |  | York RTU.System Controllers.FDD Subordinate Controller:Present Value <> Not Present | AV:29868 | IR:246 | ADF:112
Prop | Templates.Cooling Circuit Diagnostics | Subcool Low | 1675 | 445 | 7020 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | 12 | Subcool Low | SE-FDD1001-05/FDSI FDD | Subcool Low Limit Circuit 4 | FALSE |  |  | York RTU.System Controllers.FDD Subordinate Controller:Present Value <> Not Present | AV:29872 | IR:247 | ADF:113
Prop | Templates.Cooling Circuit Diagnostics | Evaporating Temperature High | 1675 | 446 | 7021 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | 12 | Evaporating Temperature High | SE-FDD1001-05/FDSI FDD | Evaporating Temperature High Limit Circuit 4 | FALSE |  |  | York RTU.System Controllers.FDD Subordinate Controller:Present Value <> Not Present | AV:29876 | IR:248 | ADF:114
Prop | Templates.Cooling Circuit Diagnostics | Evaporating Temperature Low | 1675 | 447 | 7022 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | [5 empty] | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | 12 | Evaporating Temperature Low | SE-FDD1001-05/FDSI FDD | Evaporating Temperature Low Limit Circuit 4 | FALSE |  |  | York RTU.System Controllers.FDD Subordinate Controller:Present Value <> Not Present | AV:29880 | IR:249 | ADF:115
Prop | Templates.Cooling Circuit Diagnostics | Service Alarm | 1675 | 588 | 7023 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | CPO5 Alarms | 2594 | None | [6 empty] | CPO5 Alarms | 2594 | [6 empty] | 2594 | 0 = None 1 = Chiller 1 Interlock Alarm 2 = Chiller 2 Interlock Alarm 3 = Chiller 3 Interlock Alarm ... |  | Attr | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | 12 | Service Alarm | FDDApp.FDD.DIAGNOSTIC_CODE_CIRCUIT_4o | Present Value | FALSE |  |  | York RTU.System Controllers.FDD Subordinate Controller:Present Value <> Not Present
Prop | Templates.Cooling Circuit Diagnostics | Discharge Line Pressure | 2644 | 482 | 7024 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 6 | psi | 507:56 |  | 0 | 750 |  |  | 1s | 0 | kPa | 507:54 | 0 | 5172 | [7 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | 12 | Discharge Line Pressure | EM Variable: 0 |  | FALSE
Prop | Templates.Cooling Circuit Diagnostics | Discharge Line Temperature | 2644 | 483 | 7025 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 |  | -50 | 250 |  |  | 10ths | 0 | deg C | 507:62 | -45.6 | 121.1 | [7 empty] | Attr | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | 12 | Discharge Line Temperature | EM Variable: 0 |  | FALSE
Prop | Templates.Cooling Circuit Diagnostics | High Pressure Limit | 1675 | 93 | 7026 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Alarm/Normal | 1696 | Enable | [6 empty] | Alarm/Normal | 1696 | [6 empty] | 1696 | 0 = Alarm 1 = Normal | High Pressure Unload Alarm | Attr | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | 12 | High Pressure Limit | FDDApp.FDD.Clg_En_4_HP_Unload_Src | Present Value | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 1 |  |  |  | C4 High Pressure Unload Alarm
Prop | Templates.Cooling Circuit Diagnostics | High Pressure Lockout | 1675 | 94 | 7027 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal Lockout | 1604 | Normal | [6 empty] | Normal Lockout | 1604 | [6 empty] | 1604 | 0 = Normal 1 = Lockout | High Pressure Unload Lockout | Attr | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | 12 | High Pressure Lockout | FDDApp.FDD.Clg_LO_4_HP_Unload_Src | Present Value | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 1 |  |  |  | C4 High Pressure Unload Lockout
Prop | Templates.Cooling Circuit Diagnostics | Low Pressure Limit | 1675 | 95 | 7028 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Alarm/Normal | 1696 | Enable | [6 empty] | Alarm/Normal | 1696 | [6 empty] | 1696 | 0 = Alarm 1 = Normal | Low Pressure Unload Alarm | Attr | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | 12 | Low Pressure Limit | FDDApp.FDD.Clg_En_4_LP_Unload_Src | Present Value | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 1 |  |  |  | C4 Low Pressure Unload Alarm
Prop | Templates.Cooling Circuit Diagnostics | Low Pressure Lockout | 1675 | 96 | 7029 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal Lockout | 1604 | Normal | [6 empty] | Normal Lockout | 1604 | [6 empty] | 1604 | 0 = Normal 1 = Lockout | Low Pressure Unload Lockout | Attr | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | 12 | Low Pressure Lockout | FDDApp.FDD.Clg_LO_4_LP_Unload_Src | Present Value | FALSE |  |  | UCBapp.newUCB.EFF_FDD_DISPLAY:Present Value = 1 |  |  |  | C4 Low Pressure Unload Lockout
Tmpl | Templates.Heating Control | [31 empty] | Model | York RTU.Heating Control | 13
Prop | Templates.Heating Control | Heating Mode Enabled For Operation | 1675 | 105 | 7000 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Enable | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Heating Control | 13 | Heating Mode Enabled For Operation | UCBapp.newUCB.HTG_EN | Relinquish Default | FALSE |  |  |  | MV:29707 | HR:105 | ADI:64 |  | Value |  |  | Views.Commissioning.Standard | Heating Mode Enabled For Operation | 1675 | 105 |  | Views.Commission.Standard | Htg-En | 1709 | 224
Prop | Templates.Heating Control | Heating Mode Enabled For Operation | 1675 | 105 | 7000 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Enable | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Heating Control | 13 | Heating Mode Enabled For Operation | UCBapp.newUCB.HTG_EN | Relinquish Default | FALSE |  |  |  | MV:29707 | HR:105 | ADI:64 |  | Value |  |  | Views.Commissioning.Options | Heating Mode Enabled For Operation | 1675 | 105 |  | Views.Commission.Options | Htg-En | 1709 | 224
Prop | Templates.Heating Control | Heating Mode Enabled For Operation | 1675 | 105 | 7000 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Enable | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Heating Control | 13 | Heating Mode Enabled For Operation | UCBapp.newUCB.HTG_EN | Relinquish Default | FALSE |  |  |  | MV:29707 | HR:105 | ADI:64 |  | Value |  |  | Views.Commissioning.Quick Start | Heating Mode Enabled For Operation | 1675 | 105 |  | Views.Commission.Quick Start | Htg-En | 1709 | 224
Prop | Templates.Heating Control | Heating Status | 1675 | 106 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | SE RTU Heating Control Status | 1742 | Off_Idle | [6 empty] | SE RTU Heating Control Status | 1742 | [6 empty] | 1742 | 0 = Off-Idle 1 = On-Defrost 2 = SAT Tempering 3 = Morning Warmup ... |  | Attr | York RTU.Heating Control | 13 | Heating Status | UCBapp.newUCB.Heating_Status | Present Value | FALSE |  |  |  | MV:29708 | IR:347 | ADI:65 |  | Value |  |  | Views.Details.Heating.Service | Heating Status | 1675 | 106 |  | Views.Details.Htg.Service | Htg-S | 1709 | 225
Prop | Templates.Heating Control | Heating Status | 1675 | 106 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | SE RTU Heating Control Status | 1742 | Off_Idle | [6 empty] | SE RTU Heating Control Status | 1742 | [6 empty] | 1742 | 0 = Off-Idle 1 = On-Defrost 2 = SAT Tempering 3 = Morning Warmup ... |  | Attr | York RTU.Heating Control | 13 | Heating Status | UCBapp.newUCB.Heating_Status | Present Value | FALSE |  |  |  | MV:29708 | IR:347 | ADI:65 |  | Value |  |  | Views.Details.FanVFD.Service | Heating Status | 1675 | 106 |  | Views.Details.FanVFD.Service | Htg-S | 1709 | 225
Prop | Templates.Heating Control | Heating Status | 1675 | 106 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | SE RTU Heating Control Status | 1742 | Off_Idle | [6 empty] | SE RTU Heating Control Status | 1742 | [6 empty] | 1742 | 0 = Off-Idle 1 = On-Defrost 2 = SAT Tempering 3 = Morning Warmup ... |  | Attr | York RTU.Heating Control | 13 | Heating Status | UCBapp.newUCB.Heating_Status | Present Value | FALSE |  |  |  | MV:29708 | IR:347 | ADI:65 |  | Value |  |  | Views.Commissioning.Quick Start | Heating Status | 1675 | 106 |  | Views.Commission.Quick Start | Htg-S | 1709 | 225
Prop | Templates.Heating Control | Heating Status | 1675 | 106 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | SE RTU Heating Control Status | 1742 | Off_Idle | [6 empty] | SE RTU Heating Control Status | 1742 | [6 empty] | 1742 | 0 = Off-Idle 1 = On-Defrost 2 = SAT Tempering 3 = Morning Warmup ... |  | Attr | York RTU.Heating Control | 13 | Heating Status | UCBapp.newUCB.Heating_Status | Present Value | FALSE |  |  |  | MV:29708 | IR:347 | ADI:65 |  | Value |  |  | Views.Status.Status | Heating Status | 1675 | 106 |  | Views.Status.Status | Htg-S | 1709 | 225
Prop | Templates.Heating Control | SAT Air Temp Limit for Heating Enabled | 1675 | 108 | 7002 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | TRUE | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Heating Control | 13 | SAT Air Temp Limit for Heating Enabled | UCBapp.newUCB.SAT_Air_Temp_Lim_for_Heat_En | Relinquish Default | FALSE |  |  |  | MV:29709 | HR:106 | ADI:66 |  | Value |  |  | Views.Commissioning.Options | SAT Air Temp Limit for Heating Enabled | 1675 | 108 |  | Views.Commission.Options | SATHtgLimit-En | 1709 | 226
Prop | Templates.Heating Control | SAT Air Temp Limit for Heating Enabled | 1675 | 108 | 7002 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | TRUE | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Heating Control | 13 | SAT Air Temp Limit for Heating Enabled | UCBapp.newUCB.SAT_Air_Temp_Lim_for_Heat_En | Relinquish Default | FALSE |  |  |  | MV:29709 | HR:106 | ADI:66 |  | Value |  |  | Views.Details.Heating.Setup | SAT Air Temp Limit for Heating Enabled | 1675 | 108 |  | Views.Details.Htg.Setup | SATHtgLimit-En | 1709 | 226
Prop | Templates.Heating Control | SAT Air Temp Limit For Heating Setpoint | 1675 | 109 | 7003 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 140 | 100 | 180 |  |  | 1s | 0 | deg C | 507:62 | 38 | 82 | [7 empty] | Attr | York RTU.Heating Control | 13 | SAT Air Temp Limit For Heating Setpoint | UCBapp.newUCB.SAT_Air_Temp_Lim_For_Heat_SP | Relinquish Default | FALSE |  |  |  | AV:29710 | HR:37 | ADF:116 |  | Value |  |  | Views.Commissioning.Options | SAT Air Temp Limit For Heating Setpoint | 1675 | 109 |  | Views.Commission.Options | SATHtgLimit-Sp | 1709 | 227
Prop | Templates.Heating Control | SAT Air Temp Limit For Heating Setpoint | 1675 | 109 | 7003 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 140 | 100 | 180 |  |  | 1s | 0 | deg C | 507:62 | 38 | 82 | [7 empty] | Attr | York RTU.Heating Control | 13 | SAT Air Temp Limit For Heating Setpoint | UCBapp.newUCB.SAT_Air_Temp_Lim_For_Heat_SP | Relinquish Default | FALSE |  |  |  | AV:29710 | HR:37 | ADF:116 |  | Value |  |  | Views.Details.Heating.Setup | SAT Air Temp Limit For Heating Setpoint | 1675 | 109 |  | Views.Details.Htg.Setup | SATHtgLimit-Sp | 1709 | 227
Prop | Templates.Heating Control | Outdoor Air Temp Heating Cutout Setpoint | 1675 | 110 | 7004 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 75 | 0 | 100 |  |  | 1s | 0 | deg C | 507:62 | -18 | 38 | [7 empty] | Attr | York RTU.Heating Control | 13 | Outdoor Air Temp Heating Cutout Setpoint | UCBapp.newUCB.OA_Heating_Lockout_SP | Relinquish Default | FALSE |  |  |  | AV:29711 | HR:38 | ADF:117 |  | Value |  |  | Views.Commissioning.Options | Outdoor Air Temp Heating Cutout Setpoint | 1675 | 110 |  | Views.Commission.Options | HtgOATCutout-Sp | 1709 | 228
Prop | Templates.Heating Control | Outdoor Air Temp Heating Cutout Setpoint | 1675 | 110 | 7004 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 75 | 0 | 100 |  |  | 1s | 0 | deg C | 507:62 | -18 | 38 | [7 empty] | Attr | York RTU.Heating Control | 13 | Outdoor Air Temp Heating Cutout Setpoint | UCBapp.newUCB.OA_Heating_Lockout_SP | Relinquish Default | FALSE |  |  |  | AV:29711 | HR:38 | ADF:117 |  | Value |  |  | Views.Details.Heating.Setup | Outdoor Air Temp Heating Cutout Setpoint | 1675 | 110 |  | Views.Details.Htg.Setup | HtgOATCutout-Sp | 1709 | 228
Prop | Templates.Heating Control | Hot Water Freeze Stat | 1675 | 203 | 7005 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | N/A | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Heating Control | 13 | Hot Water Freeze Stat | FourStageApp.FourStage.HW_FREEZE_S | Present Value | FALSE |  |  | York RTU.Heating Control Type:Present Value = Proportional | MV:29712 | IR:348 | ADI:67 |  | Value |  |  | Views.Details.Heating.Proportional.Service | Hot Water Freeze Stat | 1675 | 203 |  | Views.Details.Htg.Prop.Service | FSHW | 1709 | 229
Prop | Templates.Heating Control | Gas Valve1 Input | 1675 | 118 | 7006 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [6 empty] | 647 | 0 = Off 1 = On |  | Attr | York RTU.Heating Control | 13 | Gas Valve1 Input | UCBapp.newUCB.GV1_S | Present Value | FALSE |  |  | York RTU.Heating Control.Number of Gas Valves Installed:Present Value > 0 | MV:29713 | IR:349 | BI:30 |  | Value |  |  | Views.Details.Heating.Safeties | Gas Valve1 Input | 1675 | 118 |  | Views.Details.Htg.Safeties | MV | 1709 | 230
Prop | Templates.Heating Control | Gas Valve2 Input | 1675 | 119 | 7007 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [6 empty] | 647 | 0 = Off 1 = On |  | Attr | York RTU.Heating Control | 13 | Gas Valve2 Input | FourStageApp.FourStage.GV_2 | Present Value | FALSE |  |  | York RTU.System Controllers.4 Stage Controller:Present Value <> Not Present | MV:29714 | IR:350 | BI:31 |  | Value |  |  | Views.Details.Heating.Safeties | Gas Valve2 Input | 1675 | 119 |  | Views.Details.Htg.Safeties | GV2 | 1709 | 231
Prop | Templates.Heating Control | Gas Valve3 Input | 1675 | 120 | 7008 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [6 empty] | 647 | 0 = Off 1 = On |  | Attr | York RTU.Heating Control | 13 | Gas Valve3 Input | FourStageApp.FourStage.GV_3 | Present Value | FALSE |  |  | York RTU.System Controllers.4 Stage Controller:Present Value <> Not Present | MV:29715 | IR:351 | BI:32 |  | Value |  |  | Views.Details.Heating.Safeties | Gas Valve3 Input | 1675 | 120 |  | Views.Details.Htg.Safeties | GV3 | 1709 | 232
Prop | Templates.Heating Control | Heat Limit1 Switch | 1675 | 121 | 7009 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Heating Control | 13 | Heat Limit1 Switch | UCBapp.newUCB.Heat_Limit1_Switch | Present Value | FALSE |  |  | York RTU.Heating Control.Number of Limit Switches:Present Value > 0 | MV:29716 | IR:352 | BI:33 |  | Value |  |  | Views.Details.Heating.Safeties | Heat Limit1 Switch | 1675 | 121 |  | Views.Details.Htg.Safeties | Limit | 1709 | 233
Prop | Templates.Heating Control | Heat Limit1 Switch Lockout | 1675 | 122 | 7010 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal Lockout | 1604 | Normal | [6 empty] | Normal Lockout | 1604 | [6 empty] | 1604 | 0 = Normal 1 = Lockout |  | Attr | York RTU.Heating Control | 13 | Heat Limit1 Switch Lockout | UCBapp.newUCB.Heat_Limit1_Switch_Lockout | Present Value | FALSE |  |  |  | MV:29717 | IR:353 | ADI:68 |  | Value |  |  | Views.Details.Heating.Safeties | Heat Limit1 Switch Lockout | 1675 | 122 |  | Views.Details.Htg.Safeties | LimitLO | 1709 | 234
Prop | Templates.Heating Control | Heat Limit2 Switch | 1675 | 123 | 7011 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Heating Control | 13 | Heat Limit2 Switch | UCBapp.newUCB.Heat_Limit2_Switch | Present Value | FALSE |  |  | York RTU.System Controllers.4 Stage Controller:Present Value <> Not Present | MV:29718 | IR:354 | BI:34 |  | Value |  |  | Views.Details.Heating.Safeties | Heat Limit2 Switch | 1675 | 123 |  | Views.Details.Htg.Safeties | Lim2 | 1709 | 235
Prop | Templates.Heating Control | Heat Limit2 Switch Lockout | 1675 | 124 | 7012 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal Lockout | 1604 | Normal | [6 empty] | Normal Lockout | 1604 | [6 empty] | 1604 | 0 = Normal 1 = Lockout |  | Attr | York RTU.Heating Control | 13 | Heat Limit2 Switch Lockout | UCBapp.newUCB.Heat_Limit2_Switch_Lockout | Present Value | FALSE |  |  | York RTU.System Controllers.4 Stage Controller:Present Value <> Not Present | MV:29719 | IR:355 | ADI:69 |  | Value |  |  | Views.Details.Heating.Safeties | Heat Limit2 Switch Lockout | 1675 | 124 |  | Views.Details.Htg.Safeties | Lim2LO | 1709 | 236
Prop | Templates.Heating Control | Heat Limit3 Switch | 1675 | 125 | 7013 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Heating Control | 13 | Heat Limit3 Switch | UCBapp.newUCB.Heat_Limit3_Switch | Present Value | FALSE |  |  | York RTU.System Controllers.4 Stage Controller:Present Value <> Not Present | MV:29720 | IR:356 | BI:35 |  | Value |  |  | Views.Details.Heating.Safeties | Heat Limit3 Switch | 1675 | 125 |  | Views.Details.Htg.Safeties | Lim3 | 1709 | 237
Prop | Templates.Heating Control | Heat Limit3 Switch Lockout | 1675 | 126 | 7014 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal Lockout | 1604 | Normal | [6 empty] | Normal Lockout | 1604 | [6 empty] | 1604 | 0 = Normal 1 = Lockout |  | Attr | York RTU.Heating Control | 13 | Heat Limit3 Switch Lockout | UCBapp.newUCB.Heat_Limit3_Switch_Lockout | Present Value | FALSE |  |  | York RTU.System Controllers.4 Stage Controller:Present Value <> Not Present | MV:29721 | IR:357 | ADI:70 |  | Value |  |  | Views.Details.Heating.Safeties | Heat Limit3 Switch Lockout | 1675 | 126 |  | Views.Details.Htg.Safeties | Lim3LO | 1709 | 238
Prop | Templates.Heating Control | VAV Occupied Heating Enabled | 1675 | 204 | 7015 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Available | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Heating Control | 13 | VAV Occupied Heating Enabled | UCBapp.newUCB.VAV_Occ_Heating_Enabled | Relinquish Default | FALSE |  |  | York RTU.Fan Control.Fan Control Type:Present Value = Variable Speed | MV:29722 | HR:107 | ADI:71 |  | Value |  |  | Views.Details.FanVFD.Setup | VAV Occupied Heating Enabled | 1675 | 204 |  | Views.Details.FanVFD.Setup | HtgOcc-En | 1709 | 239
Prop | Templates.Heating Control | VAV Occupied Heating Enabled | 1675 | 204 | 7015 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Available | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Heating Control | 13 | VAV Occupied Heating Enabled | UCBapp.newUCB.VAV_Occ_Heating_Enabled | Relinquish Default | FALSE |  |  | York RTU.Fan Control.Fan Control Type:Present Value = Variable Speed | MV:29722 | HR:107 | ADI:71 |  | Value |  |  | Views.Clone.Partial Clone 1 | VAV Occupied Heating Enabled | 1675 | 204 |  |  | HtgOcc-En | 1709 | 239
Prop | Templates.Heating Control | VAV Occupied Heating Setpoint | 1675 | 205 | 7016 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 68 | 40 | 85 |  |  | 1s | 0 | deg C | 507:62 | 4 | 30 | [7 empty] | Attr | York RTU.Heating Control | 13 | VAV Occupied Heating Setpoint | UCBapp.newUCB.Occ_Htg_Setpoint | Relinquish Default | FALSE |  |  | UCBapp.newUCB.Setpoint_Input_Presence:Present Value = Curve 2 | AV:29723 | HR:39 | ADF:118 |  | Value |  |  | Views.Details.FanVFD.Setup | VAV Occupied Heating Setpoint | 1675 | 205 |  | Views.Details.FanVFD.Setup | VAVHtgOcc-SP | 1709 | 240
Prop | Templates.Heating Control | VAV Occupied Heating Setpoint | 1675 | 205 | 7016 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 68 | 40 | 85 |  |  | 1s | 0 | deg C | 507:62 | 4 | 30 | [7 empty] | Attr | York RTU.Heating Control | 13 | VAV Occupied Heating Setpoint | UCBapp.newUCB.Occ_Htg_Setpoint | Relinquish Default | FALSE |  |  | UCBapp.newUCB.Setpoint_Input_Presence:Present Value = Curve 2 | AV:29723 | HR:39 | ADF:118 |  | Value |  |  | Views.Clone.Partial Clone 1 | VAV Occupied Heating Setpoint | 1675 | 205 |  |  | VAVHtgOcc-SP | 1709 | 240
Prop | Templates.Heating Control | VAV Occupied Heating Setpoint | 1675 | 205 | 7016 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 68 | 40 | 85 |  |  | 1s | 0 | deg C | 507:62 | 4 | 30 | [7 empty] | Attr | York RTU.Heating Control | 13 | VAV Occupied Heating Setpoint | UCBapp.newUCB.Occ_Htg_Setpoint | Relinquish Default | FALSE |  |  | UCBapp.newUCB.Setpoint_Input_Presence:Present Value = Curve 2 | AV:29723 | HR:39 | ADF:118 |  | Value |  |  | Views.Details.Heating.Setup | VAV Occupied Heating Setpoint | 1675 | 205 |  | Views.Details.Htg.Setup | VAVHtgOcc-SP | 1709 | 240
Prop | Templates.Heating Control | Unoccupied Heating Enabled | 1675 | 206 | 7017 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Enable | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Heating Control | 13 | Unoccupied Heating Enabled | UCBapp.newUCB.Unoccupied_Heating_Enabled | Relinquish Default | FALSE |  |  |  | MV:29724 | HR:108 | ADI:72 |  | Value |  |  | Views.Details.FanVFD.Setup | Unoccupied Heating Enabled | 1675 | 206 |  | Views.Details.FanVFD.Setup | HtgUnocc-En | 1709 | 241
Prop | Templates.Heating Control | Unoccupied Heating Enabled | 1675 | 206 | 7017 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Enable | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Heating Control | 13 | Unoccupied Heating Enabled | UCBapp.newUCB.Unoccupied_Heating_Enabled | Relinquish Default | FALSE |  |  |  | MV:29724 | HR:108 | ADI:72 |  | Value |  |  | Views.Clone.Partial Clone 1 | Unoccupied Heating Enabled | 1675 | 206 |  |  | HtgUnocc-En | 1709 | 241
Prop | Templates.Heating Control | VAV Unoccupied Heating Setpoint | 1675 | 207 | 7018 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 60 | 45 | 98 |  |  | 1s | 0 | deg C | 507:62 | 7 | 36 | [7 empty] | Attr | York RTU.Heating Control | 13 | VAV Unoccupied Heating Setpoint | UCBapp.newUCB.Unocc_Htg_Setpoint | Relinquish Default | FALSE |  |  | UCBapp.newUCB.Setpoint_Input_Presence:Present Value = Curve 2 | AV:29725 | HR:40 | ADF:119 |  | Value |  |  | Views.Details.FanVFD.Setup | VAV Unoccupied Heating Setpoint | 1675 | 207 |  | Views.Details.FanVFD.Setup | VAVHtgUnocc-Sp | 1709 | 242
Prop | Templates.Heating Control | VAV Unoccupied Heating Setpoint | 1675 | 207 | 7018 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 60 | 45 | 98 |  |  | 1s | 0 | deg C | 507:62 | 7 | 36 | [7 empty] | Attr | York RTU.Heating Control | 13 | VAV Unoccupied Heating Setpoint | UCBapp.newUCB.Unocc_Htg_Setpoint | Relinquish Default | FALSE |  |  | UCBapp.newUCB.Setpoint_Input_Presence:Present Value = Curve 2 | AV:29725 | HR:40 | ADF:119 |  | Value |  |  | Views.Clone.Partial Clone 1 | VAV Unoccupied Heating Setpoint | 1675 | 207 |  |  | VAVHtgUnocc-Sp | 1709 | 242
Prop | Templates.Heating Control | VAV Unoccupied Heating Setpoint | 1675 | 207 | 7018 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 60 | 45 | 98 |  |  | 1s | 0 | deg C | 507:62 | 7 | 36 | [7 empty] | Attr | York RTU.Heating Control | 13 | VAV Unoccupied Heating Setpoint | UCBapp.newUCB.Unocc_Htg_Setpoint | Relinquish Default | FALSE |  |  | UCBapp.newUCB.Setpoint_Input_Presence:Present Value = Curve 2 | AV:29725 | HR:40 | ADF:119 |  | Value |  |  | Views.Details.Heating.Setup | VAV Unoccupied Heating Setpoint | 1675 | 207 |  | Views.Details.Htg.Setup | VAVHtgUnocc-Sp | 1709 | 242
Prop | Templates.Heating Control | VAV Operating Heating Setpoint | 1675 | 208 | 7019 | TRUE | FALSE | FALSE | 4 | Float | 100ths | 4 | deg F | 507:64 | 68 |  |  |  |  | 100ths | 0 | deg C | 507:62 | [5 empty] | Alternate Heating Setpoint |  |  |  | Attr | York RTU.Heating Control | 13 | VAV Operating Heating Setpoint | UCBapp.newUCB.Operating_Heating_Setpoint | Present Value | FALSE |  |  | UCBapp.newUCB.Opr_Setpoint_Presence:Present Value >= Curve 2 | AV:29726 | IR:250 | ADF:120 |  | Value |  |  | Views.Details.Heating.Proportional.Service | VAV Operating Heating Setpoint | 1675 | 208 |  | Views.Details.Htg.Prop.Service | VAVOprHtg-Sp | 1709 | 243
Prop | Templates.Heating Control | VAV Operating Heating Setpoint | 1675 | 208 | 7019 | TRUE | FALSE | FALSE | 4 | Float | 100ths | 4 | deg F | 507:64 | 68 |  |  |  |  | 100ths | 0 | deg C | 507:62 | [5 empty] | Alternate Heating Setpoint |  |  |  | Attr | York RTU.Heating Control | 13 | VAV Operating Heating Setpoint | UCBapp.newUCB.Operating_Heating_Setpoint | Present Value | FALSE |  |  | UCBapp.newUCB.Opr_Setpoint_Presence:Present Value >= Curve 2 | AV:29726 | IR:250 | ADF:120 |  | Value |  |  | Views.Details.FanVFD.Service | VAV Operating Heating Setpoint | 1675 | 208 |  | Views.Details.FanVFD.Service | VAVOprHtg-Sp | 1709 | 243
Prop | Templates.Heating Control | VAV Operating Heating Setpoint | 1675 | 208 | 7019 | TRUE | FALSE | FALSE | 4 | Float | 100ths | 4 | deg F | 507:64 | 68 |  |  |  |  | 100ths | 0 | deg C | 507:62 | [5 empty] | Alternate Heating Setpoint |  |  |  | Attr | York RTU.Heating Control | 13 | VAV Operating Heating Setpoint | UCBapp.newUCB.Operating_Heating_Setpoint | Present Value | FALSE |  |  | UCBapp.newUCB.Opr_Setpoint_Presence:Present Value >= Curve 2 | AV:29726 | IR:250 | ADF:120 |  | Value |  |  | Views.Details.Single Zone VAV.Service | SZ VAV Operating Heating Setpoint | 1675 | 647 |  | Views.Details.SZ VAV.Service | OprSZVAVHtg-Sp | 1709 | 661
Prop | Templates.Heating Control | VAV Operating Heating Setpoint | 1675 | 208 | 7019 | TRUE | FALSE | FALSE | 4 | Float | 100ths | 4 | deg F | 507:64 | 68 |  |  |  |  | 100ths | 0 | deg C | 507:62 | [5 empty] | Alternate Heating Setpoint |  |  |  | Attr | York RTU.Heating Control | 13 | VAV Operating Heating Setpoint | UCBapp.newUCB.Operating_Heating_Setpoint | Present Value | FALSE |  |  | UCBapp.newUCB.Opr_Setpoint_Presence:Present Value >= Curve 2 | AV:29726 | IR:250 | ADF:120 |  | Value |  |  | Views.Details.Heating.Service | VAV Operating Heating Setpoint | 1675 | 208 |  | Views.Details.Htg.Service | VAVOprHtg-Sp | 1709 | 243
Prop | Templates.Heating Control | Morning Warmup Enabled | 1675 | 209 | 7020 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Disable | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Heating Control | 13 | Morning Warmup Enabled | UCBapp.newUCB.Morning_Warmup_Enabled | Relinquish Default | FALSE |  |  | York RTU.Thermostat Control.Thermostat Only Control Enabled:Present Value = No | MV:29822 | HR:109 | ADI:73 |  | Value |  |  | Views.Commissioning.Options | Morning Warmup Enabled | 1675 | 209 |  | Views.Commission.Options | MornW-En | 1709 | 244
Prop | Templates.Heating Control | Morning Warmup Enabled | 1675 | 209 | 7020 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Disable | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Heating Control | 13 | Morning Warmup Enabled | UCBapp.newUCB.Morning_Warmup_Enabled | Relinquish Default | FALSE |  |  | York RTU.Thermostat Control.Thermostat Only Control Enabled:Present Value = No | MV:29822 | HR:109 | ADI:73 |  | Value |  |  | Views.Details.FanVFD.Setup | Morning Warmup Enabled | 1675 | 209 |  | Views.Details.FanVFD.Setup | MornW-En | 1709 | 244
Prop | Templates.Heating Control | Morning Warmup Enabled | 1675 | 209 | 7020 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Disable | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Heating Control | 13 | Morning Warmup Enabled | UCBapp.newUCB.Morning_Warmup_Enabled | Relinquish Default | FALSE |  |  | York RTU.Thermostat Control.Thermostat Only Control Enabled:Present Value = No | MV:29822 | HR:109 | ADI:73 |  | Value |  |  | Views.Clone.Partial Clone 1 | Morning Warmup Enabled | 1675 | 209 |  |  | MornW-En | 1709 | 244
Prop | Templates.Heating Control | Morning Warmup/Return Air Temp Setpoint | 1675 | 210 | 7021 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 70 | 50 | 85 |  |  | 1s | 0 | deg C | 507:62 | 10 | 30 | [7 empty] | Attr | York RTU.Heating Control | 13 | Morning Warmup/Return Air Temp Setpoint | UCBapp.newUCB.Morning_Warm_Up_Setpoint | Relinquish Default | FALSE |  |  | York RTU.Thermostat Control.Thermostat Only Control Enabled:Present Value = No | AV:29823 | HR:41 | ADF:121 |  | Value |  |  | Views.Details.FanVFD.Setup | Morning Warmup/Return Air Temp Setpoint | 1675 | 210 |  | Views.Details.FanVFD.Setup | MornWRAT-Sp | 1709 | 245
Prop | Templates.Heating Control | Morning Warmup/Return Air Temp Setpoint | 1675 | 210 | 7021 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 70 | 50 | 85 |  |  | 1s | 0 | deg C | 507:62 | 10 | 30 | [7 empty] | Attr | York RTU.Heating Control | 13 | Morning Warmup/Return Air Temp Setpoint | UCBapp.newUCB.Morning_Warm_Up_Setpoint | Relinquish Default | FALSE |  |  | York RTU.Thermostat Control.Thermostat Only Control Enabled:Present Value = No | AV:29823 | HR:41 | ADF:121 |  | Value |  |  | Views.Clone.Partial Clone 1 | Morning Warmup/Return Air Temp Setpoint | 1675 | 210 |  |  | MornWRAT-Sp | 1709 | 245
Prop | Templates.Heating Control | VAV Box Heat Command | 1675 | 211 | 7022 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [6 empty] | 647 | 0 = Off 1 = On |  | Attr | York RTU.Heating Control | 13 | VAV Box Heat Command | FourStageApp.FourStage.VAV_HTG_C | Present Value | FALSE |  |  | UCBapp.newUCB.VAV_Heat_Command_Presence:Present Value = Active | MV:29727 | IR:358 | BO:9 |  | Value |  |  | Views.Details.FanVFD.Service | VAV Box Heat Command | 1675 | 211 |  | Views.Details.FanVFD.Service | VAV Box | 1709 | 246
Prop | Templates.Heating Control | CV Occupied Heating Setpoint | 1675 | 212 | 7023 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 68 | 46 | 99 |  |  | 1s | 0 | deg C | 507:62 | 8 | 37 |  |  |  | Occupied Heating Setpoint |  |  |  | Attr | York RTU.Heating Control | 13 | CV Occupied Heating Setpoint | UCBapp.newUCB.Occ_Htg_Setpoint | Relinquish Default | FALSE |  |  | UCBapp.newUCB.Setpoint_Input_Presence:Present Value = Curve 1 | AV:29728 | HR:42 | ADF:122 |  | Value |  |  | Views.Details.Heating.Setup | CV Occupied Heating Setpoint | 1675 | 212 |  | Views.Details.Htg.Setup | CVHtgOcc-SP | 1709 | 461
Prop | Templates.Heating Control | CV Occupied Heating Setpoint | 1675 | 212 | 7023 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 68 | 46 | 99 |  |  | 1s | 0 | deg C | 507:62 | 8 | 37 |  |  |  | Occupied Heating Setpoint |  |  |  | Attr | York RTU.Heating Control | 13 | CV Occupied Heating Setpoint | UCBapp.newUCB.Occ_Htg_Setpoint | Relinquish Default | FALSE |  |  | UCBapp.newUCB.Setpoint_Input_Presence:Present Value = Curve 1 | AV:29728 | HR:42 | ADF:122 |  | Value |  |  | Views.Details.Heating.Proportional.Service | CV Occupied Heating Setpoint | 1675 | 212 |  | Views.Details.Htg.Prop.Service | CVHtgOcc-SP | 1709 | 461
Prop | Templates.Heating Control | CV Occupied Heating Setpoint | 1675 | 212 | 7023 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 68 | 46 | 99 |  |  | 1s | 0 | deg C | 507:62 | 8 | 37 |  |  |  | Occupied Heating Setpoint |  |  |  | Attr | York RTU.Heating Control | 13 | CV Occupied Heating Setpoint | UCBapp.newUCB.Occ_Htg_Setpoint | Relinquish Default | FALSE |  |  | UCBapp.newUCB.Setpoint_Input_Presence:Present Value = Curve 1 | AV:29728 | HR:42 | ADF:122 |  | Value |  |  | Views.Clone.Partial Clone 1 | CV Occupied Heating Setpoint | 1675 | 212 |  |  | CVHtgOcc-SP | 1709 | 461
Prop | Templates.Heating Control | CV Unoccupied Heating Setpoint | 1675 | 213 | 7024 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 60 | 45 | 98 |  |  | 1s | 0 | deg C | 507:62 | 7 | 36 |  |  |  | Unoccupied Heating Setpoint |  |  |  | Attr | York RTU.Heating Control | 13 | CV Unoccupied Heating Setpoint | UCBapp.newUCB.Unocc_Htg_Setpoint | Relinquish Default | FALSE |  |  | UCBapp.newUCB.Setpoint_Input_Presence:Present Value = Curve 1 | AV:29729 | HR:43 | ADF:123 |  | Value |  |  | Views.Details.Heating.Setup | CV Unoccupied Heating Setpoint | 1675 | 213 |  | Views.Details.Htg.Setup | CVHtgUnocc-Sp | 1709 | 462
Prop | Templates.Heating Control | CV Unoccupied Heating Setpoint | 1675 | 213 | 7024 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 60 | 45 | 98 |  |  | 1s | 0 | deg C | 507:62 | 7 | 36 |  |  |  | Unoccupied Heating Setpoint |  |  |  | Attr | York RTU.Heating Control | 13 | CV Unoccupied Heating Setpoint | UCBapp.newUCB.Unocc_Htg_Setpoint | Relinquish Default | FALSE |  |  | UCBapp.newUCB.Setpoint_Input_Presence:Present Value = Curve 1 | AV:29729 | HR:43 | ADF:123 |  | Value |  |  | Views.Details.Heating.Proportional.Service | CV Unoccupied Heating Setpoint | 1675 | 213 |  | Views.Details.Htg.Prop.Service | CVHtgUnocc-Sp | 1709 | 462
Prop | Templates.Heating Control | CV Unoccupied Heating Setpoint | 1675 | 213 | 7024 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 60 | 45 | 98 |  |  | 1s | 0 | deg C | 507:62 | 7 | 36 |  |  |  | Unoccupied Heating Setpoint |  |  |  | Attr | York RTU.Heating Control | 13 | CV Unoccupied Heating Setpoint | UCBapp.newUCB.Unocc_Htg_Setpoint | Relinquish Default | FALSE |  |  | UCBapp.newUCB.Setpoint_Input_Presence:Present Value = Curve 1 | AV:29729 | HR:43 | ADF:123 |  | Value |  |  | Views.Clone.Partial Clone 1 | CV Unoccupied Heating Setpoint | 1675 | 213 |  |  | CVHtgUnocc-Sp | 1709 | 462
Prop | Templates.Heating Control | CV Operating Heating Setpoint | 1675 | 214 | 7025 | TRUE | FALSE | FALSE | 4 | Float | 100ths | 4 | deg F | 507:64 | 68 |  |  |  |  | 100ths | 0 | deg C | 507:62 | [5 empty] | Heating Setpoint |  |  |  | Attr | York RTU.Heating Control | 13 | CV Operating Heating Setpoint | UCBapp.newUCB.Operating_Heating_Setpoint | Present Value | FALSE |  |  | UCBapp.newUCB.Opr_Setpoint_Presence:Present Value = Curve 1 | AV:29730 | IR:251 | ADF:124 |  | Value |  |  | Views.Details.Heating.Service | CV Operating Heating Setpoint | 1675 | 214 |  | Views.Details.Htg.Service | CVOprHtg-Sp | 1709 | 463
Prop | Templates.Heating Control | CV Operating Heating Setpoint | 1675 | 214 | 7025 | TRUE | FALSE | FALSE | 4 | Float | 100ths | 4 | deg F | 507:64 | 68 |  |  |  |  | 100ths | 0 | deg C | 507:62 | [5 empty] | Heating Setpoint |  |  |  | Attr | York RTU.Heating Control | 13 | CV Operating Heating Setpoint | UCBapp.newUCB.Operating_Heating_Setpoint | Present Value | FALSE |  |  | UCBapp.newUCB.Opr_Setpoint_Presence:Present Value = Curve 1 | AV:29730 | IR:251 | ADF:124 |  | Value |  |  | Views.Details.Heating.Proportional.Service | CV Operating Heating Setpoint | 1675 | 214 |  | Views.Details.Htg.Prop.Service | CVOprHtg-Sp | 1709 | 463
Prop | Templates.Heating Control | Main Valve No Proof Fault | 1675 | 347 | 7026 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | No | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Heating Control | 13 | Main Valve No Proof Fault | UCBapp.newUCB.Main_Valve_No_Proof_Fault | Present Value | FALSE
Prop | Templates.Heating Control | Gas Valve 2 No Proof Fault | 1675 | 348 | 7027 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | No | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Heating Control | 13 | Gas Valve 2 No Proof Fault | UCBapp.newUCB.GV_2_No_Proof_Fault | Present Value | FALSE
Prop | Templates.Heating Control | Gas Valve 3 No Proof Fault | 1675 | 349 | 7028 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | No | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Heating Control | 13 | Gas Valve 3 No Proof Fault | UCBapp.newUCB.GV_3_No_Proof_Fault | Present Value | FALSE
Prop | Templates.Heating Control | Main Valve On When Shouldn't Fault | 1675 | 350 | 7029 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | No | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Heating Control | 13 | Main Valve On When Shouldn't Fault | UCBapp.newUCB.Main_Valve_On_When_Shouldnt_F | Present Value | FALSE
Prop | Templates.Heating Control | Gas Valve 2 On When Shouldn't Fault | 1675 | 351 | 7030 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | No | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Heating Control | 13 | Gas Valve 2 On When Shouldn't Fault | UCBapp.newUCB.GV_2_On_When_Shouldnt_Fault | Present Value | FALSE
Prop | Templates.Heating Control | Gas Valve 3 On When Shouldn't Fault | 1675 | 352 | 7031 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | No | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Heating Control | 13 | Gas Valve 3 On When Shouldn't Fault | UCBapp.newUCB.GV_3 On_When_Shouldnt_Fault | Present Value | FALSE
Prop | Templates.Heating Control | Heating Lockout due to High Outdoor Air Temp | 1675 | 353 | 7032 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | FALSE | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Heating Control | 13 | Heating Lockout due to High Outdoor Air Temp | UCBapp.newUCB.Heat_Lockout_due_to_High_OAT | Present Value | FALSE
Prop | Templates.Heating Control | Excessive Supply Air Heating Fault | 1675 | 355 | 7033 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | SE RTU Excessive SAT State | 1644 | Normal | [6 empty] | SE RTU Excessive SAT State | 1644 | [6 empty] | 1644 | 0 = Normal 1 = Drop Stage 2 = Wait 3 = SAT Unreliable |  | Attr | York RTU.Heating Control | 13 | Excessive Supply Air Heating Fault | UCBapp.newUCB.Excessive_SA_Heating_Fault | Present Value | FALSE
Prop | Templates.Heating Control | Morning Cooldown Enabled | 1675 | 375 | 7034 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Disable | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Heating Control | 13 | Morning Cooldown Enabled | UCBapp.newUCB.Morning_Cooldown_Enabled | Relinquish Default | FALSE |  |  | York RTU.Thermostat Control.Thermostat Only Control Enabled:Present Value = No | MV:29891 | HR:110 | ADI:74 |  | Value |  |  | Views.Details.FanVFD.Setup | Morning Cooldown Enabled | 1675 | 375 |  | Views.Details.FanVFD.Setup | MornC-En | 1709 | 486
Prop | Templates.Heating Control | Morning Cooldown/Return Air Temp Setpoint | 1675 | 376 | 7035 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 74 | 50 | 85 |  |  | 1s | 0 | deg C | 507:62 | 10 | 30 | [7 empty] | Attr | York RTU.Heating Control | 13 | Morning Cooldown/Return Air Temp Setpoint | UCBapp.newUCB.Morning_Cool_Down_Setpoint | Relinquish Default | FALSE |  |  | York RTU.Thermostat Control.Thermostat Only Control Enabled:Present Value = No | AV:29892 | HR:44 | ADF:125 |  | Value |  |  | Views.Details.FanVFD.Setup | Morning Cooldown/Return Air Temp Setpoint | 1675 | 376 |  | Views.Details.FanVFD.Setup | MornCRAT-Sp | 1709 | 487
Prop | Templates.Heating Control | Optimal Start Enabled | 1675 | 377 | 7036 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Disable | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Heating Control | 13 | Optimal Start Enabled | UCBapp.newUCB.Optimal_Start_Enable | Relinquish Default | FALSE |  |  | York RTU.Thermostat Control.Thermostat Only Control Enabled:Present Value = No | MV:29893 | HR:111 | ADI:75 |  | Value |  |  | Views.Details.Occupancy Status | Optimal Start Enabled | 1675 | 377 |  | Views.Details.OCC | OptStrt-En | 1709 | 488
Prop | Templates.Heating Control | Optimal Start Enabled | 1675 | 377 | 7036 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Disable | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Heating Control | 13 | Optimal Start Enabled | UCBapp.newUCB.Optimal_Start_Enable | Relinquish Default | FALSE |  |  | York RTU.Thermostat Control.Thermostat Only Control Enabled:Present Value = No | MV:29893 | HR:111 | ADI:75 |  | Value |  |  | Views.Details.FanVFD.Setup | Optimal Start Enabled | 1675 | 377 |  | Views.Details.FanVFD.Setup | OptStrt-En | 1709 | 488
Prop | Templates.Heating Control | Occupancy BI Enabled | 1675 | 378 | 7037 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Enable | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Heating Control | 13 | Occupancy BI Enabled | UCBapp.newUCB.Occ_Sensor_Enable | Relinquish Default | FALSE |  |  |  | MV:29894 | HR:112 | ADI:76
Prop | Templates.Heating Control | Early Start Period | 1675 | 379 | 7038 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | minutes | 507:72 | 60 | 0 | 120 |  |  | 1s | 0 | minutes | 507:72 | 0 | 120 | [7 empty] | Attr | York RTU.Heating Control | 13 | Early Start Period | UCBapp.newUCB.Early_Start_Period | Relinquish Default | FALSE |  |  | York RTU.Thermostat Control.Thermostat Only Control Enabled:Present Value = No | AV:29895 | HR:45 | ADF:126 |  | Value |  |  | Views.Details.Occupancy Status | Early Start Period | 1675 | 379 |  | Views.Details.OCC | EarlyStrtPeriod | 1709 | 490
Prop | Templates.Heating Control | Early Start Period | 1675 | 379 | 7038 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | minutes | 507:72 | 60 | 0 | 120 |  |  | 1s | 0 | minutes | 507:72 | 0 | 120 | [7 empty] | Attr | York RTU.Heating Control | 13 | Early Start Period | UCBapp.newUCB.Early_Start_Period | Relinquish Default | FALSE |  |  | York RTU.Thermostat Control.Thermostat Only Control Enabled:Present Value = No | AV:29895 | HR:45 | ADF:126 |  | Value |  |  | Views.Details.FanVFD.Setup | Early Start Period | 1675 | 379 |  | Views.Details.FanVFD.Setup | EarlyStrtPeriod | 1709 | 490
Prop | Templates.Heating Control | Number of Gas Valves Installed | 1675 | 439 | 7039 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 |  | 507:95 | 0 | 0 | 3 |  |  | 1s | 0 |  | 507:95 | 0 | 3 | [7 empty] | Attr | York RTU.Heating Control | 13 | Number of Gas Valves Installed | UCBapp.newUCB.Number_of_Gas_Valves | Relinquish Default | TRUE | [7 empty] | Value |  |  | Views.Details.Heating.Setup | Number of Gas Valves Installed | 1675 | 439 |  | Views.Details.Htg.Setup | #GasVlvs | 1709 | 550
Prop | Templates.Heating Control | Heating Adaptive Tuning Enable | 1675 | 485 | 7041 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Disable | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Heating Control | 13 | Heating Adaptive Tuning Enable | UCBapp.newUCB.Heating_Adaptive_Tuning_Enable | Relinquish Default | FALSE |  |  |  | MV:29881 | HR:114 | ADI:78 |  | Value |  |  | Views.Details.Heating.Setup | Heating Adaptive Tuning Enable | 1675 | 485 |  | Views.Details.Htg.Setup | HtgAdapTunEn | 1709 | 616
Prop | Templates.Heating Control | Number of Limit Switches | 1675 | 490 | 7042 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 |  | 507:95 | 0 |  |  |  |  | 1s | 0 |  | 507:95 | [9 empty] | Attr | York RTU.Heating Control | 13 | Number of Limit Switches | UCBapp.newUCB.Number_of_Limit_Switches | Present Value | TRUE | [5 empty] | ADF:128 |  | Value |  |  | Views.Details.Heating.Setup | Number of Limit Switches | 1675 | 490 |  | Views.Details.Htg.Setup | #LimSwtchs | 1709 | 622
Prop | Templates.Heating Control | DAT Max Heating SP | 1675 | 492 | 7043 | TRUE | TRUE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | 105 | 80 | 110 |  |  | 10ths | 0 | deg C | 507:62 | 26.6 | 43.4 | [7 empty] | Attr | York RTU.Heating Control | 13 | DAT Max Heating SP | UCBapp.newUCB.DAT_Max_Heating_SP | Relinquish Default | FALSE |  |  | York RTU.SZ VAV Enabled:Present Value = On | AV:29905 | IR:75 | ADF:161 |  | Value |  |  | Views.Details.Single Zone VAV.Setup | DAT Max Heating SP | 1675 | 492 |  | Views.Details.SZ VAV.Setup | DATMaxHtgSP | 1709 | 624
Prop | Templates.Heating Control | DAT Satisfied SP | 1675 | 493 | 7044 | TRUE | TRUE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | 70 | 65 | 75 |  |  | 10ths | 0 | deg C | 507:62 | 18.3 | 23.9 | [7 empty] | Attr | York RTU.Heating Control | 13 | DAT Satisfied SP | UCBapp.newUCB.DAT_Satisfied_SP | Relinquish Default | FALSE |  |  | York RTU.SZ VAV Enabled:Present Value = On | AV:29906 | IR:76 | ADF:162 |  | Value |  |  | Views.Details.Single Zone VAV.Setup | DAT Satisfied SP | 1675 | 493 |  | Views.Details.SZ VAV.Setup | DATSatSP | 1709 | 625
Prop | Templates.Heating Control | Staged Heating Command | 1675 | 629 | 7045 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 0 |  |  |  |  | 1s | 0 | % | 507:98 | [9 empty] | Attr | York RTU.Heating Control | 13 | Staged Heating Command | UCBapp.newUCB.Staged_Heating_Command | Present Value | FALSE |  |  | York RTU.Heating Control Type:Present Value = Staged | AV:29923 | IR:264 | ADF:166 |  | Value |  |  | Views.Details.Heating.Service | Staged Heating Command | 1675 | 629 |  | Views.Details.Htg.Service | StgHtgCmd | 1709 | 649
Prop | Templates.Heating Control | Staged Heating Command | 1675 | 629 | 7045 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 0 |  |  |  |  | 1s | 0 | % | 507:98 | [9 empty] | Attr | York RTU.Heating Control | 13 | Staged Heating Command | UCBapp.newUCB.Staged_Heating_Command | Present Value | FALSE |  |  | York RTU.Heating Control Type:Present Value = Staged | AV:29923 | IR:264 | ADF:166 |  | Value |  |  | Views.Details.FanVFD.Service | Staged Heating Command | 1675 | 629 |  | Views.Details.FanVFD.Service | StgHtgCmd | 1709 | 649
Prop | Templates.Heating Control | Proportional Heating Command | 1675 | 630 | 7046 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 0 |  |  |  |  | 1s | 0 | % | 507:98 | [9 empty] | Attr | York RTU.Heating Control | 13 | Proportional Heating Command | UCBapp.newUCB.Proportional_Heating_Command | Present Value | FALSE |  |  |  | AV:29924
Prop | Templates.Heating Control | SZ VAV Occupied Heating Setpoint | 1675 | 643 | 7047 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 68 | 46 | 99 |  |  | 1s | 0 | deg C | 507:62 | 8 | 37 | [7 empty] | Attr | York RTU.Heating Control | 13 | SZ VAV Occupied Heating Setpoint | UCBapp.newUCB.Occ_Htg_Setpoint | Relinquish Default | FALSE |  |  | UCBapp.newUCB.Setpoint_Input_Presence:Present Value = Curve 3 | AV:29929 | HR:272 | ADF:172 |  | Value |  |  | Views.Details.Heating.Setup | SZ VAV Occupied Heating Setpoint | 1675 | 643 |  | Views.Details.Htg.Setup | SZVAVHtgOcc-Sp | 1709 | 658
Prop | Templates.Heating Control | SZ VAV Occupied Heating Setpoint | 1675 | 643 | 7047 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 68 | 46 | 99 |  |  | 1s | 0 | deg C | 507:62 | 8 | 37 | [7 empty] | Attr | York RTU.Heating Control | 13 | SZ VAV Occupied Heating Setpoint | UCBapp.newUCB.Occ_Htg_Setpoint | Relinquish Default | FALSE |  |  | UCBapp.newUCB.Setpoint_Input_Presence:Present Value = Curve 3 | AV:29929 | HR:272 | ADF:172 |  | Value |  |  | Views.Details.Single Zone VAV.Setup | SZ VAV Occupied Heating Setpoint | 1675 | 643 |  | Views.Details.SZ VAV.Setup | SZVAVHtgOcc-Sp | 1709 | 658
Prop | Templates.Heating Control | SZ VAV Unoccupied Heating Setpoint | 1675 | 645 | 7048 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 60 | 45 | 98 |  |  | 1s | 0 | deg C | 507:62 | 7 | 36 | [7 empty] | Attr | York RTU.Heating Control | 13 | SZ VAV Unoccupied Heating Setpoint | UCBapp.newUCB.Unocc_Htg_Setpoint | Relinquish Default | FALSE |  |  | UCBapp.newUCB.Setpoint_Input_Presence:Present Value = Curve 3 | AV:29930 | HR:273 | ADF:173 |  | Value |  |  | Views.Details.Heating.Setup | SZ VAV Unoccupied Heating Setpoint | 1675 | 645 |  | Views.Details.Htg.Setup | SZVAVHtgUnocc-Sp | 1709 | 659
Prop | Templates.Heating Control | SZ VAV Unoccupied Heating Setpoint | 1675 | 645 | 7048 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 60 | 45 | 98 |  |  | 1s | 0 | deg C | 507:62 | 7 | 36 | [7 empty] | Attr | York RTU.Heating Control | 13 | SZ VAV Unoccupied Heating Setpoint | UCBapp.newUCB.Unocc_Htg_Setpoint | Relinquish Default | FALSE |  |  | UCBapp.newUCB.Setpoint_Input_Presence:Present Value = Curve 3 | AV:29930 | HR:273 | ADF:173 |  | Value |  |  | Views.Details.Single Zone VAV.Setup | SZ VAV Unoccupied Heating Setpoint | 1675 | 645 |  | Views.Details.SZ VAV.Setup | SZVAVHtgUnocc-Sp | 1709 | 659
Prop | Templates.Heating Control | SZ VAV Operating Heating Setpoint | 1675 | 647 | 7049 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 100 |  |  |  |  | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Heating Control | 13 | SZ VAV Operating Heating Setpoint | UCBapp.newUCB.SZVAV_Cascaded_DAT_Sp_Htg | Present Value | FALSE |  |  | UCBapp.newUCB.Opr_Setpoint_Presence:Present Value = Curve 3 | AV:30108 | IR:880 | ADF:214 |  | Value |  |  | Views.Details.Single Zone VAV.Service | Operating Heating Discharge Air Temp Setpoint | 2644 | 40 |  | Views.Details.SZ VAV.Service | OprHtgDAT-SP | 2645 | 359
Prop | Templates.Heating Control | SZ VAV Operating Heating Setpoint | 1675 | 647 | 7049 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 100 |  |  |  |  | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Heating Control | 13 | SZ VAV Operating Heating Setpoint | UCBapp.newUCB.SZVAV_Cascaded_DAT_Sp_Htg | Present Value | FALSE |  |  | UCBapp.newUCB.Opr_Setpoint_Presence:Present Value = Curve 3 | AV:30108 | IR:880 | ADF:214 |  | Value |  |  | Views.Details.Heating.Service | Operating Heating Discharge Air Temp Setpoint | 2644 | 40 |  | Views.Details.Htg.Service | OprHtgDAT-SP | 2645 | 359
Prop | Templates.Heating Control | SZ VAV Heating Load | 1675 | 745 | 7050 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | % | 507:98 | 0 |  |  |  |  | 10ths | 0 | % | 507:98 | [9 empty] | Attr | York RTU.Heating Control | 13 | SZ VAV Heating Load | UCBapp.newUCB.SZ_VAV_Heating_Load | Present Value | FALSE |  |  | York RTU.SZ VAV Enabled:Present Value = On | AV:29936 | IR:439 | ADF:187 |  | Value |  |  | Views.Details.Single Zone VAV.Service | SZ VAV Heating Load | 1675 | 745 |  | Views.Details.SZ VAV.Service | SZVAVHtgLd | 1709 | 666
Prop | Templates.Heating Control | Operational Error Sigma | 1675 | 1076 | 7051 | TRUE | TRUE | FALSE | 4 | Float | 10ths | 5 | delta deg F | 507:120 | 1.4 | 1 | 2.5 |  |  | 10ths | 0 | delta deg C | 507:359 | 0.6 | 1.5 | [7 empty] | Attr | York RTU.Heating Control | 13 | Operational Error Sigma | UCBapp.newUCB.Htg_Min_Tune_Band | Relinquish Default | FALSE | [7 empty] | Value |  |  | Views.Details.Heating.Setup | Heating Manual Tuning | 1675 | 479 |  | Views.Details.Htg.Setup | HtgManualTune | 1709 | 691
Prop | Templates.Heating Control | Low Limit Enable | 1675 | 1405 | 7052 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Disable/Enable | 658 | Disable | [6 empty] | Disable/Enable | 658 | [6 empty] | 658 | 0 = Disable 1 = Enable |  | Attr | York RTU.Heating Control | 13 | Low Limit Enable | UCBapp.newUCB.Low_Limit_Enable | Relinquish Default | FALSE | [7 empty] | Value |  |  | Views.Details.Heating.Setup | Low Limit Enable | 1675 | 1405 |  | Views.Details.Htg.Setup | LL_Enable | 1709 | 692
Prop | Templates.Heating Control | Low Limit Upper SAT Setpoint | 1675 | 1406 | 7053 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 80 | 65 | 85 |  |  | 1s | 0 | deg C | 507:62 | 18 | 30 | [7 empty] | Attr | York RTU.Heating Control | 13 | Low Limit Upper SAT Setpoint | UCBapp.newUCB.Low_Limit_Upper_SAT_Setpoint | Relinquish Default | FALSE | [7 empty] | Value |  |  | Views.Details.Heating.Setup | Low Limit Upper SAT Setpoint | 1675 | 1406 |  | Views.Details.Htg.Setup | LL_UpSAT_SP | 1709 | 693
Prop | Templates.Heating Control | Low Limit Lower SAT Setpoint | 1675 | 1407 | 7054 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 65 | 60 | 80 |  |  | 1s | 0 | deg C | 507:62 | 15 | 27 | [7 empty] | Attr | York RTU.Heating Control | 13 | Low Limit Lower SAT Setpoint | UCBapp.newUCB.Low_Limit_Lower_SAT_Setpoint | Relinquish Default | FALSE | [7 empty] | Value |  |  | Views.Details.Heating.Setup | Low Limit Lower SAT Setpoint | 1675 | 1407 |  | Views.Details.Htg.Setup | LL_LowSAT_SP | 1709 | 694
Prop | Templates.Heating Control | COBP Occupied Heating Enabled | 1675 | 1456 | 7055 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Available | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Heating Control | 13 | COBP Occupied Heating Enabled | UCBapp.newUCB.VAV_Occ_Heating_Enabled | Relinquish Default | FALSE | [7 empty] | Value |  |  | Views.Details.FanVFD.Setup | COBP Occupied Heating Enabled | 1675 | 1456 |  | Views.Details.FanVFD.Setup | HtgOcc-En | 1709 | 239
Prop | Templates.Heating Control | Heating Rapid Start Enable | 1714 | 268 | 7056 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Disable/Enable | 658 | Disable | [6 empty] | Disable/Enable | 658 | [6 empty] | 658 | 0 = Disable 1 = Enable |  | Attr | York RTU.Heating Control | 13 | Heating Rapid Start Enable | UCBapp.newUCB.Heating_Rapid_Start_Enable | Relinquish Default | TRUE |  |  | York RTU.Thermostat Control.Thermostat Only Control Enabled:Present Value = No | MV:30107 | HR:879 | ADI:213 |  | Value |  |  | Views.Details.Heating.Setup | Heating Rapid Start Enable | 1714 | 268 |  | Views.Details.Htg.Setup | HtgRapidStartEn | 1709 | 768
Prop | Templates.Heating Control | Heating Rapid Start Time | 1714 | 270 | 7057 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | minutes | 507:72 | 300 | 2 | 30 |  |  | 1s | 0 | minutes | 507:72 | 2 | 30 | [7 empty] | Attr | York RTU.Heating Control | 13 | Heating Rapid Start Time | UCBapp.newUCB.Heating_Rapid_Start_Time | Relinquish Default | FALSE |  |  | York RTU.Heating Control.Heating Rapid Start Enable:Present Value = Enable | AV:30141 | HR:890 | ADF:224 |  | Value |  |  | Views.Details.Heating.Setup | Heating Rapid Start Time | 1714 | 270 |  | Views.Details.Htg.Setup | HtgRapidStartTime | 1709 | 770
Tmpl | Templates.Staged Heat Control | [31 empty] | Model | York RTU.Heating Control.Staged Heat Control | 14
Prop | Templates.Staged Heat Control | Number of Heating Stages Installed | 1675 | 215 | 7000 | TRUE | TRUE | FALSE | 16 | Byte | 1s | 6 |  | 507:95 | 0 | 0 | 3 |  |  | 1s | 0 |  | 507:95 | 0 | 3 |  |  |  | Number of Heating Stages |  |  |  | Attr | York RTU.Heating Control.Staged Heat Control | 14 | Number of Heating Stages Installed | UCBapp.newUCB.Max_Heating_Stages | Relinquish Default | TRUE |  |  |  | AV:29731 | HR:430 | ADI:141 |  | Value |  |  | Views.Commissioning.Standard | Number of Heating Stages Installed | 1675 | 215 |  | Views.Commission.Standard | #HtgStgs | 1709 | 250
Prop | Templates.Staged Heat Control | Number of Heating Stages Installed | 1675 | 215 | 7000 | TRUE | TRUE | FALSE | 16 | Byte | 1s | 6 |  | 507:95 | 0 | 0 | 3 |  |  | 1s | 0 |  | 507:95 | 0 | 3 |  |  |  | Number of Heating Stages |  |  |  | Attr | York RTU.Heating Control.Staged Heat Control | 14 | Number of Heating Stages Installed | UCBapp.newUCB.Max_Heating_Stages | Relinquish Default | TRUE |  |  |  | AV:29731 | HR:430 | ADI:141 |  | Value |  |  | Views.Commissioning.Quick Start | Number of Heating Stages Installed | 1675 | 215 |  | Views.Commission.Quick Start | #HtgStgs | 1709 | 250
Tmpl | Templates.Heating Stage | [31 empty] | Model | York RTU.Heating Control.Staged Heat Control.Heating Stage 1 | 15 | [6 empty] | York RTU.Heating Control.Staged Heat Control.Number of Heating Stages Installed:Present Value > 0
Prop | Templates.Heating Stage | Heat Stage Command | 1675 | 111 | 7000 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [5 empty] | Heating Stage 1 | 647 | 0 = Off 1 = On |  | Attr | York RTU.Heating Control.Staged Heat Control.Heating Stage 1 | 15 | Heat Stage Command | UCBapp.newUCB.HTG1ORRVLV_C | Present Value | FALSE |  |  |  | MV:29732 | IR:359 | BO:10 |  | Value |  |  | Views.Details.Heating.Service | Heating Stage Command 1 | 1714 | 149 |  | Views.Details.Htg.Service | H1 | 1709 | 251
Prop | Templates.Heating Stage | Heat Stage Command | 1675 | 111 | 7000 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [5 empty] | Heating Stage 1 | 647 | 0 = Off 1 = On |  | Attr | York RTU.Heating Control.Staged Heat Control.Heating Stage 1 | 15 | Heat Stage Command | UCBapp.newUCB.HTG1ORRVLV_C | Present Value | FALSE |  |  |  | MV:29732 | IR:359 | BO:10 |  | Value |  |  | Views.Details.FanVFD.Service | Heating Stage Command 1 | 1714 | 149 |  | Views.Details.FanVFD.Service | H1 | 1709 | 251
Prop | Templates.Heating Stage | Heat Stage Status | 1675 | 112 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | SE RTU Heating Stage 1 Status | 1743 | Off_Idle | [6 empty] | SE RTU Heating Stage 1 Status | 1743 | [6 empty] | 1743 | 0 = Off-Idle 1 = On-Minimum Runtime Timer 2 = On-Normal Command 3 = Off-Heating Is Disabled ... |  | Attr | York RTU.Heating Control.Staged Heat Control.Heating Stage 1 | 15 | Heat Stage Status | UCBapp.newUCB.Heat_Stage_1_Status | Present Value | FALSE |  |  |  | MV:29735 | IR:360 | BI:36 |  | Value |  |  | Views.Details.Heating.Service | Heating Stage 1 Status | 1714 | 103 |  | Views.Details.Htg.Service | H1-S | 1709 | 254
Prop | Templates.Heating Stage | Heating Stage Min On Time Remaining | 1675 | 216 | 7003 | TRUE | FALSE | FALSE | 17 | SignedInteger | 1s | 6 | seconds | 507:73 | 0 |  |  |  |  | 1s | 0 | seconds | 507:73 | [9 empty] | Attr | York RTU.Heating Control.Staged Heat Control.Heating Stage 1 | 15 | Heating Stage Min On Time Remaining | UCBapp.newUCB.Heat_Min_On_Time_Remaining_1 | Present Value | FALSE | [7 empty] | Value |  |  | Views.Details.Heating.Service | Heating Stage 1 Min On Time Remaining | 1714 | 105 |  | Views.Details.Htg.Service | H1OnTmr | 1709 | 260
Prop | Templates.Heating Stage | Heating Stage Anti-Short Cycle Delay Time Remaining | 1675 | 217 | 7004 | TRUE | FALSE | FALSE | 17 | SignedInteger | 1s | 6 | seconds | 507:73 | 0 |  |  |  |  | 1s | 0 | seconds | 507:73 | [9 empty] | Attr | York RTU.Heating Control.Staged Heat Control.Heating Stage 1 | 15 | Heating Stage Anti-Short Cycle Delay Time Remaining | UCBapp.newUCB.Heat_Min_Off_Time_Remaining_1 | Present Value | FALSE | [7 empty] | Value |  |  | Views.Details.Heating.Service | Heating Stage 1 Anti-Short Cycle Delay Time Remaining | 1714 | 106 |  | Views.Details.Htg.Service | H1ASCDTmr | 1709 | 263
Prop | Templates.Heating Stage | Heat Stage Accumulated Runtime | 1675 | 116 | 7006 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | hours | 507:71 |  | 0 | 10000 |  |  | 1s | 0 | hours | 507:71 | 0 | 10000 | [7 empty] | Attr | York RTU.Heating Control.Staged Heat Control.Heating Stage 1 | 15 | Heat Stage Accumulated Runtime | 8-1/UCBApp.Htg_Runtime_1 | Present Value | FALSE |  |  |  | AV:29738 | IR:48 | ADF:129 |  | Value |  |  | Views.Details.Heating.Service | Heating Stage 1 Accumulated Runtime | 1714 | 108 |  | Views.Details.Htg.Service | H1RunTim | 1709 | 269
Prop | Templates.Heating Stage | Heat Stage Accumulated Runtime | 1675 | 116 | 7006 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | hours | 507:71 |  | 0 | 10000 |  |  | 1s | 0 | hours | 507:71 | 0 | 10000 | [7 empty] | Attr | York RTU.Heating Control.Staged Heat Control.Heating Stage 1 | 15 | Heat Stage Accumulated Runtime | 8-1/UCBApp.Htg_Runtime_1 | Present Value | FALSE |  |  |  | AV:29738 | IR:48 | ADF:129 |  | Value |  |  | Views.Clone.Full Clone | Heating Stage 1 Accumulated Runtime | 1714 | 108 |  |  | H1RunTim | 1709 | 269
Prop | Templates.Heating Stage | Heat Stage Number of Times On | 1675 | 117 | 7007 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 |  | 507:95 |  | 0 | 2000000 |  |  | 1s | 0 |  | 507:95 | 0 | 2000000 | [7 empty] | Attr | York RTU.Heating Control.Staged Heat Control.Heating Stage 1 | 15 | Heat Stage Number of Times On | 8-1/UCBApp.Htg_Starts_1 | Relinquish Default | FALSE
Tmpl | Templates.Heating Stage | [31 empty] | Model | York RTU.Heating Control.Staged Heat Control.Heating Stage 2 | 16 | [6 empty] | York RTU.Heating Control.Staged Heat Control.Number of Heating Stages Installed:Present Value > 1
Prop | Templates.Heating Stage | Heat Stage Command | 1675 | 111 | 7000 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [5 empty] | Heating Stage 1 | 647 | 0 = Off 1 = On |  | Attr | York RTU.Heating Control.Staged Heat Control.Heating Stage 2 | 16 | Heat Stage Command | UCBapp.newUCB.HTG2ORAUX_C | Present Value | FALSE |  |  |  | MV:29733 | IR:361 | BO:11 |  | Value |  |  | Views.Details.Heating.Service | Heating Stage Command 2 | 1714 | 150 |  | Views.Details.Htg.Service | H2 | 1709 | 252
Prop | Templates.Heating Stage | Heat Stage Command | 1675 | 111 | 7000 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [5 empty] | Heating Stage 1 | 647 | 0 = Off 1 = On |  | Attr | York RTU.Heating Control.Staged Heat Control.Heating Stage 2 | 16 | Heat Stage Command | UCBapp.newUCB.HTG2ORAUX_C | Present Value | FALSE |  |  |  | MV:29733 | IR:361 | BO:11 |  | Value |  |  | Views.Details.FanVFD.Service | Heating Stage Command 2 | 1714 | 150 |  | Views.Details.FanVFD.Service | H2 | 1709 | 252
Prop | Templates.Heating Stage | Heat Stage Status | 1675 | 112 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | SE RTU Heating Stage 1 Status | 1743 | Off_Idle | [6 empty] | SE RTU Heating Stage 1 Status | 1743 | [6 empty] | 1743 | 0 = Off-Idle 1 = On-Minimum Runtime Timer 2 = On-Normal Command 3 = Off-Heating Is Disabled ... |  | Attr | York RTU.Heating Control.Staged Heat Control.Heating Stage 2 | 16 | Heat Stage Status | UCBapp.newUCB.Heat_Stage_2_Status | Present Value | FALSE |  |  |  | MV:29736 | IR:362 | BI:37 |  | Value |  |  | Views.Details.Heating.Service | Heating Stage 2 Status | 1714 | 109 |  | Views.Details.Htg.Service | H2-S | 1709 | 255
Prop | Templates.Heating Stage | Heating Stage Min On Time Remaining | 1675 | 216 | 7003 | TRUE | FALSE | FALSE | 17 | SignedInteger | 1s | 6 | seconds | 507:73 | 0 |  |  |  |  | 1s | 0 | seconds | 507:73 | [9 empty] | Attr | York RTU.Heating Control.Staged Heat Control.Heating Stage 2 | 16 | Heating Stage Min On Time Remaining | UCBapp.newUCB.Heat_Min_On_Time_Remaining_2 | Present Value | FALSE | [7 empty] | Value |  |  | Views.Details.Heating.Service | Heating Stage 2 Min On Time Remaining | 1714 | 111 |  | Views.Details.Htg.Service | H2OnTmr | 1709 | 261
Prop | Templates.Heating Stage | Heating Stage Anti-Short Cycle Delay Time Remaining | 1675 | 217 | 7004 | TRUE | FALSE | FALSE | 17 | SignedInteger | 1s | 6 | seconds | 507:73 | 0 |  |  |  |  | 1s | 0 | seconds | 507:73 | [9 empty] | Attr | York RTU.Heating Control.Staged Heat Control.Heating Stage 2 | 16 | Heating Stage Anti-Short Cycle Delay Time Remaining | UCBapp.newUCB.Heat_Min_Off_Time_Remaining_2 | Present Value | FALSE | [7 empty] | Value |  |  | Views.Details.Heating.Service | Heating Stage 2 Anti-Short Cycle Delay Time Remaining | 1714 | 112 |  | Views.Details.Htg.Service | H2ASCDTmr | 1709 | 264
Prop | Templates.Heating Stage | Heat Stage Accumulated Runtime | 1675 | 116 | 7006 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | hours | 507:71 |  | 0 | 10000 |  |  | 1s | 0 | hours | 507:71 | 0 | 10000 | [7 empty] | Attr | York RTU.Heating Control.Staged Heat Control.Heating Stage 2 | 16 | Heat Stage Accumulated Runtime | 8-1/UCBApp.Htg_Runtime_2 | Present Value | FALSE |  |  |  | AV:29739 | IR:49 | ADF:130 |  | Value |  |  | Views.Details.Heating.Service | Heating Stage 2 Accumulated Runtime | 1714 | 114 |  | Views.Details.Htg.Service | H2RunTim | 1709 | 270
Prop | Templates.Heating Stage | Heat Stage Accumulated Runtime | 1675 | 116 | 7006 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | hours | 507:71 |  | 0 | 10000 |  |  | 1s | 0 | hours | 507:71 | 0 | 10000 | [7 empty] | Attr | York RTU.Heating Control.Staged Heat Control.Heating Stage 2 | 16 | Heat Stage Accumulated Runtime | 8-1/UCBApp.Htg_Runtime_2 | Present Value | FALSE |  |  |  | AV:29739 | IR:49 | ADF:130 |  | Value |  |  | Views.Clone.Full Clone | Heating Stage 2 Accumulated Runtime | 1714 | 114 |  |  | H2RunTim | 1709 | 270
Prop | Templates.Heating Stage | Heat Stage Number of Times On | 1675 | 117 | 7007 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 |  | 507:95 |  | 0 | 2000000 |  |  | 1s | 0 |  | 507:95 | 0 | 2000000 | [7 empty] | Attr | York RTU.Heating Control.Staged Heat Control.Heating Stage 2 | 16 | Heat Stage Number of Times On | 8-1/UCBApp.Htg_Starts_2 | Relinquish Default | FALSE
Tmpl | Templates.Heating Stage | [31 empty] | Model | York RTU.Heating Control.Staged Heat Control.Heating Stage 3 | 17 | [6 empty] | York RTU.Heating Control.Staged Heat Control.Number of Heating Stages Installed:Present Value > 2
Prop | Templates.Heating Stage | Heat Stage Command | 1675 | 111 | 7000 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [5 empty] | Heating Stage 1 | 647 | 0 = Off 1 = On |  | Attr | York RTU.Heating Control.Staged Heat Control.Heating Stage 3 | 17 | Heat Stage Command | FourStageApp.FourStage.HTG3_C | Present Value | FALSE |  |  |  | MV:29734 | IR:363 | BO:12 |  | Value |  |  | Views.Details.Heating.Service | Heating Stage Command 3 | 1714 | 151 |  | Views.Details.Htg.Service | H3 | 1709 | 253
Prop | Templates.Heating Stage | Heat Stage Command | 1675 | 111 | 7000 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [5 empty] | Heating Stage 1 | 647 | 0 = Off 1 = On |  | Attr | York RTU.Heating Control.Staged Heat Control.Heating Stage 3 | 17 | Heat Stage Command | FourStageApp.FourStage.HTG3_C | Present Value | FALSE |  |  |  | MV:29734 | IR:363 | BO:12 |  | Value |  |  | Views.Details.FanVFD.Service | Heating Stage Command 3 | 1714 | 151 |  | Views.Details.FanVFD.Service | H3 | 1709 | 253
Prop | Templates.Heating Stage | Heat Stage Status | 1675 | 112 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | SE RTU Heating Stage 1 Status | 1743 | Off_Idle | [6 empty] | SE RTU Heating Stage 1 Status | 1743 | [6 empty] | 1743 | 0 = Off-Idle 1 = On-Minimum Runtime Timer 2 = On-Normal Command 3 = Off-Heating Is Disabled ... |  | Attr | York RTU.Heating Control.Staged Heat Control.Heating Stage 3 | 17 | Heat Stage Status | UCBapp.newUCB.Heat_Stage_3_Status | Present Value | FALSE |  |  |  | MV:29737 | IR:364 | BI:38 |  | Value |  |  | Views.Details.Heating.Service | Heating Stage 3 Status | 1714 | 115 |  | Views.Details.Htg.Service | H3-S | 1709 | 256
Prop | Templates.Heating Stage | Heating Stage Min On Time Remaining | 1675 | 216 | 7003 | TRUE | FALSE | FALSE | 17 | SignedInteger | 1s | 6 | seconds | 507:73 | 0 |  |  |  |  | 1s | 0 | seconds | 507:73 | [9 empty] | Attr | York RTU.Heating Control.Staged Heat Control.Heating Stage 3 | 17 | Heating Stage Min On Time Remaining | UCBapp.newUCB.Heat_Min_On_Time_Remaining_3 | Present Value | FALSE | [7 empty] | Value |  |  | Views.Details.Heating.Service | Heating Stage 3 Min On Time Remaining | 1714 | 117 |  | Views.Details.Htg.Service | H3OnTmr | 1709 | 262
Prop | Templates.Heating Stage | Heating Stage Anti-Short Cycle Delay Time Remaining | 1675 | 217 | 7004 | TRUE | FALSE | FALSE | 17 | SignedInteger | 1s | 6 | seconds | 507:73 | 0 |  |  |  |  | 1s | 0 | seconds | 507:73 | [9 empty] | Attr | York RTU.Heating Control.Staged Heat Control.Heating Stage 3 | 17 | Heating Stage Anti-Short Cycle Delay Time Remaining | UCBapp.newUCB.Heat_Min_Off_Time_Remaining_3 | Present Value | FALSE | [7 empty] | Value |  |  | Views.Details.Heating.Service | Heating Stage 3 Anti-Short Cycle Delay Time Remaining | 1714 | 118 |  | Views.Details.Htg.Service | H3ASCDTmr | 1709 | 265
Prop | Templates.Heating Stage | Heat Stage Accumulated Runtime | 1675 | 116 | 7006 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | hours | 507:71 |  | 0 | 10000 |  |  | 1s | 0 | hours | 507:71 | 0 | 10000 | [7 empty] | Attr | York RTU.Heating Control.Staged Heat Control.Heating Stage 3 | 17 | Heat Stage Accumulated Runtime | 8-1/UCBApp.Htg_Runtime_3 | Present Value | FALSE |  |  |  | AV:29740 | IR:50 | ADF:131 |  | Value |  |  | Views.Details.Heating.Service | Heating Stage 3 Accumulated Runtime | 1714 | 120 |  | Views.Details.Htg.Service | H3RunTim | 1709 | 271
Prop | Templates.Heating Stage | Heat Stage Accumulated Runtime | 1675 | 116 | 7006 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | hours | 507:71 |  | 0 | 10000 |  |  | 1s | 0 | hours | 507:71 | 0 | 10000 | [7 empty] | Attr | York RTU.Heating Control.Staged Heat Control.Heating Stage 3 | 17 | Heat Stage Accumulated Runtime | 8-1/UCBApp.Htg_Runtime_3 | Present Value | FALSE |  |  |  | AV:29740 | IR:50 | ADF:131 |  | Value |  |  | Views.Clone.Full Clone | Heating Stage 3 Accumulated Runtime | 1714 | 120 |  |  | H3RunTim | 1709 | 271
Prop | Templates.Heating Stage | Heat Stage Number of Times On | 1675 | 117 | 7007 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 |  | 507:95 |  | 0 | 2000000 |  |  | 1s | 0 |  | 507:95 | 0 | 2000000 | [7 empty] | Attr | York RTU.Heating Control.Staged Heat Control.Heating Stage 3 | 17 | Heat Stage Number of Times On | 8-1/UCBApp.Htg_Starts_3 | Relinquish Default | FALSE
Tmpl | Templates.Hydronic Heat Control | [31 empty] | Model | York RTU.Heating Control.Hydronic Heat Control | 18 | [6 empty] | York RTU.Heating Control Type:Present Value = Proportional
Prop | Templates.Hydronic Heat Control | Hydronic Heat Valve % Command | 1675 | 218 | 7000 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | N/A |  |  |  |  | 1s | 0 | % | 507:98 | [5 empty] | Heating Command |  |  |  | Attr | York RTU.Heating Control.Hydronic Heat Control | 18 | Hydronic Heat Valve % Command | FourStageApp.FourStage.HWVLV_O | Present Value | FALSE |  |  |  | AV:29741 | IR:252 | AO:2 |  | Value |  |  | Views.Details.Heating.Proportional.Service | Hydronic Heat Valve % Command | 1675 | 218 |  | Views.Details.Htg.Prop.Service | HWV | 1709 | 275
Prop | Templates.Hydronic Heat Control | Hydronic Heat Valve Reverse Acting | 1675 | 219 | 7001 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Normal | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Heating Control.Hydronic Heat Control | 18 | Hydronic Heat Valve Reverse Acting | UCBapp.newUCB.Hydronic_Heat_Valve_Rev_Acting | Relinquish Default | FALSE |  |  |  | MV:29742 | HR:115 | ADI:79 |  | Value |  |  | Views.Details.Heating.Proportional.Setup | Hydronic Heat Valve Reverse Acting | 1675 | 219 |  | Views.Details.Htg.Prop.Setup | HydReverse | 1709 | 276
Prop | Templates.Hydronic Heat Control | Hydronic Heat Valve Reverse Acting | 1675 | 219 | 7001 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Normal | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Heating Control.Hydronic Heat Control | 18 | Hydronic Heat Valve Reverse Acting | UCBapp.newUCB.Hydronic_Heat_Valve_Rev_Acting | Relinquish Default | FALSE |  |  |  | MV:29742 | HR:115 | ADI:79 |  | Value |  |  | Views.Details.Heating.Proportional.Service | Hydronic Heat Valve Reverse Acting | 1675 | 219 |  | Views.Details.Htg.Prop.Service | HydReverse | 1709 | 276
Prop | Templates.Hydronic Heat Control | Hydronic Heating Stage #1 Supply Air Setpoint | 1675 | 220 | 7002 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 120 | 80 | 180 |  |  | 1s | 0 | deg C | 507:62 | 27 | 82 | [7 empty] | Attr | York RTU.Heating Control.Hydronic Heat Control | 18 | Hydronic Heating Stage #1 Supply Air Setpoint | UCBapp.newUCB.Hydronic_Heating_Stg_1_SA_SP | Relinquish Default | FALSE |  |  |  | AV:29743 | HR:51 | ADF:132 |  | Value |  |  | Views.Details.Heating.Proportional.Setup | Hydronic Heating Stage #1 Supply Air Setpoint | 1675 | 220 |  | Views.Details.Htg.Prop.Setup | HydH1SA-Sp | 1709 | 277
Prop | Templates.Hydronic Heat Control | Hydronic Heating Stage #1 Supply Air Setpoint | 1675 | 220 | 7002 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 120 | 80 | 180 |  |  | 1s | 0 | deg C | 507:62 | 27 | 82 | [7 empty] | Attr | York RTU.Heating Control.Hydronic Heat Control | 18 | Hydronic Heating Stage #1 Supply Air Setpoint | UCBapp.newUCB.Hydronic_Heating_Stg_1_SA_SP | Relinquish Default | FALSE |  |  |  | AV:29743 | HR:51 | ADF:132 |  | Value |  |  | Views.Clone.Partial Clone 1 | Hydronic Heating Stage #1 Supply Air Setpoint | 1675 | 220 |  |  | HydH1SA-Sp | 1709 | 277
Prop | Templates.Hydronic Heat Control | Hydronic Heating Stage #2 Supply Air Setpoint | 1675 | 221 | 7003 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 150 | 80 | 180 |  |  | 1s | 0 | deg C | 507:62 | 27 | 82 | [7 empty] | Attr | York RTU.Heating Control.Hydronic Heat Control | 18 | Hydronic Heating Stage #2 Supply Air Setpoint | UCBapp.newUCB.Hydronic_Heating_Stg_2_SA_SP | Relinquish Default | FALSE |  |  |  | AV:29744 | HR:52 | ADF:133 |  | Value |  |  | Views.Details.Heating.Proportional.Setup | Hydronic Heating Stage #2 Supply Air Setpoint | 1675 | 221 |  | Views.Details.Htg.Prop.Setup | HydH2SA-Sp | 1709 | 278
Prop | Templates.Hydronic Heat Control | Hydronic Heating Stage #2 Supply Air Setpoint | 1675 | 221 | 7003 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 150 | 80 | 180 |  |  | 1s | 0 | deg C | 507:62 | 27 | 82 | [7 empty] | Attr | York RTU.Heating Control.Hydronic Heat Control | 18 | Hydronic Heating Stage #2 Supply Air Setpoint | UCBapp.newUCB.Hydronic_Heating_Stg_2_SA_SP | Relinquish Default | FALSE |  |  |  | AV:29744 | HR:52 | ADF:133 |  | Value |  |  | Views.Clone.Partial Clone 1 | Hydronic Heating Stage #2 Supply Air Setpoint | 1675 | 221 |  |  | HydH2SA-Sp | 1709 | 278
Prop | Templates.Hydronic Heat Control | Hydronic Heat SAT Tempering Enabled | 1675 | 222 | 7004 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Disable | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Heating Control.Hydronic Heat Control | 18 | Hydronic Heat SAT Tempering Enabled | UCBapp.newUCB.Hydronic_Heat_SAT_Tempering_En | Relinquish Default | TRUE |  |  |  | MV:29745 | HR:116 | ADI:80 |  | Value |  |  | Views.Details.Heating.Proportional.Setup | Hydronic Heat SAT Tempering Enabled | 1675 | 222 |  | Views.Details.Htg.Prop.Setup | SATTempHydHt-En | 1709 | 279
Prop | Templates.Hydronic Heat Control | Hydronic Heat SAT Tempering Setpoint | 1675 | 223 | 7005 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 40 | 40 | 60 |  |  | 1s | 0 | deg C | 507:62 | 4 | 15 | [7 empty] | Attr | York RTU.Heating Control.Hydronic Heat Control | 18 | Hydronic Heat SAT Tempering Setpoint | UCBapp.newUCB.Hydronic_Heat_SAT_Tempering_SP | Relinquish Default | FALSE |  |  | York RTU.Heating Control.Hydronic Heat Control.Hydronic Heat SAT Tempering Enabled:Present Value = Yes | AV:29746 | HR:53 | ADF:134 |  | Value |  |  | Views.Details.Heating.Proportional.Setup | Hydronic Heat SAT Tempering Setpoint | 1675 | 223 |  | Views.Details.Htg.Prop.Setup | SATTempHydHt-Sp | 1709 | 280
Prop | Templates.Hydronic Heat Control | Hydronic Heat On due to Freeze Stat | 1675 | 354 | 7006 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Normal | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Heating Control.Hydronic Heat Control | 18 | Hydronic Heat On due to Freeze Stat | UCBapp.newUCB.Hydr_Heat_On_due_to_Freeze_Stat | Present Value | FALSE
Prop | Templates.Hydronic Heat Control | Hot Water Freeze Stat Opened When It Should Not | 1675 | 361 | 7007 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Heating Control.Hydronic Heat Control | 18 | Hot Water Freeze Stat Opened When It Should Not | UCBapp.newUCB.HW_F_S_Open_When_It_Should_Not | Present Value | FALSE
Tmpl | Templates.Economizer | [31 empty] | Model | York RTU.Economizer | 19 | [6 empty] | York RTU.System Controllers.Econ Controller:Present Value <> Not Present
Prop | Templates.Economizer | Economizer Enabled For Operation | 1675 | 50 | 7000 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Enable | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Economizer | 19 | Economizer Enabled For Operation | UCBapp.newUCB.ECON_EN | Relinquish Default | FALSE |  |  |  | MV:29747 | HR:118 | ADI:84 |  | Value |  |  | Views.Commissioning.Standard | Economizer Enabled For Operation | 1675 | 50 |  | Views.Commission.Standard | Econ-En | 1709 | 281
Prop | Templates.Economizer | Economizer Enabled For Operation | 1675 | 50 | 7000 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Enable | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Economizer | 19 | Economizer Enabled For Operation | UCBapp.newUCB.ECON_EN | Relinquish Default | FALSE |  |  |  | MV:29747 | HR:118 | ADI:84 |  | Value |  |  | Views.Details.Economizer.Setup | Economizer Enabled For Operation | 1675 | 50 |  | Views.Details.Econ.Setup | Econ-En | 1709 | 281
Prop | Templates.Economizer | Economizer Enabled For Operation | 1675 | 50 | 7000 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Enable | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Economizer | 19 | Economizer Enabled For Operation | UCBapp.newUCB.ECON_EN | Relinquish Default | FALSE |  |  |  | MV:29747 | HR:118 | ADI:84 |  | Value |  |  | Views.Details.Demand Ventilation | Economizer Enabled For Operation | 1675 | 50 |  | Views.Details.DVent | Econ-En | 1709 | 281
Prop | Templates.Economizer | Economizer Enabled For Operation | 1675 | 50 | 7000 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Enable | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Economizer | 19 | Economizer Enabled For Operation | UCBapp.newUCB.ECON_EN | Relinquish Default | FALSE |  |  |  | MV:29747 | HR:118 | ADI:84 |  | Value |  |  | Views.Details.Air Monitor Station | Economizer Enabled For Operation | 1675 | 50 |  | Views.Details.AirMonStation | Econ-En | 1709 | 281
Prop | Templates.Economizer | Economizer Damper % Command | 1675 | 51 | 7001 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | N/A |  |  |  |  | 1s | 0 | % | 507:98 | [9 empty] | Attr | York RTU.Economizer | 19 | Economizer Damper % Command | EconApp.Econ.OAD-O | Present Value | FALSE |  |  |  | AV:29748 | IR:253 | AO:3 |  | Value |  |  | Views.Details.Economizer.Service | Economizer Damper % Command | 1675 | 51 |  | Views.Details.Econ.Service | Econ | 1709 | 282
Prop | Templates.Economizer | Economizer Damper % Command | 1675 | 51 | 7001 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | N/A |  |  |  |  | 1s | 0 | % | 507:98 | [9 empty] | Attr | York RTU.Economizer | 19 | Economizer Damper % Command | EconApp.Econ.OAD-O | Present Value | FALSE |  |  |  | AV:29748 | IR:253 | AO:3 |  | Value |  |  | Views.Details.Single Zone VAV.Service | Economizer Damper % Command | 1675 | 51 |  | Views.Details.SZ VAV.Service | Econ | 1709 | 282
Prop | Templates.Economizer | Econ Free Cooling Available | 1675 | 52 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | No | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Economizer | 19 | Econ Free Cooling Available | EconApp.Econ.Free Cooling Available | Present Value | FALSE |  |  |  | MV:29749 | IR:369 | ADI:85 |  | Value |  |  | Views.Details.Cooling.Service.Unit | Econ Free Cooling Available | 1675 | 52 |  | Views.Details.Clg.Service.Unit | Econ-Free | 1709 | 283
Prop | Templates.Economizer | Econ Free Cooling Available | 1675 | 52 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | No | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Economizer | 19 | Econ Free Cooling Available | EconApp.Econ.Free Cooling Available | Present Value | FALSE |  |  |  | MV:29749 | IR:369 | ADI:85 |  | Value |  |  | Views.Details.Economizer.Service | Econ Free Cooling Available | 1675 | 52 |  | Views.Details.Econ.Service | Econ-Free | 1709 | 283
Prop | Templates.Economizer | Econ Free Cooling Available | 1675 | 52 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | No | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Economizer | 19 | Econ Free Cooling Available | EconApp.Econ.Free Cooling Available | Present Value | FALSE |  |  |  | MV:29749 | IR:369 | ADI:85 |  | Value |  |  | Views.Details.FanVFD.Service | Econ Free Cooling Available | 1675 | 52 |  | Views.Details.FanVFD.Service | Econ-Free | 1709 | 283
Prop | Templates.Economizer | Econ Free Cooling Available | 1675 | 52 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | No | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Economizer | 19 | Econ Free Cooling Available | EconApp.Econ.Free Cooling Available | Present Value | FALSE |  |  |  | MV:29749 | IR:369 | ADI:85 |  | Value |  |  | Views.Details.ERV | Econ Free Cooling Available | 1675 | 52 |  | Views.Details.ERV | Econ-Free | 1709 | 283
Prop | Templates.Economizer | Economizer Status | 1675 | 53 | 7003 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | SE RTU Economizer Status | 1738 | Disabled | [6 empty] | SE RTU Economizer Status | 1738 | [6 empty] | 1738 | 0 = Disabled 1 = Damper Not Functional 2 = Purge 3 = Unavailable-Sensor Fault ... |  | Attr | York RTU.Economizer | 19 | Economizer Status | UCBapp.newUCB.Economizer_Status | Present Value | FALSE |  |  |  | MV:29750 | IR:370 | ADI:86 |  | Value |  |  | Views.Status.Status | Economizer Status | 1675 | 53 |  | Views.Status.Status | Econ-S | 1709 | 284
Prop | Templates.Economizer | Economizer Status | 1675 | 53 | 7003 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | SE RTU Economizer Status | 1738 | Disabled | [6 empty] | SE RTU Economizer Status | 1738 | [6 empty] | 1738 | 0 = Disabled 1 = Damper Not Functional 2 = Purge 3 = Unavailable-Sensor Fault ... |  | Attr | York RTU.Economizer | 19 | Economizer Status | UCBapp.newUCB.Economizer_Status | Present Value | FALSE |  |  |  | MV:29750 | IR:370 | ADI:86 |  | Value |  |  | Views.Details.Economizer.Service | Economizer Status | 1675 | 53 |  | Views.Details.Econ.Service | Econ-S | 1709 | 284
Prop | Templates.Economizer | Free Cooling Current Mode | 1675 | 54 | 7004 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Actual Economizer Type Advanced | 3338 | Dry_Bulb_Temperature | [6 empty] | Actual Economizer Type Advanced | 3338 | [6 empty] | 3338 | 0 = Dry Bulb Temperature 1 = Differential Dry Bulb 2 = Single Enthalpy 3 = Dual Enthalpy 4 = Unreliable |  | Attr | York RTU.Economizer | 19 | Free Cooling Current Mode | UCBapp.newUCB.Free_Cooling_Current_Mode | Present Value | FALSE |  |  |  | MV:29751 | IR:371 | ADI:87 |  | Value |  |  | Views.Details.Economizer.Setup | Free Cooling Current Mode | 1675 | 54 |  | Views.Details.Econ.Setup | FreeClg-Mode | 1709 | 285
Prop | Templates.Economizer | Free Cooling Selection | 1675 | 55 | 7005 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | SE RTU Economizer Type | 3398 | Auto | [6 empty] | SE RTU Economizer Type | 3398 | [6 empty] | 3398 | 0 = Dry Bulb Temperature 1 = Single Enthalpy 2 = Dual Enthalpy 3 = Auto 4 = Differential Dry Bulb |  | Attr | York RTU.Economizer | 19 | Free Cooling Selection | UCBapp.newUCB.Free_Cooling_Selection | Relinquish Default | FALSE |  |  |  | MV:29752 | HR:119 | ADI:88 |  | Value |  |  | Views.Details.Economizer.Setup | Free Cooling Selection | 1675 | 55 |  | Views.Details.Econ.Setup | FreeClg-Sel | 1709 | 286
Prop | Templates.Economizer | Free Cooling Selection | 1675 | 55 | 7005 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | SE RTU Economizer Type | 3398 | Auto | [6 empty] | SE RTU Economizer Type | 3398 | [6 empty] | 3398 | 0 = Dry Bulb Temperature 1 = Single Enthalpy 2 = Dual Enthalpy 3 = Auto 4 = Differential Dry Bulb |  | Attr | York RTU.Economizer | 19 | Free Cooling Selection | UCBapp.newUCB.Free_Cooling_Selection | Relinquish Default | FALSE |  |  |  | MV:29752 | HR:119 | ADI:88 |  | Value |  |  | Views.Clone.Partial Clone 1 | Free Cooling Selection | 1675 | 55 |  |  | FreeClg-Sel | 1709 | 286
Prop | Templates.Economizer | Economizer Outdoor Air Temp Enable Setpoint | 1675 | 56 | 7006 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 55 | 0 | 80 |  |  | 1s | 0 | deg C | 507:62 | -17.8 | 27 | [7 empty] | Attr | York RTU.Economizer | 19 | Economizer Outdoor Air Temp Enable Setpoint | UCBapp.newUCB.Econ_OA_Temp_Enable_SP | Relinquish Default | FALSE |  |  |  | AV:29753 | HR:55 | ADF:136 |  | Value |  |  | Views.Details.Economizer.Setup | Economizer Outdoor Air Temp Enable Setpoint | 1675 | 56 |  | Views.Details.Econ.Setup | EconOAT-SpEn | 1709 | 287
Prop | Templates.Economizer | Economizer Outdoor Air Temp Enable Setpoint | 1675 | 56 | 7006 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 55 | 0 | 80 |  |  | 1s | 0 | deg C | 507:62 | -17.8 | 27 | [7 empty] | Attr | York RTU.Economizer | 19 | Economizer Outdoor Air Temp Enable Setpoint | UCBapp.newUCB.Econ_OA_Temp_Enable_SP | Relinquish Default | FALSE |  |  |  | AV:29753 | HR:55 | ADF:136 |  | Value |  |  | Views.Clone.Partial Clone 1 | Economizer Outdoor Air Temp Enable Setpoint | 1675 | 56 |  |  | EconOAT-SpEn | 1709 | 287
Prop | Templates.Economizer | Economizer Outdoor Air Enthalpy Setpoint | 1675 | 57 | 7007 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | Btu/lb dry air | 507:24 | 27 | 10 | 50 |  |  | 1s | 0 | kJ/kg | 507:125 | 23 | 116 | [7 empty] | Attr | York RTU.Economizer | 19 | Economizer Outdoor Air Enthalpy Setpoint | UCBapp.newUCB.Econ_Outdoor_Air_Enthalpy_SP | Relinquish Default | FALSE |  |  |  | AV:29754 | HR:56 | ADF:137 |  | Value |  |  | Views.Details.Economizer.Setup | Economizer Outdoor Air Enthalpy Setpoint | 1675 | 57 |  | Views.Details.Econ.Setup | EconOAEnth-Sp | 1709 | 288
Prop | Templates.Economizer | Economizer Outdoor Air Enthalpy Setpoint | 1675 | 57 | 7007 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | Btu/lb dry air | 507:24 | 27 | 10 | 50 |  |  | 1s | 0 | kJ/kg | 507:125 | 23 | 116 | [7 empty] | Attr | York RTU.Economizer | 19 | Economizer Outdoor Air Enthalpy Setpoint | UCBapp.newUCB.Econ_Outdoor_Air_Enthalpy_SP | Relinquish Default | FALSE |  |  |  | AV:29754 | HR:56 | ADF:137 |  | Value |  |  | Views.Clone.Partial Clone 1 | Economizer Outdoor Air Enthalpy Setpoint | 1675 | 57 |  |  | EconOAEnth-Sp | 1709 | 288
Prop | Templates.Economizer | Low Ambient Economizer Setpoint | 1675 | 58 | 7008 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 35 | -20 | 60 |  |  | 1s | 0 | deg C | 507:62 | -29 | 15 | [7 empty] | Attr | York RTU.Economizer | 19 | Low Ambient Economizer Setpoint | EconApp.Econ.Low_Ambient_Temperature_Setpoint | Relinquish Default | FALSE |  |  |  | AV:29755 | HR:57 | ADF:138 |  | Value |  |  | Views.Details.Economizer.Setup | Low Ambient Economizer Setpoint | 1675 | 58 |  | Views.Details.Econ.Setup | LowAmb-Sp | 1709 | 289
Prop | Templates.Economizer | Low Ambient Economizer Setpoint | 1675 | 58 | 7008 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 35 | -20 | 60 |  |  | 1s | 0 | deg C | 507:62 | -29 | 15 | [7 empty] | Attr | York RTU.Economizer | 19 | Low Ambient Economizer Setpoint | EconApp.Econ.Low_Ambient_Temperature_Setpoint | Relinquish Default | FALSE |  |  |  | AV:29755 | HR:57 | ADF:138 |  | Value |  |  | Views.Clone.Partial Clone 1 | Low Ambient Economizer Setpoint | 1675 | 58 |  |  | LowAmb-Sp | 1709 | 289
Prop | Templates.Economizer | Low Ambient Economizer Minimum Position | 1675 | 59 | 7009 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 0 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Economizer | 19 | Low Ambient Economizer Minimum Position | EconApp.Econ.Low Ambient Damper Position | Relinquish Default | FALSE |  |  |  | AV:29756 | HR:58 | ADF:139 |  | Value |  |  | Views.Details.Economizer.Setup | Low Ambient Economizer Minimum Position | 1675 | 59 |  | Views.Details.Econ.Setup | LowAmb-MinPos | 1709 | 290
Prop | Templates.Economizer | Low Ambient Economizer Minimum Position | 1675 | 59 | 7009 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 0 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Economizer | 19 | Low Ambient Economizer Minimum Position | EconApp.Econ.Low Ambient Damper Position | Relinquish Default | FALSE |  |  |  | AV:29756 | HR:58 | ADF:139 |  | Value |  |  | Views.Clone.Partial Clone 1 | Low Ambient Economizer Minimum Position | 1675 | 59 |  |  | LowAmb-MinPos | 1709 | 290
Prop | Templates.Economizer | Economizer Damper Position | 1675 | 335 | 7011 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | % open | 507:264 | N/A |  |  |  |  | 1s | 0 | % open | 507:264 | [9 empty] | Attr | York RTU.Economizer | 19 | Economizer Damper Position | EconApp.Econ.MAD-POS | Present Value | FALSE |  |  |  | AV:29824 | IR:254 | ADF:141 |  | Value |  |  | Views.Details.Economizer.Service | Economizer Damper Position | 1675 | 335 |  | Views.Details.Econ.Service | EconDampPos | 1709 | 449
Prop | Templates.Economizer | Economizer Damper Position | 1675 | 335 | 7011 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | % open | 507:264 | N/A |  |  |  |  | 1s | 0 | % open | 507:264 | [9 empty] | Attr | York RTU.Economizer | 19 | Economizer Damper Position | EconApp.Econ.MAD-POS | Present Value | FALSE |  |  |  | AV:29824 | IR:254 | ADF:141 |  | Value |  |  | Views.Details.Demand Ventilation | Economizer Damper Position | 1675 | 335 |  | Views.Details.DVent | EconDampPos | 1709 | 449
Prop | Templates.Economizer | Economizer Damper Position | 1675 | 335 | 7011 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | % open | 507:264 | N/A |  |  |  |  | 1s | 0 | % open | 507:264 | [9 empty] | Attr | York RTU.Economizer | 19 | Economizer Damper Position | EconApp.Econ.MAD-POS | Present Value | FALSE |  |  |  | AV:29824 | IR:254 | ADF:141 |  | Value |  |  | Views.Details.Air Monitor Station | Economizer Damper Position | 1675 | 335 |  | Views.Details.AirMonStation | EconDampPos | 1709 | 449
Prop | Templates.Economizer | Mixed Air Temperature | 1675 | 62 | 7012 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | N/A |  |  |  |  | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Economizer | 19 | Mixed Air Temperature | EconApp.Econ.MA-T | Present Value | FALSE |  |  |  | AV:29760 | IR:255 | AI:29 |  | Value |  |  | Views.Summary.Sensors.Sensors | Mixed Air Temperature | 1675 | 62 |  | Views.Summary.Sensors.Sensors | MAT | 1709 | 293
Prop | Templates.Economizer | Supply Air Humidity | 1675 | 224 | 7014 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | %RH | 507:29 | N/A |  |  |  |  | 1s | 0 | %RH | 507:29 | [9 empty] | Attr | York RTU.Economizer | 19 | Supply Air Humidity | EconApp.Econ.SA-H | Present Value | FALSE |  |  |  | AV:29762 | IR:256 | AI:30 |  | Value |  |  | Views.Summary.Sensors.Sensors | Supply Air Humidity | 1675 | 224 |  | Views.Summary.Sensors.Sensors | SAH | 1709 | 295
Prop | Templates.Economizer | Return Air Enthalpy | 1675 | 64 | 7015 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | Btu/lb | 507:117 | 0 |  |  |  |  | 1s | 0 | kJ/kg | 507:125 | [9 empty] | Attr | York RTU.Economizer | 19 | Return Air Enthalpy | UCBapp.newUCB.Return_Air_Enthalpy | Present Value | FALSE |  |  |  | AV:29763 | IR:257 | ADF:142 |  | Value |  |  | Views.Details.Economizer.Service | Return Air Enthalpy | 1675 | 64 |  | Views.Details.Econ.Service | RA-Enth | 1709 | 296
Prop | Templates.Economizer | Economizer Minimum Position Setpoint | 1675 | 292 | 7017 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 10 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Economizer | 19 | Economizer Minimum Position Setpoint | EconApp.Econ.User Damper Min Pos | Relinquish Default | FALSE |  |  |  | AV:29759 | HR:77 | ADF:163 |  | Value |  |  | Views.Commissioning.Standard | Economizer Minimum Position Setpoint | 1675 | 292 |  | Views.Commission.Standard | Econ-MinPos | 1709 | 381
Prop | Templates.Economizer | Economizer Minimum Position Setpoint | 1675 | 292 | 7017 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 10 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Economizer | 19 | Economizer Minimum Position Setpoint | EconApp.Econ.User Damper Min Pos | Relinquish Default | FALSE |  |  |  | AV:29759 | HR:77 | ADF:163 |  | Value |  |  | Views.Details.Economizer.Setup | Economizer Minimum Position Setpoint | 1675 | 292 |  | Views.Details.Econ.Setup | Econ-MinPos | 1709 | 381
Prop | Templates.Economizer | Economizer Minimum Position Setpoint | 1675 | 292 | 7017 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 10 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Economizer | 19 | Economizer Minimum Position Setpoint | EconApp.Econ.User Damper Min Pos | Relinquish Default | FALSE |  |  |  | AV:29759 | HR:77 | ADF:163 |  | Value |  |  | Views.Commissioning.Quick Start | Economizer Minimum Position Setpoint | 1675 | 292 |  | Views.Commission.Quick Start | Econ-MinPos | 1709 | 381
Prop | Templates.Economizer | Economizer Minimum Position Setpoint | 1675 | 292 | 7017 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 10 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Economizer | 19 | Economizer Minimum Position Setpoint | EconApp.Econ.User Damper Min Pos | Relinquish Default | FALSE |  |  |  | AV:29759 | HR:77 | ADF:163 |  | Value |  |  | Views.Clone.Partial Clone 1 | Economizer Minimum Position Setpoint | 1675 | 292 |  |  | Econ-MinPos | 1709 | 381
Prop | Templates.Economizer | Economizer Minimum Position Setpoint | 1675 | 292 | 7017 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 10 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Economizer | 19 | Economizer Minimum Position Setpoint | EconApp.Econ.User Damper Min Pos | Relinquish Default | FALSE |  |  |  | AV:29759 | HR:77 | ADF:163 |  | Value |  |  | Views.Details.Verasys | Economizer Minimum Position Setpoint | 1675 | 292 |  | Views.Details.Verasys | Econ-MinPos | 1709 | 381
Prop | Templates.Economizer | Excess Outdoor Air | 1675 | 293 | 7018 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | No | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Economizer | 19 | Excess Outdoor Air | EconApp.Econ.Excess_OA_Fault | Present Value | FALSE |  |  |  | MV:29809 | IR:372 | ADI:89
Prop | Templates.Economizer | Not Economizing When Should | 1675 | 294 | 7019 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | No | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Economizer | 19 | Not Economizing When Should | EconApp.Econ.Econ No Op Fault | Present Value | FALSE |  |  |  | MV:29810 | IR:373 | ADI:90
Prop | Templates.Economizer | Damper Not Modulating | 1675 | 295 | 7020 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | No | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Economizer | 19 | Damper Not Modulating | EconApp.Econ.Damper Mod Fault | Present Value | FALSE |  |  |  | MV:29811 | IR:374 | ADI:91
Prop | Templates.Economizer | Economizing When Should Not | 1675 | 296 | 7021 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | No | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Economizer | 19 | Economizing When Should Not | EconApp.Econ.Econ Op Fault | Present Value | FALSE |  |  |  | MV:29812 | IR:375 | ADI:92
Prop | Templates.Economizer | Mixed Air Temperature Sensor Fault | 1675 | 310 | 7022 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | No | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Economizer | 19 | Mixed Air Temperature Sensor Fault | EconApp.Econ.MA-T Alarm | Present Value | FALSE
Prop | Templates.Economizer | Supply Air Humidity Sensor Fault | 1675 | 311 | 7023 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | No | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Economizer | 19 | Supply Air Humidity Sensor Fault | EconApp.Econ.SA-H Alarm | Present Value | FALSE
Prop | Templates.Economizer | Economizer Damper Minimum Position Low Speed Fan | 1675 | 327 | 7025 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 15 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Economizer | 19 | Economizer Damper Minimum Position Low Speed Fan | EconApp.Econ.Damper Min Pos Low Speed Fan | Relinquish Default | FALSE |  |  |  | AV:29808 | HR:54 | ADF:135 |  | Value |  |  | Views.Commissioning.Standard | Economizer Damper Minimum Position Low Speed Fan | 1675 | 327 |  | Views.Commission.Standard | LowSpeedFan-MinPos | 1709 | 447
Prop | Templates.Economizer | Economizer Damper Minimum Position Low Speed Fan | 1675 | 327 | 7025 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 15 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Economizer | 19 | Economizer Damper Minimum Position Low Speed Fan | EconApp.Econ.Damper Min Pos Low Speed Fan | Relinquish Default | FALSE |  |  |  | AV:29808 | HR:54 | ADF:135 |  | Value |  |  | Views.Details.Economizer.Setup | Economizer Damper Minimum Position Low Speed Fan | 1675 | 327 |  | Views.Details.Econ.Setup | LowSpeedFan-MinPos | 1709 | 447
Prop | Templates.Economizer | Economizer Damper Minimum Position Low Speed Fan | 1675 | 327 | 7025 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 15 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Economizer | 19 | Economizer Damper Minimum Position Low Speed Fan | EconApp.Econ.Damper Min Pos Low Speed Fan | Relinquish Default | FALSE |  |  |  | AV:29808 | HR:54 | ADF:135 |  | Value |  |  | Views.Clone.Partial Clone 1 | Economizer Damper Minimum Position Low Speed Fan | 1675 | 327 |  |  | LowSpeedFan-MinPos | 1709 | 447
Prop | Templates.Economizer | Not Economizing - No Supply Air Sensor | 1675 | 362 | 7026 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Economizer | 19 | Not Economizing - No Supply Air Sensor | UCBapp.newUCB.Not_Economizing_No_SA_Sensor | Present Value | FALSE
Prop | Templates.Economizer | EconMech Setup | 1675 | 498 | 7027 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | SE RTU EconMech Setup | 1752 | Option_B | [6 empty] | SE RTU EconMech Setup | 1752 | [6 empty] | 1752 | 0 = Option A 1 = Option B |  | Attr | York RTU.Economizer | 19 | EconMech Setup | UCBapp.newUCB.EconMech_Setup | Relinquish Default | FALSE |  |  |  | MV:29912 | HR:409 | ADI:126 |  | Value |  |  | Views.Details.Economizer.Setup | EconMech Setup | 1675 | 498 |  | Views.Details.Econ.Setup | EconMechStp | 1709 | 630
Prop | Templates.Economizer | EconMech Setup | 1675 | 498 | 7027 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | SE RTU EconMech Setup | 1752 | Option_B | [6 empty] | SE RTU EconMech Setup | 1752 | [6 empty] | 1752 | 0 = Option A 1 = Option B |  | Attr | York RTU.Economizer | 19 | EconMech Setup | UCBapp.newUCB.EconMech_Setup | Relinquish Default | FALSE |  |  |  | MV:29912 | HR:409 | ADI:126 |  | Value |  |  | Views.Clone.Partial Clone 1 | EconMech Setup | 1675 | 498 |  |  | EconMechStp | 1709 | 630
Prop | Templates.Economizer | Economizer Fault Detection Enable | 1675 | 626 | 7028 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Disable/Enable | 658 | Disable | [6 empty] | Disable/Enable | 658 | [6 empty] | 658 | 0 = Disable 1 = Enable |  | Attr | York RTU.Economizer | 19 | Economizer Fault Detection Enable | EconApp.Econ.Econ Fault Detect Enable | Relinquish Default | FALSE |  |  |  | MV:29915 | HR:132; HR:843 | ADI:115 |  | Value |  |  | Views.Details.Economizer.Setup | Economizer Fault Detection Enable | 1675 | 626 |  | Views.Details.Econ.Setup | EconFltDetectEn | 1709 | 646
Prop | Templates.Economizer | Economizer Fault Detection Enable | 1675 | 626 | 7028 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Disable/Enable | 658 | Disable | [6 empty] | Disable/Enable | 658 | [6 empty] | 658 | 0 = Disable 1 = Enable |  | Attr | York RTU.Economizer | 19 | Economizer Fault Detection Enable | EconApp.Econ.Econ Fault Detect Enable | Relinquish Default | FALSE |  |  |  | MV:29915 | HR:132; HR:843 | ADI:115 |  | Value |  |  | Views.Clone.Partial Clone 1 | Economizer Fault Detection Enable | 1675 | 626 |  |  | EconFltDetectEn | 1709 | 646
Prop | Templates.Economizer | FDD Economizer Alarm Delay | 1675 | 633 | 7029 | TRUE | TRUE | FALSE | 4 | Float | 10s | 7 | seconds | 507:73 | 600 | 0 | 3600 |  |  | 10s | 0 | seconds | 507:73 | 0 | 3600 | [7 empty] | Attr | York RTU.Economizer | 19 | FDD Economizer Alarm Delay | EconApp.Econ.Econ Fault Detect Alarm Delay | Relinquish Default | FALSE |  |  |  | AV:29916 | HR:431 | ADF:182 |  | Value |  |  | Views.Details.Economizer.Service | FDD Economizer Alarm Delay | 1675 | 633 |  | Views.Details.Econ.Service | EconAlrmDly | 1709 | 653
Prop | Templates.Economizer | FDD Economizer Damper Allowed Error | 1675 | 634 | 7030 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 8 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Economizer | 19 | FDD Economizer Damper Allowed Error | EconApp.Econ.Damper Pos Error | Relinquish Default | FALSE |  |  |  | AV:29917 | HR:432 | ADF:183 |  | Value |  |  | Views.Details.Economizer.Service | FDD Economizer Damper Allowed Error | 1675 | 634 |  | Views.Details.Econ.Service | EconPosErr | 1709 | 654
Prop | Templates.Economizer | FDD Damper Min Position Tolerance | 1675 | 635 | 7031 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 5 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Economizer | 19 | FDD Damper Min Position Tolerance | EconApp.Econ.Damper Min Pos Fault Tolerance | Relinquish Default | FALSE |  |  |  | AV:29918 | HR:433 | ADF:184 |  | Value |  |  | Views.Details.Economizer.Service | FDD Damper Min Position Tolerance | 1675 | 635 |  | Views.Details.Econ.Service | EconMinErr | 1709 | 655
Prop | Templates.Economizer | Calibration Fault Detect Enable | 1714 | 226 | 7032 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Disable/Enable | 658 | Disable | [6 empty] | Disable/Enable | 658 | [6 empty] | 658 | 0 = Disable 1 = Enable |  | Attr | York RTU.Economizer | 19 | Calibration Fault Detect Enable | EconApp.Econ.Calibration_Fault_Enable | Relinquish Default | FALSE |  |  |  | MV:30067 |  | ADI:191 |  | Value |  |  | Views.Details.Economizer.Setup | Calibration Fault Detect Enable | 1714 | 226 |  | Views.Details.Econ.Setup | CalFaultDetectEn | 1709 | 723
Prop | Templates.Economizer | Econ Sensor Fault Indications | 1675 | 1605 | 7033 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Disable/Enable | 658 | Enable | [6 empty] | Disable/Enable | 658 | [6 empty] | 658 | 0 = Disable 1 = Enable |  | Attr | York RTU.Economizer | 19 | Econ Sensor Fault Indications | EconApp.Econ.Econ Sensor Fault Enable | Relinquish Default | FALSE |  |  |  | MV:30078 | HR:849 | ADI:197 |  | Value |  |  | Views.Commissioning.Options | Econ Sensor Fault Indications | 1675 | 1605 |  | Views.Commission.Options | EconSensorFaults | 1709 | 736
Prop | Templates.Economizer | Mixed Air Temperature Cooling Limit | 2644 | 274 | 7034 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Disable/Enable | 658 | Yes | [6 empty] | Disable/Enable | 658 | [6 empty] | 658 | 0 = Disable 1 = Enable |  | Attr | York RTU.Economizer | 19 | Mixed Air Temperature Cooling Limit | EconApp.Econ.MA_Low_Limit_Enable | Relinquish Default | FALSE |  |  |  | MV:30111 | HR:881 | ADI:215 |  | Value |  |  | Views.Details.Economizer.Setup | Mixed Air Temperature Cooling Limit | 2644 | 274 |  | Views.Details.Econ.Setup | MATClgLim | 2645 | 293
Tmpl | Templates.Hot Gas Reheat | [31 empty] | Model | York RTU.Hot Gas Reheat | 20
Prop | Templates.Hot Gas Reheat | Hot Gas Reheat Enabled For Operation | 1675 | 249 | 7000 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | No | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Hot Gas Reheat | 20 | Hot Gas Reheat Enabled For Operation | UCBapp.newUCB.HGR_Enabled_For_Operation | Relinquish Default | TRUE |  |  |  | MV:29789 | HR:123 | ADI:96 |  | Value |  |  | Views.Commissioning.Options | Hot Gas Reheat Enabled For Operation | 1675 | 249 |  | Views.Commission.Options | HGR-En | 1709 | 323
Prop | Templates.Hot Gas Reheat | Hot Gas Reheat Enabled For Operation | 1675 | 249 | 7000 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | No | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Hot Gas Reheat | 20 | Hot Gas Reheat Enabled For Operation | UCBapp.newUCB.HGR_Enabled_For_Operation | Relinquish Default | TRUE |  |  |  | MV:29789 | HR:123 | ADI:96 |  | Value |  |  | Views.Details.Hot Gas Reheat.Setup | Hot Gas Reheat Enabled For Operation | 1675 | 249 |  | Views.Details.HGR.Setup | HGR-En | 1709 | 323
Prop | Templates.Hot Gas Reheat | Hot Gas Reheat Enabled For Operation | 1675 | 249 | 7000 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | No | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Hot Gas Reheat | 20 | Hot Gas Reheat Enabled For Operation | UCBapp.newUCB.HGR_Enabled_For_Operation | Relinquish Default | TRUE |  |  |  | MV:29789 | HR:123 | ADI:96 |  | Value |  |  | Views.Details.Mod Hot Gas Reheat.Setup | Hot Gas Reheat Enabled For Operation | 1675 | 249 |  | Views.Details.ModHGR.Setup | HGR-En | 1709 | 323
Prop | Templates.Hot Gas Reheat | Hot Gas Reheat Command | 1675 | 250 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [6 empty] | 647 | 0 = Off 1 = On |  | Attr | York RTU.Hot Gas Reheat | 20 | Hot Gas Reheat Command | UCBapp.newUCB.HGRHV_C | Present Value | FALSE |  |  | York RTU.Hot Gas Reheat.HGR-Inst:Present Value = 1 | MV:29790 | IR:379 | BO:16 |  | Value |  |  | Views.Details.Hot Gas Reheat.Service | Hot Gas Reheat Command | 1675 | 250 |  | Views.Details.HGR.Service | HGR | 1709 | 324
Prop | Templates.Hot Gas Reheat | Hot Gas Reheat Status | 1675 | 251 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | SE RTU Hot Gas Reheat | 1744 | Off_Idle | [6 empty] | SE RTU Hot Gas Reheat | 1744 | [6 empty] | 1744 | 0 = Off-Idle 1 = On-Normal Command 2 = On-Alternate Operation Command 3 = Off-Disabled |  | Attr | York RTU.Hot Gas Reheat | 20 | Hot Gas Reheat Status | UCBapp.newUCB.Hot_Gas_Reheat_Status | Present Value | FALSE |  |  |  | MV:29791 | IR:380 | BI:41 |  | Value |  |  | Views.Status.Status | Hot Gas Reheat Status | 1675 | 251 |  | Views.Status.Status | HGR-S | 1709 | 325
Prop | Templates.Hot Gas Reheat | Hot Gas Reheat Status | 1675 | 251 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | SE RTU Hot Gas Reheat | 1744 | Off_Idle | [6 empty] | SE RTU Hot Gas Reheat | 1744 | [6 empty] | 1744 | 0 = Off-Idle 1 = On-Normal Command 2 = On-Alternate Operation Command 3 = Off-Disabled |  | Attr | York RTU.Hot Gas Reheat | 20 | Hot Gas Reheat Status | UCBapp.newUCB.Hot_Gas_Reheat_Status | Present Value | FALSE |  |  |  | MV:29791 | IR:380 | BI:41 |  | Value |  |  | Views.Details.Hot Gas Reheat.Service | Hot Gas Reheat Status | 1675 | 251 |  | Views.Details.HGR.Service | HGR-S | 1709 | 325
Prop | Templates.Hot Gas Reheat | Hot Gas Reheat Status | 1675 | 251 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | SE RTU Hot Gas Reheat | 1744 | Off_Idle | [6 empty] | SE RTU Hot Gas Reheat | 1744 | [6 empty] | 1744 | 0 = Off-Idle 1 = On-Normal Command 2 = On-Alternate Operation Command 3 = Off-Disabled |  | Attr | York RTU.Hot Gas Reheat | 20 | Hot Gas Reheat Status | UCBapp.newUCB.Hot_Gas_Reheat_Status | Present Value | FALSE |  |  |  | MV:29791 | IR:380 | BI:41 |  | Value |  |  | Views.Details.Mod Hot Gas Reheat.Service | Hot Gas Reheat Status | 1675 | 251 |  | Views.Details.ModHGR.Service | HGR-S | 1709 | 325
Prop | Templates.Hot Gas Reheat | Hot Gas Reheat Humidity Setpoint | 1675 | 252 | 7003 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | %RH | 507:29 | 50 | 0 | 100 |  |  | 1s | 0 | %RH | 507:29 | 0 | 100 |  |  |  | Humidity Setpoint |  |  |  | Attr | York RTU.Hot Gas Reheat | 20 | Hot Gas Reheat Humidity Setpoint | UCBapp.newUCB.Hot_Gas_Reheat_Humidity_SP | Relinquish Default | FALSE |  |  | York RTU.Hot Gas Reheat.HGR-Inst:Present Value > 0 | AV:29792 | HR:68 | ADF:153 |  | Value |  |  | Views.Details.Hot Gas Reheat.Setup | Hot Gas Reheat Humidity Setpoint | 1675 | 252 |  | Views.Details.HGR.Setup | HGRHum-Sp | 1709 | 326
Prop | Templates.Hot Gas Reheat | Hot Gas Reheat Humidity Setpoint | 1675 | 252 | 7003 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | %RH | 507:29 | 50 | 0 | 100 |  |  | 1s | 0 | %RH | 507:29 | 0 | 100 |  |  |  | Humidity Setpoint |  |  |  | Attr | York RTU.Hot Gas Reheat | 20 | Hot Gas Reheat Humidity Setpoint | UCBapp.newUCB.Hot_Gas_Reheat_Humidity_SP | Relinquish Default | FALSE |  |  | York RTU.Hot Gas Reheat.HGR-Inst:Present Value > 0 | AV:29792 | HR:68 | ADF:153 |  | Value |  |  | Views.Details.Hot Gas Reheat.Service | Hot Gas Reheat Humidity Setpoint | 1675 | 252 |  | Views.Details.HGR.Service | HGRHum-Sp | 1709 | 326
Prop | Templates.Hot Gas Reheat | Hot Gas Reheat Humidity Setpoint | 1675 | 252 | 7003 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | %RH | 507:29 | 50 | 0 | 100 |  |  | 1s | 0 | %RH | 507:29 | 0 | 100 |  |  |  | Humidity Setpoint |  |  |  | Attr | York RTU.Hot Gas Reheat | 20 | Hot Gas Reheat Humidity Setpoint | UCBapp.newUCB.Hot_Gas_Reheat_Humidity_SP | Relinquish Default | FALSE |  |  | York RTU.Hot Gas Reheat.HGR-Inst:Present Value > 0 | AV:29792 | HR:68 | ADF:153 |  | Value |  |  | Views.Details.Mod Hot Gas Reheat.Setup | Hot Gas Reheat Humidity Setpoint | 1675 | 252 |  | Views.Details.ModHGR.Setup | HGRHum-Sp | 1709 | 326
Prop | Templates.Hot Gas Reheat | Hot Gas Reheat Humidity Setpoint | 1675 | 252 | 7003 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | %RH | 507:29 | 50 | 0 | 100 |  |  | 1s | 0 | %RH | 507:29 | 0 | 100 |  |  |  | Humidity Setpoint |  |  |  | Attr | York RTU.Hot Gas Reheat | 20 | Hot Gas Reheat Humidity Setpoint | UCBapp.newUCB.Hot_Gas_Reheat_Humidity_SP | Relinquish Default | FALSE |  |  | York RTU.Hot Gas Reheat.HGR-Inst:Present Value > 0 | AV:29792 | HR:68 | ADF:153 |  | Value |  |  | Views.Details.Mod Hot Gas Reheat.Service | Hot Gas Reheat Humidity Setpoint | 1675 | 252 |  | Views.Details.ModHGR.Service | HGRHum-Sp | 1709 | 326
Prop | Templates.Hot Gas Reheat | Hot Gas Reheat Alternate Operation Enabled | 1675 | 253 | 7004 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | No | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Hot Gas Reheat | 20 | Hot Gas Reheat Alternate Operation Enabled | UCBapp.newUCB.HGR_Alternate_Operation_En | Relinquish Default | FALSE |  |  | York RTU.Hot Gas Reheat.HGR-Inst:Present Value = 1 | MV:29793 | HR:124 | ADI:97 |  | Value |  |  | Views.Details.Hot Gas Reheat.Setup | Hot Gas Reheat Alternate Operation Enabled | 1675 | 253 |  | Views.Details.HGR.Setup | HGRAlt-En | 1709 | 327
Prop | Templates.Hot Gas Reheat | Hot Gas Reheat Alternate Operation Writeable | 1675 | 254 | 7005 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | No | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Hot Gas Reheat | 20 | Hot Gas Reheat Alternate Operation Writeable | UCBapp.newUCB.HGR_Alternate_Op_Writeable | Relinquish Default | FALSE |  |  | York RTU.Hot Gas Reheat.HGR-Inst:Present Value = 1 | MV:29794 | HR:410 | ADI:127 |  | Value |  |  | Views.Details.Hot Gas Reheat.Setup | Hot Gas Reheat Alternate Operation Writeable | 1675 | 254 |  | Views.Details.HGR.Setup | HGRAltWrite | 1709 | 328
Prop | Templates.Hot Gas Reheat | HGR Unoccupied Humidity Setpoint | 1675 | 602 | 7006 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 70 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Hot Gas Reheat | 20 | HGR Unoccupied Humidity Setpoint | UCBapp.newUCB.HGR_Unoccupied_Humidity_SP | Relinquish Default | FALSE |  |  | York RTU.Hot Gas Reheat.HGR-Inst:Present Value > 0 | AV:29903 | HR:78 | ADF:164 |  | Value |  |  | Views.Details.Hot Gas Reheat.Setup | HGR Unoccupied Humidity Setpoint | 1675 | 602 |  | Views.Details.HGR.Setup | HGRUnoccHum-SP | 1709 | 642
Prop | Templates.Hot Gas Reheat | HGR Unoccupied Humidity Setpoint | 1675 | 602 | 7006 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 70 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Hot Gas Reheat | 20 | HGR Unoccupied Humidity Setpoint | UCBapp.newUCB.HGR_Unoccupied_Humidity_SP | Relinquish Default | FALSE |  |  | York RTU.Hot Gas Reheat.HGR-Inst:Present Value > 0 | AV:29903 | HR:78 | ADF:164 |  | Value |  |  | Views.Details.Mod Hot Gas Reheat.Setup | HGR Unoccupied Humidity Setpoint | 1675 | 602 |  | Views.Details.ModHGR.Setup | HGRUnoccHum-SP | 1709 | 642
Prop | Templates.Hot Gas Reheat | HGR Enabled for Unoccupied Operation | 1675 | 603 | 7007 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Enable | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Hot Gas Reheat | 20 | HGR Enabled for Unoccupied Operation | UCBapp.newUCB.HGR_En_for_Unocc_Operation | Relinquish Default | FALSE |  |  | York RTU.Hot Gas Reheat.HGR-Inst:Present Value > 0 | MV:29904 | HR:133 | ADI:116 |  | Value |  |  | Views.Details.Hot Gas Reheat.Setup | HGR Enabled for Unoccupied Operation | 1675 | 603 |  | Views.Details.HGR.Setup | HGRUnocc-En | 1709 | 643
Prop | Templates.Hot Gas Reheat | HGR Enabled for Unoccupied Operation | 1675 | 603 | 7007 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Enable | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Hot Gas Reheat | 20 | HGR Enabled for Unoccupied Operation | UCBapp.newUCB.HGR_En_for_Unocc_Operation | Relinquish Default | FALSE |  |  | York RTU.Hot Gas Reheat.HGR-Inst:Present Value > 0 | MV:29904 | HR:133 | ADI:116 |  | Value |  |  | Views.Details.Mod Hot Gas Reheat.Setup | HGR Enabled for Unoccupied Operation | 1675 | 603 |  | Views.Details.ModHGR.Setup | HGRUnocc-En | 1709 | 643
Prop | Templates.Hot Gas Reheat | HGR Humidity Setpoint Differential | 1675 | 872 | 7008 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 3 | 1 | 10 |  |  | 1s | 0 | % | 507:98 | 1 | 10 | [7 empty] | Attr | York RTU.Hot Gas Reheat | 20 | HGR Humidity Setpoint Differential | UCBapp.newUCB.HGR_Humidity_SP_Differential | Relinquish Default | FALSE |  |  | York RTU.Hot Gas Reheat.HGR-Inst:Present Value > 0 | AV:29937 | HR:886 | ADF:220 |  | Value |  |  | Views.Details.Hot Gas Reheat.Setup | HGR Humidity Setpoint Differential | 1675 | 872 |  | Views.Details.HGR.Setup | HGR-Diff | 1709 | 669
Prop | Templates.Hot Gas Reheat | HGR Humidity Setpoint Differential | 1675 | 872 | 7008 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 3 | 1 | 10 |  |  | 1s | 0 | % | 507:98 | 1 | 10 | [7 empty] | Attr | York RTU.Hot Gas Reheat | 20 | HGR Humidity Setpoint Differential | UCBapp.newUCB.HGR_Humidity_SP_Differential | Relinquish Default | FALSE |  |  | York RTU.Hot Gas Reheat.HGR-Inst:Present Value > 0 | AV:29937 | HR:886 | ADF:220 |  | Value |  |  | Views.Details.Mod Hot Gas Reheat.Setup | HGR Humidity Setpoint Differential | 1675 | 872 |  | Views.Details.ModHGR.Setup | HGR-Diff | 1709 | 669
Prop | Templates.Hot Gas Reheat | Aux Mode | 1675 | 791 | 7009 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Off/On | 647 | Off | [6 empty] | Off/On | 647 | [6 empty] | 647 | 0 = Off 1 = On |  | Attr | York RTU.Hot Gas Reheat | 20 | Aux Mode | UCBapp.newUCB.Hybrid_Mode | Relinquish Default | FALSE |  |  | York RTU.Hot Gas Reheat.HGR-Inst:Present Value = 1 | MV:30139 | HR:888 | ADI:222 |  | Value |  |  | Views.Details.Hot Gas Reheat.Setup | Hybrid Mode | 1714 | 251 |  | Views.Details.HGR.Setup | Hybrid Mode | 1714 | 251
Prop | Templates.Hot Gas Reheat | Use DFS For Dehum | 1714 | 224 | 7010 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | No | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Hot Gas Reheat | 20 | Use DFS For Dehum | UCBapp.newUCB.USE_DFS_FOR_DEHUM | Relinquish Default | FALSE |  |  | York RTU.Hot Gas Reheat.HGR-Inst:Present Value > 0 | MV:30138 | HR:887 | ADI:221 |  | Value |  |  | Views.Details.Hot Gas Reheat.Setup | Use DFS For Dehum | 1714 | 224 |  | Views.Details.HGR.Setup | Use DFS For Dehum | 1714 | 224
Prop | Templates.Hot Gas Reheat | Use DFS For Dehum | 1714 | 224 | 7010 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | No | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Hot Gas Reheat | 20 | Use DFS For Dehum | UCBapp.newUCB.USE_DFS_FOR_DEHUM | Relinquish Default | FALSE |  |  | York RTU.Hot Gas Reheat.HGR-Inst:Present Value > 0 | MV:30138 | HR:887 | ADI:221 |  | Value |  |  | Views.Details.Mod Hot Gas Reheat.Setup | Use DFS For Dehum | 1714 | 224 |  | Views.Details.ModHGR.Setup | Use DFS For Dehum | 1714 | 224
Prop | Templates.Hot Gas Reheat | Dehumidification % Command | 1714 | 234 | 7011 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 80 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Hot Gas Reheat | 20 | Dehumidification % Command | UCBapp.newUCB.Dehum_Fan_Speed | Relinquish Default | FALSE |  |  | York RTU.Hot Gas Reheat.HGR-Inst:Present Value > 1 |  |  |  |  | Value |  |  | Views.Details.Mod Hot Gas Reheat.Setup | Dehumidification % Command | 1714 | 234 |  | Views.Details.ModHGR.Setup | Dehum%Cmd | 1709 | 731
Prop | Templates.Hot Gas Reheat | Dehumidify In Satisfied | 1714 | 228 | 7012 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | False/True | 1701 | Enable | [6 empty] | False/True | 1701 | [6 empty] | 1701 | 0 = False 1 = True |  | Attr | York RTU.Hot Gas Reheat | 20 | Dehumidify In Satisfied | UCBapp.newUCB.Dehum_In_Satisfied | Relinquish Default | FALSE |  |  | York RTU.Hot Gas Reheat.HGR-Inst:Present Value > 1 | MV:30099 | HR:875 | ADI:209 |  | Value |  |  | Views.Details.Mod Hot Gas Reheat.Setup | Dehumidify In Satisfied | 1714 | 228 |  | Views.Details.ModHGR.Setup | SatisfiedDehum | 1709 | 726
Prop | Templates.Hot Gas Reheat | Max Heating Setpoint | 1675 | 514 | 7013 | TRUE | TRUE | FALSE | 4 | Float | 10ths | 5 | % | 507:98 | 80 | 0 | 100 |  |  | 10ths | 0 | % | 507:98 | 0 | 100 | [6 empty] | Max HGR Valve Position | Attr | York RTU.Hot Gas Reheat | 20 | Max Heating Setpoint | FourStageApp.FourStage.HOT_GAS_REHEAT_MAX_PCT | Relinquish Default | FALSE |  |  | York RTU.Hot Gas Reheat.HGR-Inst:Present Value > 1 | AV:30137 | HR:885 | ADF:219 |  | Value |  |  | Views.Details.Mod Hot Gas Reheat.Setup | HGR Mod Valve Max Setpoint | 1714 | 275 |  | Views.Details.ModHGR.Setup | HGRModVlvMaxSP | 1709 | 782
Prop | Templates.Hot Gas Reheat | Min Heating Setpoint | 1675 | 1448 | 7014 | TRUE | TRUE | FALSE | 4 | Float | 10ths | 5 | % | 507:98 | 20 | 0 | 100 |  |  | 10ths | 0 | % | 507:98 | 0 | 100 | [6 empty] | HGR Minimum Valve Position | Attr | York RTU.Hot Gas Reheat | 20 | Min Heating Setpoint | FourStageApp.FourStage.HOT_GAS_REHEAT_MIN_PCT | Relinquish Default | FALSE |  |  | York RTU.Hot Gas Reheat.HGR-Inst:Present Value > 1 | AV:30136 | HR:884 | ADF:218 |  | Value |  |  | Views.Details.Mod Hot Gas Reheat.Setup | HGR Mod Valve Min Setpoint | 1714 | 274 |  | Views.Details.ModHGR.Setup | HGRModVlvMinSP | 1709 | 783
Prop | Templates.Hot Gas Reheat | Operational Evap Temperature Sp | 1714 | 232 | 7015 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | 0 | 0 | 100 |  |  | 10ths | 0 | deg C | 507:62 | 0 | 100 | [7 empty] | Attr | York RTU.Hot Gas Reheat | 20 | Operational Evap Temperature Sp | UCBapp.newUCB.Evap_Air_Temp_SP | Present Value | FALSE |  |  | York RTU.Hot Gas Reheat.HGR-Inst:Present Value > 1 | AV:30095 | IR:872 | ADF:206 |  | Value |  |  | Views.Details.Mod Hot Gas Reheat.Service | Operational Evap Temperature Sp | 1714 | 232 |  | Views.Details.ModHGR.Service | OprEvapTempSp | 1709 | 729
Prop | Templates.Hot Gas Reheat | Operational HGR Temperature Sp | 1714 | 233 | 7016 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | 70 | 0 | 100 |  |  | 10ths | 0 | deg C | 507:62 | 0 | 100 | [7 empty] | Attr | York RTU.Hot Gas Reheat | 20 | Operational HGR Temperature Sp | UCBapp.newUCB.HGR_Setpoint | Present Value | FALSE |  |  | York RTU.Hot Gas Reheat.HGR-Inst:Present Value > 1 | AV:30096 | IR:873 | ADF:207 |  | Value |  |  | Views.Details.Mod Hot Gas Reheat.Service | Operational HGR Temperature Sp | 1714 | 233 |  | Views.Details.ModHGR.Service | OprHGRTempSp | 1709 | 730
Prop | Templates.Hot Gas Reheat | Setpoint Lower Limit | 1675 | 1494 | 7017 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 42 | 40 | 79 |  |  | 1s | 0 | deg C | 507:62 | 4 | 26 | [6 empty] | Used for the Evap Setpoint Limit. This will always be the lower setpoint minus 3 degrees. | Attr | York RTU.Hot Gas Reheat | 20 | Setpoint Lower Limit | UCBapp.newUCB.Dehum_Evap_Low_SP_Lim | Present Value | FALSE
Prop | Templates.Hot Gas Reheat | Dehum Evap Low Setpoint | 1714 | 229 | 7018 | TRUE | TRUE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | 40 | 40 |  |  | 7017 | 10ths | 0 | deg C | 507:62 | 4 |  |  | 7017 | [5 empty] | Attr | York RTU.Hot Gas Reheat | 20 | Dehum Evap Low Setpoint | UCBapp.newUCB.Dehum_Evap_Low_Setpoint | Relinquish Default | FALSE |  |  | York RTU.Hot Gas Reheat.HGR-Inst:Present Value > 1 | AV:30097 | HR:874 | ADF:208 |  | Value |  |  | Views.Details.Mod Hot Gas Reheat.Setup | Dehum Evap Low Setpoint | 1714 | 229 |  | Views.Details.ModHGR.Setup | DehumEvapLowSp | 1709 | 725
Prop | Templates.Hot Gas Reheat | VAV Cooling Supply Air Temp Upper Setpoint | 1675 | 137 | 7019 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 60 | 41 | 70 |  |  | 1s | 0 | deg C | 507:62 | 5 | 21 | [7 empty] | Attr | York RTU.Hot Gas Reheat | 20 | VAV Cooling Supply Air Temp Upper Setpoint | UCBapp.newUCB.Upper_SAT_Clg_Setpoint | Relinquish Default | FALSE |  |  | York RTU.Hot Gas Reheat.HGR-Inst:Present Value > 1 |  |  |  |  | Value |  |  | Views.Details.Mod Hot Gas Reheat.Setup | VAV Cooling Supply Air Temp Upper Setpoint | 1675 | 137 |  | Views.Details.ModHGR.Setup | SATUp-Sp | 1709 | 119
Prop | Templates.Hot Gas Reheat | VAV Cooling Supply Air Temp Lower Setpoint | 1675 | 138 | 7020 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 55 | 40 | 69 |  |  | 1s | 0 | deg C | 507:62 | 4 | 20 | [7 empty] | Attr | York RTU.Hot Gas Reheat | 20 | VAV Cooling Supply Air Temp Lower Setpoint | UCBapp.newUCB.Lower_SAT_Clg_Setpoint | Relinquish Default | FALSE |  |  | York RTU.Hot Gas Reheat.HGR-Inst:Present Value > 1 |  |  |  |  | Value |  |  | Views.Details.Mod Hot Gas Reheat.Setup | VAV Cooling Supply Air Temp Lower Setpoint | 1675 | 138 |  | Views.Details.ModHGR.Setup | SATLo-Sp | 1709 | 120
Prop | Templates.Hot Gas Reheat | VAV Supply Air Temp Reset Setpoint | 1675 | 139 | 7021 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 72 | 40 | 85 |  |  | 1s | 0 | deg C | 507:62 | 4 | 30 | [7 empty] | Attr | York RTU.Hot Gas Reheat | 20 | VAV Supply Air Temp Reset Setpoint | UCBapp.newUCB.VAV_Supply_Air_Temp_Reset_SP | Relinquish Default | FALSE |  |  | York RTU.Hot Gas Reheat.HGR-Inst:Present Value = 3 |  |  |  |  | Value |  |  | Views.Details.Mod Hot Gas Reheat.Setup | VAV Supply Air Temp Reset Setpoint | 1675 | 139 |  | Views.Details.ModHGR.Setup | SATRst-Sp | 1709 | 121
Prop | Templates.Hot Gas Reheat | Occupied Cooling Setpoint | 1675 | 562 | 7022 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 72 | 45 | 98 |  |  | 1s | 0 | deg C | 507:62 | 7 | 36 | [7 empty] | Attr | York RTU.Hot Gas Reheat | 20 | Occupied Cooling Setpoint | UCBapp.newUCB.Occ_Clg_Setpoint | Relinquish Default | FALSE |  |  | York RTU.Hot Gas Reheat.HGR-Inst:Present Value = 2 |  |  |  |  | Value |  |  | Views.Details.Mod Hot Gas Reheat.Setup | Occupied Cooling Setpoint | 1675 | 562 |  | Views.Details.ModHGR.Setup | ClgOcc-Sp | 1709 | 123
Prop | Templates.Hot Gas Reheat | Condenser Fan 2 OAT Cutout Setpoint | 1714 | 235 | 7023 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 75 | 50 | 80 |  |  | 1s | 0 | deg C | 507:62 | 10 | 27 | [7 empty] | Attr | York RTU.Hot Gas Reheat | 20 | Condenser Fan 2 OAT Cutout Setpoint | UCBapp.newUCB.OAT_HGR_CF2_Cutout | Relinquish Default | FALSE |  |  | York RTU.Hot Gas Reheat.HGR-Inst:Present Value > 1 | AV:30101 | HR:877 | ADF:211 |  | Value |  |  | Views.Details.Mod Hot Gas Reheat.Setup | Condenser Fan 2 OAT Cutout Setpoint | 1714 | 235 |  | Views.Details.ModHGR.Setup | CondFan2OATCutoutSP | 1709 | 732
Prop | Templates.Hot Gas Reheat | Modulating HGR Valve Full Open Allowed | 1714 | 231 | 7024 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | No | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Hot Gas Reheat | 20 | Modulating HGR Valve Full Open Allowed | FourStageApp.FourStage.HGR_FULL_OPEN_AVAIL | Relinquish Default | FALSE |  |  | York RTU.Hot Gas Reheat.HGR-Inst:Present Value > 1 | MV:30100 | HR:876 | ADI:210 |  | Value |  |  | Views.Details.Mod Hot Gas Reheat.Setup | Modulating HGR Valve Full Open Allowed | 1714 | 231 |  | Views.Details.ModHGR.Setup | ModHGRFullOpenAllowed | 1709 | 728
Prop | Templates.Hot Gas Reheat | HGR-Inst | 1709 | 7 | 7025 | TRUE | FALSE | FALSE | 16 | Byte | 1s | 6 |  | 507:95 | 0 | 0 | 4 |  |  | 1s | 0 |  | 507:95 | 0 | 4 | [6 empty] | HGR Presence Indication logic | Attr | York RTU.Hot Gas Reheat | 20 | HGR-Inst | UCBapp.newUCB.EFF_HGR_DISPLAY | Present Value | TRUE
Prop | Templates.Hot Gas Reheat | Evaporator Coil Temp | 1675 | 100 | 7026 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | 0 |  |  |  |  | 10ths | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Hot Gas Reheat | 20 | Evaporator Coil Temp | UCBapp.newUCB.Evap_Air_Temp | Present Value | FALSE |  |  | York RTU.Hot Gas Reheat.HGR-Inst:Present Value > 1 | AV:30074 | IR:854 | ADF:196 |  | Value |  |  | Views.Details.Mod Hot Gas Reheat.Service | Evaporator Coil Temp | 1675 | 100 |  | Views.Details.ModHGR.Service | Evaporator Coil Temp | 1675 | 100
Prop | Templates.Hot Gas Reheat | Hot Gas Reheat Command | 1675 | 250 | 7027 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | % | 507:98 | N/A |  |  |  |  | 10ths | 0 | % | 507:98 | [9 empty] | Attr | York RTU.Hot Gas Reheat | 20 | Hot Gas Reheat Command | FourStageApp.FourStage.HGR_MOD | Present Value | FALSE |  |  | UCBapp.newUCB.ModHGR_PI:Present Value = Active | AV:29949 | IR:389 | AO:6 |  | Value |  |  | Views.Details.Mod Hot Gas Reheat.Service | Hot Gas Reheat Command | 1675 | 250 |  | Views.Details.ModHGR.Service | ModHGR | 1709 | 737
Prop | Templates.Hot Gas Reheat | Hot Gas Reheat Command | 1675 | 250 | 7027 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | % | 507:98 | N/A |  |  |  |  | 10ths | 0 | % | 507:98 | [9 empty] | Attr | York RTU.Hot Gas Reheat | 20 | Hot Gas Reheat Command | FourStageApp.FourStage.HGR_MOD | Present Value | FALSE |  |  | UCBapp.newUCB.ModHGR_PI:Present Value = Active | AV:29949 | IR:389 | AO:6 |  | Value |  |  | Views.Details.Hot Gas Reheat.Service | Hot Gas Reheat Command | 1675 | 250 |  | Views.Details.HGR.Service | ModHGR | 1709 | 737
Prop | Templates.Hot Gas Reheat | Supply Air Temperature | 1675 | 182 | 7028 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | N/A |  |  |  |  | 10ths | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Hot Gas Reheat | 20 | Supply Air Temperature | UCBapp.newUCB.SA_T | Present Value | FALSE |  |  | York RTU.Hot Gas Reheat.HGR-Inst:Present Value > 1 |  |  |  |  | Value |  |  | Views.Details.Mod Hot Gas Reheat.Service | Supply Air Temperature | 1675 | 182 |  | Views.Details.ModHGR.Service | SAT | 1709 | 80
Prop | Templates.Hot Gas Reheat | Hot Gas Reheat Bleed Valve Command | 2644 | 238 | 7029 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Close/Open | 939 | N/A | [6 empty] | Close/Open | 939 | [6 empty] | 939 | 0 = Close 1 = Open |  | Attr | York RTU.Hot Gas Reheat | 20 | Hot Gas Reheat Bleed Valve Command | UCBapp.newUCB.HGRHV_C | Present Value | FALSE |  |  | York RTU.Hot Gas Reheat.HGR-Inst:Present Value > 1 | MV:30075 | IR:855 | BO:17 |  | Value |  |  | Views.Details.Mod Hot Gas Reheat.Service | Hot Gas Reheat Bleed Valve Command | 2644 | 238 |  | Views.Details.ModHGR.Service | Hot Gas Reheat Bleed Valve Command | 2644 | 238
Prop | Templates.Hot Gas Reheat | Condenser Fan 2 Max Pos Cutout Enable | 1714 | 253 | 7030 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Disable/Enable | 658 | Enable | [6 empty] | Disable/Enable | 658 | [6 empty] | 658 | 0 = Disable 1 = Enable |  | Attr | York RTU.Hot Gas Reheat | 20 | Condenser Fan 2 Max Pos Cutout Enable | UCBapp.newUCB.HGR_Max_Pos_CF2_Cutout_En | Relinquish Default | FALSE |  |  | York RTU.Hot Gas Reheat.HGR-Inst:Present Value > 1 |  |  |  |  | Value |  |  | Views.Details.Mod Hot Gas Reheat.Setup | Condenser Fan 2 Max Pos Cutout Enable | 1714 | 253 |  | Views.Details.ModHGR.Setup | CondFan2MaxPosCutoutEn | 1709 | 753
Prop | Templates.Hot Gas Reheat | Use OprST for HGR | 1714 | 272 | 7031 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | No | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Hot Gas Reheat | 20 | Use OprST for HGR | UCBapp.newUCB.Use_OprST_For_HGR | Relinquish Default | FALSE |  |  | York RTU.Hot Gas Reheat.HGR-Inst:Present Value > 1 | MV:30133 | HR:883 | ADI:217 |  | Value |  |  | Views.Details.Mod Hot Gas Reheat.Setup | Use OprST for HGR | 1714 | 272 |  | Views.Details.ModHGR.Setup | UseOprSTforHGR | 1709 | 777
Prop | Templates.Hot Gas Reheat | Neutral Air ModHGR Enable | 1714 | 281 | 7032 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Disable/Enable | 658 | Disable | [6 empty] | Disable/Enable | 658 | [6 empty] | 658 | 0 = Disable 1 = Enable |  | Attr | York RTU.Hot Gas Reheat | 20 | Neutral Air ModHGR Enable | UCBapp.newUCB.Neutral_Air_ModHGR_Enable | Relinquish Default | TRUE |  |  | York RTU.Neutral Air ModHGR Enable:Present Value = Enable | MV:30143 | HR:894 | ADI:228 |  | Value |  |  | Views.Details.Hot Gas Reheat.Setup | Neutral Air ModHGR Enable | 1714 | 281 |  | Views.Details.HGR.Setup | NeuAirModHGR-En | 1709 | 792
Prop | Templates.Hot Gas Reheat | Neutral Air ModHGR Offset | 1714 | 282 | 7033 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | delta deg F | 507:120 | 0 | -10 | 10 |  |  | 1s | 0 | delta deg C | 507:359 | -6 | 6 | [7 empty] | Attr | York RTU.Hot Gas Reheat | 20 | Neutral Air ModHGR Offset | UCBapp.newUCB.Neutral_Air_ModHGR_Offset | Relinquish Default | FALSE |  |  | York RTU.Hot Gas Reheat.Neutral Air ModHGR Enable:Present Value = Enable | AV:30145 | HR:895 | ADF:229 |  | Value |  |  | Views.Details.Hot Gas Reheat.Setup | Neutral Air ModHGR Offset | 1714 | 282 |  | Views.Details.HGR.Setup | NeuAirModHGR-Off | 1709 | 793
Tmpl | Templates.Exhaust Fan Control | [31 empty] | Model | York RTU.Exhaust Fan Control | 21 | [6 empty] | York RTU.System Controllers.Econ Controller:Present Value <> Not Present
Prop | Templates.Exhaust Fan Control | Exhaust Fan Command | 1675 | 235 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [6 empty] | 647 | 0 = Off 1 = On |  | Attr | York RTU.Exhaust Fan Control | 21 | Exhaust Fan Command | EconApp.Econ.EXFAN-C | Present Value | FALSE |  |  | York RTU.Exhaust Type:Present Value <> None | MV:29775 | IR:376 | BO:15 |  | Value |  |  | Views.Details.Power Exhaust.Service | Exhaust Fan Command | 1675 | 235 |  | Views.Details.PowerEx.Service | ExFan | 1709 | 309
Prop | Templates.Exhaust Fan Control | Exhaust Fan Command | 1675 | 235 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [6 empty] | 647 | 0 = Off 1 = On |  | Attr | York RTU.Exhaust Fan Control | 21 | Exhaust Fan Command | EconApp.Econ.EXFAN-C | Present Value | FALSE |  |  | York RTU.Exhaust Type:Present Value <> None | MV:29775 | IR:376 | BO:15 |  | Value |  |  | Views.Details.ERV | Exhaust Fan Command | 1675 | 235 |  | Views.Details.ERV | ExFan | 1709 | 309
Prop | Templates.Exhaust Fan Control | Exhaust Fan VFD % Command | 1675 | 236 | 7002 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | N/A |  |  |  |  | 1s | 0 | % | 507:98 | [9 empty] | Attr | York RTU.Exhaust Fan Control | 21 | Exhaust Fan VFD % Command | EconApp.Econ.EX-O | Present Value | FALSE |  |  | York RTU.Exhaust Type:Present Value = Variable Frequency Fan | AV:29776 | IR:258 | AO:4 |  | Value |  |  | Views.Details.Power Exhaust.Service | Exhaust Fan VFD % Command | 1675 | 236 |  | Views.Details.PowerEx.Service | ExFanVFD | 1709 | 310
Prop | Templates.Exhaust Fan Control | Exhaust Fan Status | 1675 | 237 | 7003 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | SE RTU Exhaust Fan | 1745 | Off_Idle | [6 empty] | SE RTU Exhaust Fan | 1745 | [6 empty] | 1745 | 0 = Off-Idle 1 = On-Normal Command 2 = Off-Disabled 3 = Off-VFD Fault ... |  | Attr | York RTU.Exhaust Fan Control | 21 | Exhaust Fan Status | UCBapp.newUCB.Exhaust_Fan_Status | Present Value | FALSE |  |  | York RTU.Exhaust Type:Present Value <> None | MV:29777 | IR:377 | BI:39 |  | Value |  |  | Views.Status.Status | Exhaust Fan Status | 1675 | 237 |  | Views.Status.Status | ExF-S | 1709 | 311
Prop | Templates.Exhaust Fan Control | Exhaust Fan Status | 1675 | 237 | 7003 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | SE RTU Exhaust Fan | 1745 | Off_Idle | [6 empty] | SE RTU Exhaust Fan | 1745 | [6 empty] | 1745 | 0 = Off-Idle 1 = On-Normal Command 2 = Off-Disabled 3 = Off-VFD Fault ... |  | Attr | York RTU.Exhaust Fan Control | 21 | Exhaust Fan Status | UCBapp.newUCB.Exhaust_Fan_Status | Present Value | FALSE |  |  | York RTU.Exhaust Type:Present Value <> None | MV:29777 | IR:377 | BI:39 |  | Value |  |  | Views.Details.Power Exhaust.Service | Exhaust Fan Status | 1675 | 237 |  | Views.Details.PowerEx.Service | ExF-S | 1709 | 311
Prop | Templates.Exhaust Fan Control | Exhaust Fan VFD Fault | 1675 | 238 | 7004 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | N/A | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Exhaust Fan Control | 21 | Exhaust Fan VFD Fault | EconApp.Econ.EXFANFAULT-S | Present Value | FALSE |  |  | York RTU.Exhaust Type:Present Value = Variable Frequency Fan | MV:29778 | IR:378 | BI:40 |  | Value |  |  | Views.Details.Power Exhaust.Service | Exhaust Fan VFD Fault | 1675 | 238 |  | Views.Details.PowerEx.Service | ExFanVFDFlt | 1709 | 312
Prop | Templates.Exhaust Fan Control | Exhaust Fan Accumulated Runtime | 1675 | 239 | 7005 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | hours | 507:71 | [5 empty] | 1s | 0 | hours | 507:71 | [9 empty] | Attr | York RTU.Exhaust Fan Control | 21 | Exhaust Fan Accumulated Runtime | 8-1/EconApp.Ex_Fan_Runtime_Total | Relinquish Default | FALSE |  |  | York RTU.Exhaust Type:Present Value <> None | AV:29779 | IR:259 | ADF:146 |  | Value |  |  | Views.Details.Power Exhaust.Service | Exhaust Fan Accumulated Runtime | 1675 | 239 |  | Views.Details.PowerEx.Service | ExF-RunTim | 1709 | 313
Prop | Templates.Exhaust Fan Control | Building Pressure Setpoint | 1675 | 240 | 7006 | TRUE | TRUE | FALSE | 4 | Float | 1000ths | 3 | in wc | 507:58 | 0.1 | -0.25 | 0.25 |  |  | 1000ths | 0 | kPa | 507:54 | -0.07 | 0.07 | [7 empty] | Attr | York RTU.Exhaust Fan Control | 21 | Building Pressure Setpoint | EconApp.Econ.BSP_Setpoint | Relinquish Default | FALSE |  |  | York RTU.Exhaust Type:Present Value <> Non-Modulating | AV:29780 | HR:63 | ADF:147 |  | Value |  |  | Views.Details.Power Exhaust.Setup | Building Pressure Setpoint | 1675 | 240 |  | Views.Details.PowerEx.Setup | Bldg-Sp | 1709 | 314
Prop | Templates.Exhaust Fan Control | Building Static Pressure | 1675 | 241 | 7007 | TRUE | FALSE | FALSE | 4 | Float | 1000ths | 3 | in wc | 507:58 | N/A |  |  |  |  | 1000ths | 0 | kPa | 507:54 | [9 empty] | Attr | York RTU.Exhaust Fan Control | 21 | Building Static Pressure | EconApp.Econ.BS-P | Present Value | FALSE |  |  | York RTU.Exhaust Type:Present Value <> Non-Modulating | AV:29781 | IR:260 | AI:33 |  | Value |  |  | Views.Summary.Sensors.Sensors | Building Static Pressure | 1675 | 241 |  | Views.Summary.Sensors.Sensors | BldgPres | 1709 | 315
Prop | Templates.Exhaust Fan Control | Building Static Pressure | 1675 | 241 | 7007 | TRUE | FALSE | FALSE | 4 | Float | 1000ths | 3 | in wc | 507:58 | N/A |  |  |  |  | 1000ths | 0 | kPa | 507:54 | [9 empty] | Attr | York RTU.Exhaust Fan Control | 21 | Building Static Pressure | EconApp.Econ.BS-P | Present Value | FALSE |  |  | York RTU.Exhaust Type:Present Value <> Non-Modulating | AV:29781 | IR:260 | AI:33 |  | Value |  |  | Views.Details.Power Exhaust.Service | Building Static Pressure | 1675 | 241 |  | Views.Details.PowerEx.Service | BldgPres | 1709 | 315
Prop | Templates.Exhaust Fan Control | Exhaust Damper % Command | 1675 | 242 | 7008 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | N/A |  |  |  |  | 1s | 0 | % | 507:98 | [9 empty] | Attr | York RTU.Exhaust Fan Control | 21 | Exhaust Damper % Command | EconApp.Econ.EX-O | Present Value | FALSE |  |  | York RTU.Exhaust Type:Present Value = Modulating Damper | AV:29782 | IR:261 | AO:5 |  | Value |  |  | Views.Details.Power Exhaust.Service | Exhaust Damper % Command | 1675 | 242 |  | Views.Details.PowerEx.Service | EAD-O | 1709 | 316
Prop | Templates.Exhaust Fan Control | Exhaust Damper Position for Exhaust Fan to Turn On | 1675 | 243 | 7009 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 80 | 20 | 99 |  |  | 1s | 0 | % | 507:98 | 20 | 99 | [7 empty] | Attr | York RTU.Exhaust Fan Control | 21 | Exhaust Damper Position for Exhaust Fan to Turn On | EconApp.Econ.Exhaust EF Turn On Setpoint | Relinquish Default | FALSE |  |  | York RTU.Exhaust Type:Present Value = Modulating Damper | AV:29783 | HR:64 | ADF:149 |  | Value |  |  | Views.Details.Power Exhaust.Setup | Exhaust Damper Position for Exhaust Fan to Turn On | 1675 | 243 |  | Views.Details.PowerEx.Setup | ExDmpPosFanOn | 1709 | 317
Prop | Templates.Exhaust Fan Control | Exhaust Damper Position for Exhaust Fan to Turn Off | 1675 | 244 | 7010 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 20 | 10 | 89 |  |  | 1s | 0 | % | 507:98 | 10 | 89 | [7 empty] | Attr | York RTU.Exhaust Fan Control | 21 | Exhaust Damper Position for Exhaust Fan to Turn Off | EconApp.Econ.Exhaust EF Turn Off Setpoint | Relinquish Default | FALSE |  |  | York RTU.Exhaust Type:Present Value = Modulating Damper | AV:29784 | HR:65 | ADF:150 |  | Value |  |  | Views.Details.Power Exhaust.Setup | Exhaust Damper Position for Exhaust Fan to Turn Off | 1675 | 244 |  | Views.Details.PowerEx.Setup | ExDmpPosFanOff | 1709 | 318
Prop | Templates.Exhaust Fan Control | Economizer Damper Position for Exhaust Fan to Turn On | 1675 | 245 | 7011 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 60 | 20 | 99 |  |  | 1s | 0 | % | 507:98 | 20 | 99 | [7 empty] | Attr | York RTU.Exhaust Fan Control | 21 | Economizer Damper Position for Exhaust Fan to Turn On | EconApp.Econ.Economizer EF Turn On Setpoint | Relinquish Default | FALSE |  |  | York RTU.Exhaust Type:Present Value = Non-Modulating | AV:29785 | HR:66 | ADF:151 |  | Value |  |  | Views.Details.Power Exhaust.Setup | Economizer Damper Position for Exhaust Fan to Turn On | 1675 | 245 |  | Views.Details.PowerEx.Setup | EconDmpPosFanOn | 1709 | 319
Prop | Templates.Exhaust Fan Control | Economizer Damper Position for Exhaust Fan to Turn Off | 1675 | 246 | 7012 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 20 | 10 | 89 |  |  | 1s | 0 | % | 507:98 | 10 | 89 | [7 empty] | Attr | York RTU.Exhaust Fan Control | 21 | Economizer Damper Position for Exhaust Fan to Turn Off | EconApp.Econ.Economizer EF Turn Off Setpoint | Relinquish Default | FALSE |  |  | York RTU.Exhaust Type:Present Value = Non-Modulating | AV:29786 | HR:67 | ADF:152 |  | Value |  |  | Views.Details.Power Exhaust.Setup | Economizer Damper Position for Exhaust Fan to Turn Off | 1675 | 246 |  | Views.Details.PowerEx.Setup | EconDmpPosFanOff | 1709 | 320
Prop | Templates.Exhaust Fan Control | ERV Enabled | 1675 | 247 | 7013 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Disable | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Exhaust Fan Control | 21 | ERV Enabled | EconApp.Econ.ERV Installed | Relinquish Default | TRUE |  |  | York RTU.Exhaust Type:Present Value <> None | MV:29787 | HR:121 | ADI:94 |  | Value |  |  | Views.Details.ERV | ERV Enabled | 1675 | 247 |  | Views.Details.ERV | ERV-En | 1709 | 321
Prop | Templates.Exhaust Fan Control | ERV Unoccupied Fan Enabled | 1675 | 248 | 7014 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Disable | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Exhaust Fan Control | 21 | ERV Unoccupied Fan Enabled | EconApp.Econ.ERV Unoccupied Fan | Relinquish Default | FALSE |  |  | York RTU.Exhaust Fan Control.ERV Enabled:Present Value = Yes | MV:29788 | HR:122 | ADI:95 |  | Value |  |  | Views.Details.ERV | ERV Unoccupied Fan Enabled | 1675 | 248 |  | Views.Details.ERV | ERVUnoccFan-En | 1709 | 322
Prop | Templates.Exhaust Fan Control | Building Static Pressure Sensor Fault | 1675 | 313 | 7015 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | No | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Exhaust Fan Control | 21 | Building Static Pressure Sensor Fault | EconApp.Econ.BS-P Alarm | Present Value | FALSE
Tmpl | Templates.Demand Ventilation Control | [31 empty] | Model | York RTU.Demand Ventilation Control | 23 | [6 empty] | York RTU.System Controllers.Econ Controller:Present Value <> Not Present
Prop | Templates.Demand Ventilation Control | Demand Ventilation Mode of Operation | 1675 | 225 | 7000 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | SE RTU DCV Mode | 1729 | Disabled | [6 empty] | SE RTU DCV Mode | 1729 | [6 empty] | 1729 | 0 = Disabled 1 = Controlled by IAQ 2 = Diff between IAQ and OAQ |  | Attr | York RTU.Demand Ventilation Control | 23 | Demand Ventilation Mode of Operation | UCBapp.newUCB.Demand_Ventilation_Mode_of_Op | Relinquish Default | FALSE |  |  |  | MV:29765 | HR:120 | ADI:93 |  | Value |  |  | Views.Commissioning.Options | Demand Ventilation Mode of Operation | 1675 | 225 |  | Views.Commission.Options | DVent-Mode | 1709 | 298
Prop | Templates.Demand Ventilation Control | Demand Ventilation Mode of Operation | 1675 | 225 | 7000 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | SE RTU DCV Mode | 1729 | Disabled | [6 empty] | SE RTU DCV Mode | 1729 | [6 empty] | 1729 | 0 = Disabled 1 = Controlled by IAQ 2 = Diff between IAQ and OAQ |  | Attr | York RTU.Demand Ventilation Control | 23 | Demand Ventilation Mode of Operation | UCBapp.newUCB.Demand_Ventilation_Mode_of_Op | Relinquish Default | FALSE |  |  |  | MV:29765 | HR:120 | ADI:93 |  | Value |  |  | Views.Details.Economizer.Setup | Demand Ventilation Mode of Operation | 1675 | 225 |  | Views.Details.Econ.Setup | DVent-Mode | 1709 | 298
Prop | Templates.Demand Ventilation Control | Demand Ventilation Mode of Operation | 1675 | 225 | 7000 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | SE RTU DCV Mode | 1729 | Disabled | [6 empty] | SE RTU DCV Mode | 1729 | [6 empty] | 1729 | 0 = Disabled 1 = Controlled by IAQ 2 = Diff between IAQ and OAQ |  | Attr | York RTU.Demand Ventilation Control | 23 | Demand Ventilation Mode of Operation | UCBapp.newUCB.Demand_Ventilation_Mode_of_Op | Relinquish Default | FALSE |  |  |  | MV:29765 | HR:120 | ADI:93 |  | Value |  |  | Views.Details.Demand Ventilation | Demand Ventilation Mode of Operation | 1675 | 225 |  | Views.Details.DVent | DVent-Mode | 1709 | 298
Prop | Templates.Demand Ventilation Control | Demand Ventilation Maximum Economizer Position | 1675 | 226 | 7001 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 50 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Demand Ventilation Control | 23 | Demand Ventilation Maximum Economizer Position | EconApp.Econ.Max DV Damper Position | Relinquish Default | FALSE |  |  |  | AV:29766 | HR:60 | ADF:143 |  | Value |  |  | Views.Details.Economizer.Setup | Demand Ventilation Maximum Economizer Position | 1675 | 226 |  | Views.Details.Econ.Setup | DVentMaxEconPos | 1709 | 299
Prop | Templates.Demand Ventilation Control | Demand Ventilation Maximum Economizer Position | 1675 | 226 | 7001 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 50 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Demand Ventilation Control | 23 | Demand Ventilation Maximum Economizer Position | EconApp.Econ.Max DV Damper Position | Relinquish Default | FALSE |  |  |  | AV:29766 | HR:60 | ADF:143 |  | Value |  |  | Views.Details.Demand Ventilation | Demand Ventilation Maximum Economizer Position | 1675 | 226 |  | Views.Details.DVent | DVentMaxEconPos | 1709 | 299
Prop | Templates.Demand Ventilation Control | Demand Ventilation Maximum Economizer Position | 1675 | 226 | 7001 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 50 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Demand Ventilation Control | 23 | Demand Ventilation Maximum Economizer Position | EconApp.Econ.Max DV Damper Position | Relinquish Default | FALSE |  |  |  | AV:29766 | HR:60 | ADF:143 |  | Value |  |  | Views.Clone.Partial Clone 1 | Demand Ventilation Maximum Economizer Position | 1675 | 226 |  |  | DVentMaxEconPos | 1709 | 299
Prop | Templates.Demand Ventilation Control | Demand Ventilation Indoor Air Quality Setpoint | 1675 | 227 | 7002 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | ppm | 507:96 | 1000 | 0 | 5000 |  |  | 1s | 0 | ppm | 507:96 | 0 | 5000 | [7 empty] | Attr | York RTU.Demand Ventilation Control | 23 | Demand Ventilation Indoor Air Quality Setpoint | EconApp.Econ.IAQ Setpoint | Relinquish Default | FALSE |  |  |  | AV:29767 | HR:61 | ADF:144 |  | Value |  |  | Views.Details.Economizer.Setup | Demand Ventilation Indoor Air Quality Setpoint | 1675 | 227 |  | Views.Details.Econ.Setup | DVentIAQ-Sp | 1709 | 300
Prop | Templates.Demand Ventilation Control | Demand Ventilation Indoor Air Quality Setpoint | 1675 | 227 | 7002 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | ppm | 507:96 | 1000 | 0 | 5000 |  |  | 1s | 0 | ppm | 507:96 | 0 | 5000 | [7 empty] | Attr | York RTU.Demand Ventilation Control | 23 | Demand Ventilation Indoor Air Quality Setpoint | EconApp.Econ.IAQ Setpoint | Relinquish Default | FALSE |  |  |  | AV:29767 | HR:61 | ADF:144 |  | Value |  |  | Views.Details.Demand Ventilation | Demand Ventilation Indoor Air Quality Setpoint | 1675 | 227 |  | Views.Details.DVent | DVentIAQ-Sp | 1709 | 300
Prop | Templates.Demand Ventilation Control | Demand Ventilation Indoor Air Quality Setpoint | 1675 | 227 | 7002 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | ppm | 507:96 | 1000 | 0 | 5000 |  |  | 1s | 0 | ppm | 507:96 | 0 | 5000 | [7 empty] | Attr | York RTU.Demand Ventilation Control | 23 | Demand Ventilation Indoor Air Quality Setpoint | EconApp.Econ.IAQ Setpoint | Relinquish Default | FALSE |  |  |  | AV:29767 | HR:61 | ADF:144 |  | Value |  |  | Views.Clone.Partial Clone 1 | Demand Ventilation Indoor Air Quality Setpoint | 1675 | 227 |  |  | DVentIAQ-Sp | 1709 | 300
Prop | Templates.Demand Ventilation Control | Demand Ventilation Differential Setpoint | 1675 | 228 | 7003 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | ppm | 507:96 | 600 | 0 | 5000 |  |  | 1s | 0 | ppm | 507:96 | 0 | 5000 | [7 empty] | Attr | York RTU.Demand Ventilation Control | 23 | Demand Ventilation Differential Setpoint | UCBapp.newUCB.Demand_Ventilation_Diff_SP | Relinquish Default | FALSE |  |  |  | AV:29768 | HR:62 | ADF:145 |  | Value |  |  | Views.Details.Economizer.Setup | Demand Ventilation Differential Setpoint | 1675 | 228 |  | Views.Details.Econ.Setup | DVentDiff-Sp | 1709 | 301
Prop | Templates.Demand Ventilation Control | Demand Ventilation Differential Setpoint | 1675 | 228 | 7003 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | ppm | 507:96 | 600 | 0 | 5000 |  |  | 1s | 0 | ppm | 507:96 | 0 | 5000 | [7 empty] | Attr | York RTU.Demand Ventilation Control | 23 | Demand Ventilation Differential Setpoint | UCBapp.newUCB.Demand_Ventilation_Diff_SP | Relinquish Default | FALSE |  |  |  | AV:29768 | HR:62 | ADF:145 |  | Value |  |  | Views.Details.Demand Ventilation | Demand Ventilation Differential Setpoint | 1675 | 228 |  | Views.Details.DVent | DVentDiff-Sp | 1709 | 301
Prop | Templates.Demand Ventilation Control | Demand Ventilation Differential Setpoint | 1675 | 228 | 7003 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | ppm | 507:96 | 600 | 0 | 5000 |  |  | 1s | 0 | ppm | 507:96 | 0 | 5000 | [7 empty] | Attr | York RTU.Demand Ventilation Control | 23 | Demand Ventilation Differential Setpoint | UCBapp.newUCB.Demand_Ventilation_Diff_SP | Relinquish Default | FALSE |  |  |  | AV:29768 | HR:62 | ADF:145 |  | Value |  |  | Views.Clone.Partial Clone 1 | Demand Ventilation Differential Setpoint | 1675 | 228 |  |  | DVentDiff-Sp | 1709 | 301
Tmpl | Templates.Air Monitor Station | [31 empty] | Model | York RTU.Air Monitor Station | 24 | [6 empty] | York RTU.System Controllers.Econ Controller:Present Value <> Not Present
Prop | Templates.Air Monitor Station | Fresh Air Intake Setpoint | 1675 | 255 | 7000 | TRUE | TRUE | FALSE | 4 | Float | 10s | 7 | cfm | 507:84 | 80 | 0 | 50000 |  |  | 10s | 0 | L/s | 507:87 | 0 | 25000 | [7 empty] | Attr | York RTU.Air Monitor Station | 24 | Fresh Air Intake Setpoint | EconApp.Econ.Outdoor Air Flow Setpoint | Relinquish Default | FALSE |  |  |  | AV:29795 | HR:69 | ADF:154 |  | Value |  |  | Views.Details.Economizer.Setup | Fresh Air Intake Setpoint | 1675 | 255 |  | Views.Details.Econ.Setup | MOAFlow-Sp | 1709 | 329
Prop | Templates.Air Monitor Station | Fresh Air Intake Setpoint | 1675 | 255 | 7000 | TRUE | TRUE | FALSE | 4 | Float | 10s | 7 | cfm | 507:84 | 80 | 0 | 50000 |  |  | 10s | 0 | L/s | 507:87 | 0 | 25000 | [7 empty] | Attr | York RTU.Air Monitor Station | 24 | Fresh Air Intake Setpoint | EconApp.Econ.Outdoor Air Flow Setpoint | Relinquish Default | FALSE |  |  |  | AV:29795 | HR:69 | ADF:154 |  | Value |  |  | Views.Details.Air Monitor Station | Fresh Air Intake Setpoint | 1675 | 255 |  | Views.Details.AirMonStation | MOAFlow-Sp | 1709 | 329
Prop | Templates.Air Monitor Station | Fresh Air Intake Setpoint | 1675 | 255 | 7000 | TRUE | TRUE | FALSE | 4 | Float | 10s | 7 | cfm | 507:84 | 80 | 0 | 50000 |  |  | 10s | 0 | L/s | 507:87 | 0 | 25000 | [7 empty] | Attr | York RTU.Air Monitor Station | 24 | Fresh Air Intake Setpoint | EconApp.Econ.Outdoor Air Flow Setpoint | Relinquish Default | FALSE |  |  |  | AV:29795 | HR:69 | ADF:154 |  | Value |  |  | Views.Clone.Partial Clone 1 | Fresh Air Intake Setpoint | 1675 | 255 |  |  | MOAFlow-Sp | 1709 | 329
Prop | Templates.Air Monitor Station | Fresh Air Intake Value | 1675 | 256 | 7001 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | cfm | 507:84 | N/A |  |  |  |  | 1s | 0 | L/s | 507:87 | [9 empty] | Attr | York RTU.Air Monitor Station | 24 | Fresh Air Intake Value | EconApp.Econ.FAI-F | Present Value | FALSE |  |  |  | AV:29796 | IR:262 | ADF:155 |  | Value |  |  | Views.Details.Economizer.Service | Fresh Air Intake Value | 1675 | 256 |  | Views.Details.Econ.Service | Fr Air | 1709 | 330
Prop | Templates.Air Monitor Station | Fresh Air Intake Value | 1675 | 256 | 7001 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | cfm | 507:84 | N/A |  |  |  |  | 1s | 0 | L/s | 507:87 | [9 empty] | Attr | York RTU.Air Monitor Station | 24 | Fresh Air Intake Value | EconApp.Econ.FAI-F | Present Value | FALSE |  |  |  | AV:29796 | IR:262 | ADF:155 |  | Value |  |  | Views.Details.Air Monitor Station | Fresh Air Intake Value | 1675 | 256 |  | Views.Details.AirMonStation | Fr Air | 1709 | 330
Prop | Templates.Air Monitor Station | Fresh Air Intake Max Sensor Range | 1675 | 257 | 7002 | TRUE | TRUE | FALSE | 4 | Float | 10s | 7 | cfm | 507:84 | 10000 | 0 | 50000 |  |  | 10s | 0 | L/s | 507:87 | 0 | 25000 | [7 empty] | Attr | York RTU.Air Monitor Station | 24 | Fresh Air Intake Max Sensor Range | EconApp.Econ.FAI_Max_Sensor_Range | Relinquish Default | FALSE |  |  |  | AV:29797 | HR:70 | ADF:156 |  | Value |  |  | Views.Details.Economizer.Setup | Fresh Air Intake Max Sensor Range | 1675 | 257 |  | Views.Details.Econ.Setup | MOA-Range | 1709 | 331
Prop | Templates.Air Monitor Station | Fresh Air Intake Max Sensor Range | 1675 | 257 | 7002 | TRUE | TRUE | FALSE | 4 | Float | 10s | 7 | cfm | 507:84 | 10000 | 0 | 50000 |  |  | 10s | 0 | L/s | 507:87 | 0 | 25000 | [7 empty] | Attr | York RTU.Air Monitor Station | 24 | Fresh Air Intake Max Sensor Range | EconApp.Econ.FAI_Max_Sensor_Range | Relinquish Default | FALSE |  |  |  | AV:29797 | HR:70 | ADF:156 |  | Value |  |  | Views.Details.Air Monitor Station | Fresh Air Intake Max Sensor Range | 1675 | 257 |  | Views.Details.AirMonStation | MOA-Range | 1709 | 331
Prop | Templates.Air Monitor Station | Fresh Air Intake Max Sensor Range | 1675 | 257 | 7002 | TRUE | TRUE | FALSE | 4 | Float | 10s | 7 | cfm | 507:84 | 10000 | 0 | 50000 |  |  | 10s | 0 | L/s | 507:87 | 0 | 25000 | [7 empty] | Attr | York RTU.Air Monitor Station | 24 | Fresh Air Intake Max Sensor Range | EconApp.Econ.FAI_Max_Sensor_Range | Relinquish Default | FALSE |  |  |  | AV:29797 | HR:70 | ADF:156 |  | Value |  |  | Views.Clone.Partial Clone 1 | Fresh Air Intake Max Sensor Range | 1675 | 257 |  |  | MOA-Range | 1709 | 331
Prop | Templates.Air Monitor Station | Fresh Air Intake Sensor Fault | 1675 | 314 | 7003 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | No | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Air Monitor Station | 24 | Fresh Air Intake Sensor Fault | EconApp.Econ.FAI-F Alarm | Present Value | FALSE
Prop | Templates.Air Monitor Station | Fresh Air Intake Enable | 1675 | 741 | 7004 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Disable/Enable | 658 | Off | [6 empty] | Disable/Enable | 658 | [6 empty] | 658 | 0 = Disable 1 = Enable |  | Attr | York RTU.Air Monitor Station | 24 | Fresh Air Intake Enable | EconApp.Econ.Min OA Control | Relinquish Default | FALSE |  |  |  | MV:29933 | IR:134 | ADI:117 |  | Value |  |  | Views.Details.Air Monitor Station | Fresh Air Intake Enable | 1675 | 741 |  | Views.Details.AirMonStation | FrAir-En | 1709 | 664
Prop | Templates.Air Monitor Station | Fresh Air Range | 1675 | 1038 | 7005 | TRUE | TRUE | FALSE | 4 | Float | 10s | 7 | cfm | 507:84 | 40 | 0 | 5000 |  |  | 10s | 0 | L/s | 507:87 | 0 | 2500 | [7 empty] | Attr | York RTU.Air Monitor Station | 24 | Fresh Air Range | EconApp.Econ.Fresh_Air_Range | Relinquish Default | FALSE | [7 empty] | Value |  |  | Views.Details.Air Monitor Station | Fresh Air Range | 1675 | 1038 |  | Views.Details.AirMonStation | Control | 1709 | 387
Tmpl | Templates.HVAC Zone | [31 empty] | Model | York RTU.HVAC Zone | 25
Prop | Templates.HVAC Zone | Occupancy Input Source | 1675 | 9 | 7000 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Effective Occupancy Source | 1668 | Local_Input | [6 empty] | Effective Occupancy Source | 1668 | [6 empty] | 1668 | 0 = Local Input 1 = Local Network Sensor 2 = BAS Network Request 3 = Local Schedule 4 = Temporary Occupancy |  | Attr | York RTU.HVAC Zone | 25 | Occupancy Input Source | UCBapp.newUCB.Occupancy_Input_Source | Present Value | TRUE |  |  |  | MV:29515 | IR:290 | ADI:3 |  | Value |  |  | Views.Details.Occupancy Status | Occupancy Input Source | 1675 | 9 |  | Views.Details.OCC | OccSrc | 1709 | 22
Prop | Templates.HVAC Zone | Operational Occupancy | 1675 | 10 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Occ Effective | 345 | UnOccupied | [6 empty] | Occ Effective | 345 | [5 empty] | Occupancy Status | 345 | 0 = Occupied 1 = UnOccupied 2 = Bypass 3 = Standby |  | Attr | York RTU.HVAC Zone | 25 | Operational Occupancy | UCBapp.newUCB.Operational_Occupancy | Present Value | FALSE |  |  |  | MV:29517 | IR:292 | ADI:5 |  | Value |  |  | Views.Details.Occupancy Status | Operational Occupancy | 1675 | 10 |  | Views.Details.OCC | OprOcc | 1709 | 23
Prop | Templates.HVAC Zone | Occupancy Mode | 1675 | 161 | 7002 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | SE Occupancy Mode | 1728 | Enable | [6 empty] | SE Occupancy Mode | 1728 | [6 empty] | 1728 | 0 = Schedule 1 = External |  | Attr | York RTU.HVAC Zone | 25 | Occupancy Mode | UCBapp.newUCB.Occ_Sensor_Enable | Relinquish Default | FALSE |  |  |  | MV:29518 | HR:82 | ADI:6 |  | Value |  |  | Views.Commissioning.Standard | Occupancy Mode | 1675 | 161 |  | Views.Commission.Standard | OccMode | 1709 | 24
Prop | Templates.HVAC Zone | Occupancy Mode | 1675 | 161 | 7002 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | SE Occupancy Mode | 1728 | Enable | [6 empty] | SE Occupancy Mode | 1728 | [6 empty] | 1728 | 0 = Schedule 1 = External |  | Attr | York RTU.HVAC Zone | 25 | Occupancy Mode | UCBapp.newUCB.Occ_Sensor_Enable | Relinquish Default | FALSE |  |  |  | MV:29518 | HR:82 | ADI:6 |  | Value |  |  | Views.Details.Occupancy Status | Occupancy Mode | 1675 | 161 |  | Views.Details.OCC | OccMode | 1709 | 24
Prop | Templates.HVAC Zone | Occupancy Mode | 1675 | 161 | 7002 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | SE Occupancy Mode | 1728 | Enable | [6 empty] | SE Occupancy Mode | 1728 | [6 empty] | 1728 | 0 = Schedule 1 = External |  | Attr | York RTU.HVAC Zone | 25 | Occupancy Mode | UCBapp.newUCB.Occ_Sensor_Enable | Relinquish Default | FALSE |  |  |  | MV:29518 | HR:82 | ADI:6 |  | Value |  |  | Views.Clone.Partial Clone 1 | Occupancy Mode | 1675 | 161 |  |  | OccMode | 1709 | 24
Prop | Templates.HVAC Zone | Network Temporary Occupancy Request | 1675 | 12 | 7003 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | False/True | 1701 | Inactive | [6 empty] | False/True | 1701 | [5 empty] | Temporary Occupancy | 1701 | 0 = False 1 = True |  | Attr | York RTU.HVAC Zone | 25 | Network Temporary Occupancy Request | UCBapp.newUCB.Temp_Occ_EM | Present Value | FALSE |  |  |  | MV:29519 | HR:83 | ADI:7 |  | Value |  |  | Views.Controller.Network Inputs | Network Temporary Occupancy Request | 1675 | 12 |  | Views.Controller.NetworkInputs | NetTempOcc | 1709 | 25
Prop | Templates.HVAC Zone | Network Occupancy Request | 1675 | 13 | 7004 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Occ Sensor | 344 | Not_Set | [6 empty] | Occ Sensor | 344 | [6 empty] | 344 | 0 = Occupied 1 = UnOccupied 2 = Not Set |  | Attr | York RTU.HVAC Zone | 25 | Network Occupancy Request | UCBapp.newUCB.Network_Occupancy_Request | Relinquish Default | FALSE |  |  |  | MV:29520 | HR:84 | ADI:8 |  | Value |  |  | Views.Controller.Network Inputs | Network Occupancy Request | 1675 | 13 |  | Views.Controller.NetworkInputs | NetOcc | 1709 | 26
Prop | Templates.HVAC Zone | Temporary Occupancy Timeout | 1675 | 14 | 7005 | TRUE | TRUE | FALSE | 17 | SignedInteger | 1s | 6 | minutes | 507:72 | 7200 | 30 | 600 |  |  | 1s | 0 | minutes | 507:72 | 30 | 600 | [7 empty] | Attr | York RTU.HVAC Zone | 25 | Temporary Occupancy Timeout | UCBapp.newUCB.Temporary_Occupancy_Timeout | Relinquish Default | FALSE |  |  |  | AV:29521 | HR:85 | ADI:9 |  | Value |  |  | Views.Details.Occupancy Status | Temporary Occupancy Timeout | 1675 | 14 |  | Views.Details.OCC | TempOccTimeout | 1709 | 27
Prop | Templates.HVAC Zone | Operational Space Temperature | 1675 | 15 | 7006 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | 0 |  |  |  |  | 10ths | 0 | deg C | 507:62 | [5 empty] | Zone Temperature |  |  |  | Attr | York RTU.HVAC Zone | 25 | Operational Space Temperature | UCBapp.newUCB.Operational_Space_Temperature | Present Value | FALSE |  |  |  | AV:29522 | IR:135 | AI:31 |  | Value |  |  | Views.Summary.Sensors.Operational Mode | Operational Space Temperature | 1675 | 15 |  | Views.Summary.Sensors.OprMode | OprST | 1709 | 28
Prop | Templates.HVAC Zone | Operational Space Temperature | 1675 | 15 | 7006 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | 0 |  |  |  |  | 10ths | 0 | deg C | 507:62 | [5 empty] | Zone Temperature |  |  |  | Attr | York RTU.HVAC Zone | 25 | Operational Space Temperature | UCBapp.newUCB.Operational_Space_Temperature | Present Value | FALSE |  |  |  | AV:29522 | IR:135 | AI:31 |  | Value |  |  | Views.Details.Cooling.Service.Unit | Operational Space Temperature | 1675 | 15 |  | Views.Details.Clg.Service.Unit | OprST | 1709 | 28
Prop | Templates.HVAC Zone | Operational Space Temperature | 1675 | 15 | 7006 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | 0 |  |  |  |  | 10ths | 0 | deg C | 507:62 | [5 empty] | Zone Temperature |  |  |  | Attr | York RTU.HVAC Zone | 25 | Operational Space Temperature | UCBapp.newUCB.Operational_Space_Temperature | Present Value | FALSE |  |  |  | AV:29522 | IR:135 | AI:31 |  | Value |  |  | Views.Details.Heating.Service | Operational Space Temperature | 1675 | 15 |  | Views.Details.Htg.Service | OprST | 1709 | 28
Prop | Templates.HVAC Zone | Operational Space Temperature | 1675 | 15 | 7006 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | 0 |  |  |  |  | 10ths | 0 | deg C | 507:62 | [5 empty] | Zone Temperature |  |  |  | Attr | York RTU.HVAC Zone | 25 | Operational Space Temperature | UCBapp.newUCB.Operational_Space_Temperature | Present Value | FALSE |  |  |  | AV:29522 | IR:135 | AI:31 |  | Value |  |  | Views.Details.Heating.Proportional.Service | Operational Space Temperature | 1675 | 15 |  | Views.Details.Htg.Prop.Service | OprST | 1709 | 28
Prop | Templates.HVAC Zone | Operational Space Temperature | 1675 | 15 | 7006 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | 0 |  |  |  |  | 10ths | 0 | deg C | 507:62 | [5 empty] | Zone Temperature |  |  |  | Attr | York RTU.HVAC Zone | 25 | Operational Space Temperature | UCBapp.newUCB.Operational_Space_Temperature | Present Value | FALSE |  |  |  | AV:29522 | IR:135 | AI:31 |  | Value |  |  | Views.Details.FanVFD.Service | Operational Space Temperature | 1675 | 15 |  | Views.Details.FanVFD.Service | OprST | 1709 | 28
Prop | Templates.HVAC Zone | Operational Space Temperature | 1675 | 15 | 7006 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | 0 |  |  |  |  | 10ths | 0 | deg C | 507:62 | [5 empty] | Zone Temperature |  |  |  | Attr | York RTU.HVAC Zone | 25 | Operational Space Temperature | UCBapp.newUCB.Operational_Space_Temperature | Present Value | FALSE |  |  |  | AV:29522 | IR:135 | AI:31 |  | Value |  |  | Views.Details.Single Zone VAV.Service | Operational Space Temperature | 1675 | 15 |  | Views.Details.SZ VAV.Service | OprST | 1709 | 28
Prop | Templates.HVAC Zone | Operational Space Temperature | 1675 | 15 | 7006 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | 0 |  |  |  |  | 10ths | 0 | deg C | 507:62 | [5 empty] | Zone Temperature |  |  |  | Attr | York RTU.HVAC Zone | 25 | Operational Space Temperature | UCBapp.newUCB.Operational_Space_Temperature | Present Value | FALSE |  |  |  | AV:29522 | IR:135 | AI:31 |  | Value |  |  | Views.Details.Hot Gas Reheat.Service | Operational Space Temperature | 1675 | 15 |  | Views.Details.HGR.Service | OprST | 1709 | 28
Prop | Templates.HVAC Zone | Operational Space Temperature | 1675 | 15 | 7006 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | 0 |  |  |  |  | 10ths | 0 | deg C | 507:62 | [5 empty] | Zone Temperature |  |  |  | Attr | York RTU.HVAC Zone | 25 | Operational Space Temperature | UCBapp.newUCB.Operational_Space_Temperature | Present Value | FALSE |  |  |  | AV:29522 | IR:135 | AI:31 |  | Value |  |  | Views.Details.Mod Hot Gas Reheat.Service | Operational Space Temperature | 1675 | 15 |  | Views.Details.ModHGR.Service | OprST | 1709 | 28
Prop | Templates.HVAC Zone | Space Temperature Source | 1675 | 16 | 7007 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Effective Input Source | 1715 | Unreliable | [6 empty] | Effective Input Source | 1715 | [6 empty] | 1715 | 0 = Unreliable 1 = Return Air Temp 2 = Local Input 3 = Network Sensor ... |  | Attr | York RTU.HVAC Zone | 25 | Space Temperature Source | UCBapp.newUCB.Space_Temperature_Source | Present Value | TRUE |  |  |  | MV:29523 | IR:293 | ADI:10 |  | Value |  |  | Views.Summary.Sensors.Sensors | Space Temperature Source | 1675 | 16 |  | Views.Summary.Sensors.Sensors | STSrc | 1709 | 29
Prop | Templates.HVAC Zone | Space Temperature Alarm Setpoint Offset | 1675 | 162 | 7008 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | delta deg F | 507:120 | 5 | 0 | 25 |  |  | 1s | 0 | delta deg C | 507:359 | 0 | 14 | [7 empty] | Attr | York RTU.HVAC Zone | 25 | Space Temperature Alarm Setpoint Offset | UCBapp.newUCB.Space_Temp_Alarm_Temp | Relinquish Default | FALSE |  |  |  | AV:29524 | HR:274 | ADF:2 |  | Value |  |  | Views.Summary.Sensors.Sensors | Space Temperature Alarm Setpoint Offset | 1675 | 162 |  | Views.Summary.Sensors.Sensors | STAlarmOffset | 1709 | 30
Prop | Templates.HVAC Zone | Space Temperature Alarm Time Delay | 1675 | 163 | 7009 | TRUE | TRUE | FALSE | 17 | SignedInteger | 1s | 6 | minutes | 507:72 | 3600 | 0 | 120 |  |  | 1s | 0 | minutes | 507:72 | 0 | 120 | [7 empty] | Attr | York RTU.HVAC Zone | 25 | Space Temperature Alarm Time Delay | UCBapp.newUCB.Space_Temp_Alarm_Delay | Relinquish Default | FALSE |  |  |  | AV:29525 | HR:86 | ADI:11 |  | Value |  |  | Views.Summary.Sensors.Sensors | Space Temperature Alarm Time Delay | 1675 | 163 |  | Views.Summary.Sensors.Sensors | STAlarmDelay | 1709 | 31
Prop | Templates.HVAC Zone | Space Temperature Input | 1675 | 164 | 7010 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | 70 |  |  |  |  | 10ths | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.HVAC Zone | 25 | Space Temperature Input | UCBapp.newUCB.SPACE_T | Present Value | FALSE | [7 empty] | Value |  |  | Views.Summary.Sensors.Sensors | Space Temperature Input | 1675 | 164 |  | Views.Summary.Sensors.Sensors | ST | 1709 | 32
Prop | Templates.HVAC Zone | Network Override Space Temperature | 1675 | 18 | 7011 | TRUE | TRUE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | 70 | 0 | 100 |  |  | 10ths | 0 | deg C | 507:62 | 4 | 38 |  |  |  | Zone Temperature Destination |  |  |  | Attr | York RTU.HVAC Zone | 25 | Network Override Space Temperature | UCBapp.newUCB.Network_Override_Space_Temp | Present Value | FALSE |  |  |  | AV:29526 | HR:1 | ADF:3 |  | Value |  |  | Views.Controller.Network Inputs | Network Override Space Temperature | 1675 | 18 |  | Views.Controller.NetworkInputs | NetST | 1709 | 33
Prop | Templates.HVAC Zone | Network Override Space Temperature | 1675 | 18 | 7011 | TRUE | TRUE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | 70 | 0 | 100 |  |  | 10ths | 0 | deg C | 507:62 | 4 | 38 |  |  |  | Zone Temperature Destination |  |  |  | Attr | York RTU.HVAC Zone | 25 | Network Override Space Temperature | UCBapp.newUCB.Network_Override_Space_Temp | Present Value | FALSE |  |  |  | AV:29526 | HR:1 | ADF:3 |  | Value |  |  | Views.Clone.Network Override | Network Override Space Temperature | 1675 | 18 |  |  | NetST | 1709 | 33
Prop | Templates.HVAC Zone | Operational Indoor Air Quality | 1675 | 165 | 7012 | TRUE | FALSE | FALSE | 4 | Float | 10s | 7 | ppm | 507:96 | 0 |  |  |  |  | 10s | 0 | ppm | 507:96 | [5 empty] | CO2 |  |  |  | Attr | York RTU.HVAC Zone | 25 | Operational Indoor Air Quality | EconApp.Econ.Indoor Air Quality Src | Present Value | FALSE |  |  | York RTU.System Controllers.Econ Controller:Present Value <> Not Present | AV:29527 | IR:136 | ADF:4 |  | Value |  |  | Views.Summary.Sensors.Operational Mode | Operational Indoor Air Quality | 1675 | 165 |  | Views.Summary.Sensors.OprMode | OprIAQ | 1709 | 34
Prop | Templates.HVAC Zone | Operational Indoor Air Quality | 1675 | 165 | 7012 | TRUE | FALSE | FALSE | 4 | Float | 10s | 7 | ppm | 507:96 | 0 |  |  |  |  | 10s | 0 | ppm | 507:96 | [5 empty] | CO2 |  |  |  | Attr | York RTU.HVAC Zone | 25 | Operational Indoor Air Quality | EconApp.Econ.Indoor Air Quality Src | Present Value | FALSE |  |  | York RTU.System Controllers.Econ Controller:Present Value <> Not Present | AV:29527 | IR:136 | ADF:4 |  | Value |  |  | Views.Details.Economizer.Service | Operational Indoor Air Quality | 1675 | 165 |  | Views.Details.Econ.Service | OprIAQ | 1709 | 34
Prop | Templates.HVAC Zone | Operational Indoor Air Quality | 1675 | 165 | 7012 | TRUE | FALSE | FALSE | 4 | Float | 10s | 7 | ppm | 507:96 | 0 |  |  |  |  | 10s | 0 | ppm | 507:96 | [5 empty] | CO2 |  |  |  | Attr | York RTU.HVAC Zone | 25 | Operational Indoor Air Quality | EconApp.Econ.Indoor Air Quality Src | Present Value | FALSE |  |  | York RTU.System Controllers.Econ Controller:Present Value <> Not Present | AV:29527 | IR:136 | ADF:4 |  | Value |  |  | Views.Details.Demand Ventilation | Operational Indoor Air Quality | 1675 | 165 |  | Views.Details.DVent | OprIAQ | 1709 | 34
Prop | Templates.HVAC Zone | Indoor Air Quality Source | 1675 | 20 | 7013 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Effective Input Source 2 | 1732 | Unreliable | [6 empty] | Effective Input Source 2 | 1732 | [6 empty] | 1732 | 0 = Unreliable 1 = Local Input 2 = Network Sensor 3 = High Priority ... |  | Attr | York RTU.HVAC Zone | 25 | Indoor Air Quality Source | EconApp.Econ.Eff IA-Q State | Present Value | FALSE |  |  | York RTU.System Controllers.Econ Controller:Present Value <> Not Present | MV:29528 | IR:294 | ADI:12 |  | Value |  |  | Views.Summary.Sensors.Sensors | Indoor Air Quality Source | 1675 | 20 |  | Views.Summary.Sensors.Sensors | IAQSrc | 1709 | 35
Prop | Templates.HVAC Zone | Indoor Air Quality | 1675 | 19 | 7014 | TRUE | FALSE | FALSE | 4 | Float | 10s | 7 | ppm | 507:96 | N/A |  |  |  |  | 10s | 0 | ppm | 507:96 | [9 empty] | Attr | York RTU.HVAC Zone | 25 | Indoor Air Quality | EconApp.Econ.IAQ-CO2 | Present Value | FALSE |  |  | York RTU.System Controllers.Econ Controller:Present Value <> Not Present |  |  |  |  | Value |  |  | Views.Summary.Sensors.Sensors | Indoor Air Quality | 1675 | 19 |  | Views.Summary.Sensors.Sensors | IAQ | 1709 | 36
Prop | Templates.HVAC Zone | Indoor Air Quality Sensor Range | 1675 | 166 | 7015 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | ppm | 507:96 |  | 0 | 5000 |  |  | 1s | 0 | ppm | 507:96 | 0 | 5000 | [7 empty] | Attr | York RTU.HVAC Zone | 25 | Indoor Air Quality Sensor Range | 8-1/Econ.IAQ-CO2 | Output Range High | FALSE |  |  | York RTU.System Controllers.Econ Controller:Present Value <> Not Present | AV:29529 | HR:2 | ADF:5 |  | Value |  |  | Views.Details.Economizer.Setup | Indoor Air Quality Sensor Range | 1675 | 166 |  | Views.Details.Econ.Setup | IAQRange | 1709 | 37
Prop | Templates.HVAC Zone | Indoor Air Quality Sensor Range | 1675 | 166 | 7015 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | ppm | 507:96 |  | 0 | 5000 |  |  | 1s | 0 | ppm | 507:96 | 0 | 5000 | [7 empty] | Attr | York RTU.HVAC Zone | 25 | Indoor Air Quality Sensor Range | 8-1/Econ.IAQ-CO2 | Output Range High | FALSE |  |  | York RTU.System Controllers.Econ Controller:Present Value <> Not Present | AV:29529 | HR:2 | ADF:5 |  | Value |  |  | Views.Details.Demand Ventilation | Indoor Air Quality Sensor Range | 1675 | 166 |  | Views.Details.DVent | IAQRange | 1709 | 37
Prop | Templates.HVAC Zone | Indoor Air Quality Sensor Range | 1675 | 166 | 7015 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | ppm | 507:96 |  | 0 | 5000 |  |  | 1s | 0 | ppm | 507:96 | 0 | 5000 | [7 empty] | Attr | York RTU.HVAC Zone | 25 | Indoor Air Quality Sensor Range | 8-1/Econ.IAQ-CO2 | Output Range High | FALSE |  |  | York RTU.System Controllers.Econ Controller:Present Value <> Not Present | AV:29529 | HR:2 | ADF:5 |  | Value |  |  | Views.Clone.Partial Clone 1 | Indoor Air Quality Sensor Range | 1675 | 166 |  |  | IAQRange | 1709 | 37
Prop | Templates.HVAC Zone | Network Override Indoor Air Quality | 1675 | 22 | 7016 | TRUE | TRUE | FALSE | 4 | Float | 10s | 7 | ppm | 507:96 | 0 | 0 | 5000 |  |  | 10s | 0 | ppm | 507:96 | 0 | 5000 |  |  |  | CO2 Destination |  |  |  | Attr | York RTU.HVAC Zone | 25 | Network Override Indoor Air Quality | EconApp.Econ.IAQ Timed Override | Present Value | FALSE |  |  | York RTU.System Controllers.Econ Controller:Present Value <> Not Present | AV:29530 | HR:3 | ADF:6 |  | Value |  |  | Views.Controller.Network Inputs | Network Override Indoor Air Quality | 1675 | 22 |  | Views.Controller.NetworkInputs | NetIAQ | 1709 | 38
Prop | Templates.HVAC Zone | Network Override Indoor Air Quality | 1675 | 22 | 7016 | TRUE | TRUE | FALSE | 4 | Float | 10s | 7 | ppm | 507:96 | 0 | 0 | 5000 |  |  | 10s | 0 | ppm | 507:96 | 0 | 5000 |  |  |  | CO2 Destination |  |  |  | Attr | York RTU.HVAC Zone | 25 | Network Override Indoor Air Quality | EconApp.Econ.IAQ Timed Override | Present Value | FALSE |  |  | York RTU.System Controllers.Econ Controller:Present Value <> Not Present | AV:29530 | HR:3 | ADF:6 |  | Value |  |  | Views.Clone.Network Override | Network Override Indoor Air Quality | 1675 | 22 |  |  | NetIAQ | 1709 | 38
Prop | Templates.HVAC Zone | Operational Space Humidity | 1675 | 23 | 7017 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | %RH | 507:29 | 50 |  |  |  |  | 10ths | 0 | %RH | 507:29 | [5 empty] | Indoor Humidity |  |  |  | Attr | York RTU.HVAC Zone | 25 | Operational Space Humidity | UCBapp.newUCB.Operational_Space_Humidity | Present Value | FALSE |  |  |  | AV:29531 | IR:137 | AI:32 |  | Value |  |  | Views.Summary.Sensors.Operational Mode | Operational Space Humidity | 1675 | 23 |  | Views.Summary.Sensors.OprMode | OprSH | 1709 | 39
Prop | Templates.HVAC Zone | Operational Space Humidity | 1675 | 23 | 7017 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | %RH | 507:29 | 50 |  |  |  |  | 10ths | 0 | %RH | 507:29 | [5 empty] | Indoor Humidity |  |  |  | Attr | York RTU.HVAC Zone | 25 | Operational Space Humidity | UCBapp.newUCB.Operational_Space_Humidity | Present Value | FALSE |  |  |  | AV:29531 | IR:137 | AI:32 |  | Value |  |  | Views.Details.Cooling.Misc | Operational Space Humidity | 1675 | 23 |  | Views.Details.Clg.Misc | OprSH | 1709 | 39
Prop | Templates.HVAC Zone | Operational Space Humidity | 1675 | 23 | 7017 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | %RH | 507:29 | 50 |  |  |  |  | 10ths | 0 | %RH | 507:29 | [5 empty] | Indoor Humidity |  |  |  | Attr | York RTU.HVAC Zone | 25 | Operational Space Humidity | UCBapp.newUCB.Operational_Space_Humidity | Present Value | FALSE |  |  |  | AV:29531 | IR:137 | AI:32 |  | Value |  |  | Views.Details.Hot Gas Reheat.Service | Operational Space Humidity | 1675 | 23 |  | Views.Details.HGR.Service | OprSH | 1709 | 39
Prop | Templates.HVAC Zone | Operational Space Humidity | 1675 | 23 | 7017 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | %RH | 507:29 | 50 |  |  |  |  | 10ths | 0 | %RH | 507:29 | [5 empty] | Indoor Humidity |  |  |  | Attr | York RTU.HVAC Zone | 25 | Operational Space Humidity | UCBapp.newUCB.Operational_Space_Humidity | Present Value | FALSE |  |  |  | AV:29531 | IR:137 | AI:32 |  | Value |  |  | Views.Details.Mod Hot Gas Reheat.Service | Operational Space Humidity | 1675 | 23 |  | Views.Details.ModHGR.Service | OprSH | 1709 | 39
Prop | Templates.HVAC Zone | Space Humidity Source | 1675 | 24 | 7018 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Effective Input Source 2 | 1732 | Unreliable | [6 empty] | Effective Input Source 2 | 1732 | [6 empty] | 1732 | 0 = Unreliable 1 = Local Input 2 = Network Sensor 3 = High Priority ... |  | Attr | York RTU.HVAC Zone | 25 | Space Humidity Source | UCBapp.newUCB.Space_Humidity_Source | Present Value | FALSE |  |  |  | MV:29532 | IR:295 | ADI:13 |  | Value |  |  | Views.Summary.Sensors.Sensors | Space Humidity Source | 1675 | 24 |  | Views.Summary.Sensors.Sensors | SHSrc | 1709 | 40
Prop | Templates.HVAC Zone | Space Humidity RAH Input | 1675 | 25 | 7019 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | %RH | 507:29 | N/A |  |  |  |  | 10ths | 0 | %RH | 507:29 | [9 empty] | Attr | York RTU.HVAC Zone | 25 | Space Humidity RAH Input | UCBapp.newUCB.IA_H | Present Value | FALSE |  |  |  | AV:29828 | IR:138 | AI:1 |  | Value |  |  | Views.Summary.Sensors.Sensors | Space Humidity RAH Input | 1675 | 25 |  | Views.Summary.Sensors.Sensors | RAH | 1709 | 41
Prop | Templates.HVAC Zone | Space Humidity RAH Input | 1675 | 25 | 7019 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | %RH | 507:29 | N/A |  |  |  |  | 10ths | 0 | %RH | 507:29 | [9 empty] | Attr | York RTU.HVAC Zone | 25 | Space Humidity RAH Input | UCBapp.newUCB.IA_H | Present Value | FALSE |  |  |  | AV:29828 | IR:138 | AI:1 |  | Value |  |  | Views.Details.Hot Gas Reheat.Service | Space Humidity RAH Input | 1675 | 25 |  | Views.Details.HGR.Service | RAH | 1709 | 41
Prop | Templates.HVAC Zone | Space Humidity RAH Input | 1675 | 25 | 7019 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | %RH | 507:29 | N/A |  |  |  |  | 10ths | 0 | %RH | 507:29 | [9 empty] | Attr | York RTU.HVAC Zone | 25 | Space Humidity RAH Input | UCBapp.newUCB.IA_H | Present Value | FALSE |  |  |  | AV:29828 | IR:138 | AI:1 |  | Value |  |  | Views.Details.Mod Hot Gas Reheat.Service | Space Humidity RAH Input | 1675 | 25 |  | Views.Details.ModHGR.Service | RAH | 1709 | 41
Prop | Templates.HVAC Zone | Network Override Zone Humidity | 1675 | 26 | 7020 | TRUE | TRUE | FALSE | 4 | Float | 10ths | 5 | %RH | 507:29 | 50 | 0 | 100 |  |  | 10ths | 0 | %RH | 507:29 | 0 | 100 |  |  |  | Indoor Humidity Destination |  |  |  | Attr | York RTU.HVAC Zone | 25 | Network Override Zone Humidity | UCBapp.newUCB.Network_Override_Zone_Humidity | Present Value | FALSE |  |  |  | AV:29533 | HR:4 | ADF:8 |  | Value |  |  | Views.Controller.Network Inputs | Network Override Zone Humidity | 1675 | 26 |  | Views.Controller.NetworkInputs | NetSH | 1709 | 42
Prop | Templates.HVAC Zone | Network Override Zone Humidity | 1675 | 26 | 7020 | TRUE | TRUE | FALSE | 4 | Float | 10ths | 5 | %RH | 507:29 | 50 | 0 | 100 |  |  | 10ths | 0 | %RH | 507:29 | 0 | 100 |  |  |  | Indoor Humidity Destination |  |  |  | Attr | York RTU.HVAC Zone | 25 | Network Override Zone Humidity | UCBapp.newUCB.Network_Override_Zone_Humidity | Present Value | FALSE |  |  |  | AV:29533 | HR:4 | ADF:8 |  | Value |  |  | Views.Clone.Network Override | Network Override Zone Humidity | 1675 | 26 |  |  | NetSH | 1709 | 42
Prop | Templates.HVAC Zone | Operating Fan Request | 1675 | 27 | 7021 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | Off | [6 empty] | Off/On | 647 | [6 empty] | 647 | 0 = Off 1 = On |  | Attr | York RTU.HVAC Zone | 25 | Operating Fan Request | UCBapp.newUCB.Operating_Fan_Request | Present Value | FALSE |  |  |  | MV:29534 | IR:296 | ADI:14 |  | Value |  |  | Views.Details.Indoor Fan.Service | Operating Fan Request | 1675 | 27 |  | Views.Details.Fan.Service | OprFanReq | 1709 | 43
Prop | Templates.HVAC Zone | Fan Request Source | 1675 | 28 | 7022 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Effective Input Source 2 | 1732 | Unreliable | [6 empty] | Effective Input Source 2 | 1732 | [6 empty] | 1732 | 0 = Unreliable 1 = Local Input 2 = Network Sensor 3 = High Priority ... |  | Attr | York RTU.HVAC Zone | 25 | Fan Request Source | UCBapp.newUCB.Fan_Request_Source | Present Value | FALSE |  |  |  | MV:29535 | IR:297 | ADI:15 |  | Value |  |  | Views.Details.Indoor Fan.Service | Fan Request Source | 1675 | 28 |  | Views.Details.Fan.Service | FanReqSrc | 1709 | 44
Prop | Templates.HVAC Zone | Network Override Fan Request | 1675 | 29 | 7023 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Off/On | 647 | Off | [6 empty] | Off/On | 647 | [6 empty] | 647 | 0 = Off 1 = On |  | Attr | York RTU.HVAC Zone | 25 | Network Override Fan Request | UCBapp.newUCB.CCS_Fan_Request | Present Value | FALSE |  |  |  | MV:29536 | HR:87 | ADI:16 |  | Value |  |  | Views.Controller.Network Inputs | Network Override Fan Request | 1675 | 29 |  | Views.Controller.NetworkInputs | NetFanReq | 1709 | 45
Prop | Templates.HVAC Zone | Network Override Fan Request | 1675 | 29 | 7023 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Off/On | 647 | Off | [6 empty] | Off/On | 647 | [6 empty] | 647 | 0 = Off 1 = On |  | Attr | York RTU.HVAC Zone | 25 | Network Override Fan Request | UCBapp.newUCB.CCS_Fan_Request | Present Value | FALSE |  |  |  | MV:29536 | HR:87 | ADI:16 |  | Value |  |  | Views.Clone.Network Override | Network Override Fan Request | 1675 | 29 |  |  | NetFanReq | 1709 | 45
Prop | Templates.HVAC Zone | Operational Space Temperature Setpoint Offset | 1675 | 30 | 7024 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | delta deg F | 507:120 | 0 |  |  |  |  | 10ths | 0 | delta deg C | 507:359 | [5 empty] | Warmer Cooler Adjust |  |  |  | Attr | York RTU.HVAC Zone | 25 | Operational Space Temperature Setpoint Offset | UCBapp.newUCB.Op_Space_Temp_SP_Offset | Present Value | FALSE |  |  |  | AV:29537 | IR:140 | ADF:9 |  | Value |  |  | Views.Summary.Sensors.Operational Mode | Operational Space Temperature Setpoint Offset | 1675 | 30 |  | Views.Summary.Sensors.OprMode | OprSSO | 1709 | 46
Prop | Templates.HVAC Zone | Space Temperature Setpoint Offset Source | 1675 | 31 | 7025 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Effective Input Source 2 | 1732 | Unreliable | [6 empty] | Effective Input Source 2 | 1732 | [6 empty] | 1732 | 0 = Unreliable 1 = Local Input 2 = Network Sensor 3 = High Priority ... |  | Attr | York RTU.HVAC Zone | 25 | Space Temperature Setpoint Offset Source | UCBapp.newUCB.Space_Temp_SP_Offset_Source | Present Value | FALSE |  |  |  | MV:29538 | IR:298 | ADI:17 |  | Value |  |  | Views.Summary.Sensors.Sensors | Space Temperature Setpoint Offset Source | 1675 | 31 |  | Views.Summary.Sensors.Sensors | SSOSrc | 1709 | 47
Prop | Templates.HVAC Zone | Space Temp Setpoint Offset Input | 1675 | 32 | 7026 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | delta deg F | 507:120 | N/A |  |  |  |  | 10ths | 0 | delta deg C | 507:359 | [9 empty] | Attr | York RTU.HVAC Zone | 25 | Space Temp Setpoint Offset Input | UCBapp.newUCB.SPACEO_T | Present Value | FALSE |  |  |  | AV:29539 | IR:141 | ADF:10 |  | Value |  |  | Views.Summary.Sensors.Sensors | Space Temp Setpoint Offset Input | 1675 | 32 |  | Views.Summary.Sensors.Sensors | SSO | 1709 | 48
Prop | Templates.HVAC Zone | Network Override Space Setpoint Offset | 1675 | 33 | 7027 | TRUE | TRUE | FALSE | 4 | Float | 10ths | 5 | delta deg F | 507:120 | 0 | -5 | 5 |  |  | 10ths | 0 | delta deg C | 507:359 | -3 | 3 | [7 empty] | Attr | York RTU.HVAC Zone | 25 | Network Override Space Setpoint Offset | UCBapp.newUCB.Network_Override_Space_SP_Offset | Present Value | FALSE |  |  |  | AV:29540 | HR:5 | ADF:11 |  | Value |  |  | Views.Controller.Network Inputs | Network Override Space Setpoint Offset | 1675 | 33 |  | Views.Controller.NetworkInputs | NetSSO | 1709 | 49
Prop | Templates.HVAC Zone | Network Override Space Setpoint Offset | 1675 | 33 | 7027 | TRUE | TRUE | FALSE | 4 | Float | 10ths | 5 | delta deg F | 507:120 | 0 | -5 | 5 |  |  | 10ths | 0 | delta deg C | 507:359 | -3 | 3 | [7 empty] | Attr | York RTU.HVAC Zone | 25 | Network Override Space Setpoint Offset | UCBapp.newUCB.Network_Override_Space_SP_Offset | Present Value | FALSE |  |  |  | AV:29540 | HR:5 | ADF:11 |  | Value |  |  | Views.Clone.Network Override | Network Override Space Setpoint Offset | 1675 | 33 |  |  | NetSSO | 1709 | 49
Prop | Templates.HVAC Zone | Space Temperature Setpoint Offset Range | 1675 | 34 | 7028 | TRUE | TRUE | FALSE | 4 | Float | 10ths | 5 | delta deg F | 507:120 | 3 | 0 | 5 |  |  | 10ths | 0 | delta deg C | 507:359 | 0 | 3 | [7 empty] | Attr | York RTU.HVAC Zone | 25 | Space Temperature Setpoint Offset Range | UCBapp.newUCB.Space_Temp_SP_Offset_Range | Relinquish Default | FALSE |  |  |  | AV:30094 | HR:871 | ADF:205 |  | Value |  |  | Views.Summary.Sensors.Sensors | Space Temperature Setpoint Offset Range | 1675 | 34 |  | Views.Summary.Sensors.Sensors | SSORange | 1709 | 50
Prop | Templates.HVAC Zone | Space Temperature Setpoint Offset Range | 1675 | 34 | 7028 | TRUE | TRUE | FALSE | 4 | Float | 10ths | 5 | delta deg F | 507:120 | 3 | 0 | 5 |  |  | 10ths | 0 | delta deg C | 507:359 | 0 | 3 | [7 empty] | Attr | York RTU.HVAC Zone | 25 | Space Temperature Setpoint Offset Range | UCBapp.newUCB.Space_Temp_SP_Offset_Range | Relinquish Default | FALSE |  |  |  | AV:30094 | HR:871 | ADF:205 |  | Value |  |  | Views.Clone.Partial Clone 1 | Space Temperature Setpoint Offset Range | 1675 | 34 |  |  | SSORange | 1709 | 50
Prop | Templates.HVAC Zone | Number of Network Sensors Online | 1675 | 35 | 7029 | TRUE | FALSE | FALSE | 17 | SignedInteger | 1s | 6 |  | 507:95 | 0 |  |  |  |  | 1s | 0 |  | 507:95 | [9 empty] | Attr | York RTU.HVAC Zone | 25 | Number of Network Sensors Online | UCBapp.newUCB.NSPNP_NUM_SENSORS | Present Value | FALSE | [7 empty] | Value |  |  | Views.Controller.Network | Number of Network Sensors Online | 1675 | 35 |  | Views.Controller.Network | #NetSensors | 1709 | 51
Prop | Templates.HVAC Zone | Occupancy Input | 1675 | 291 | 7030 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | SE RTU Unocc/Occ | 1658 | Occupied | [6 empty] | SE RTU Unocc/Occ | 1658 | [6 empty] | 1658 | 0 = Occupied 1 = Unoccupied |  | Attr | York RTU.HVAC Zone | 25 | Occupancy Input | UCBapp.newUCB.OCC_S | Present Value | FALSE |  |  |  | MV:29516 | IR:291 | BI:9 |  | Value |  |  | Views.Details.Occupancy Status | Occupancy Input | 1675 | 291 |  | Views.Details.OCC | OCC | 1709 | 380
Prop | Templates.HVAC Zone | Space Temperature Sensor Fault | 1675 | 299 | 7031 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.HVAC Zone | 25 | Space Temperature Sensor Fault | UCBapp.newUCB.Space_Temp_Sensor_Fault | Present Value | FALSE
Prop | Templates.HVAC Zone | Space Temperature Setpoint Offset Fault | 1675 | 300 | 7032 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.HVAC Zone | 25 | Space Temperature Setpoint Offset Fault | UCBapp.newUCB.Space_Temp_SP_Offset_Fault | Present Value | FALSE
Prop | Templates.HVAC Zone | Indoor Air Quality Sensor Fault | 1675 | 301 | 7033 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | No | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.HVAC Zone | 25 | Indoor Air Quality Sensor Fault | EconApp.Econ.IA-Q Alarm | Present Value | FALSE
Prop | Templates.HVAC Zone | Space Humidity Sensor Fault | 1675 | 302 | 7034 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.HVAC Zone | 25 | Space Humidity Sensor Fault | UCBapp.newUCB.Space_Humidity_Sensor_Fault | Present Value | FALSE
Prop | Templates.HVAC Zone | Netsensor Battery Fault | 1675 | 323 | 7035 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.HVAC Zone | 25 | Netsensor Battery Fault | UCBapp.newUCB.NSPNP_LOW_BATT | Present Value | FALSE
Prop | Templates.HVAC Zone | Netsensor Signal Strength Fault | 1675 | 324 | 7036 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.HVAC Zone | 25 | Netsensor Signal Strength Fault | UCBapp.newUCB.NSPNP_SIG_STRENGTH | Present Value | FALSE
Prop | Templates.HVAC Zone | Scheduled Occupancy | 1675 | 325 | 7037 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | SE RTU Unocc/Occ | 1658 | Unoccupied | [6 empty] | SE RTU Unocc/Occ | 1658 | [5 empty] | Scheduled Occupancy | 1658 | 0 = Occupied 1 = Unoccupied |  | Attr | York RTU.HVAC Zone | 25 | Scheduled Occupancy | UCBapp.newUCB.OCC_SCHEDULE | Relinquish Default | FALSE
Prop | Templates.HVAC Zone | Return Air Temperature | 1675 | 65 | 7038 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | N/A |  |  |  |  | 10ths | 0 | deg C | 507:62 | [5 empty] | Return Air Temperature |  |  |  | Attr | York RTU.HVAC Zone | 25 | Return Air Temperature | UCBapp.newUCB.RA_T | Present Value | FALSE |  |  |  | AV:29764 | IR:139 | AI:2 |  | Value |  |  | Views.Summary.Sensors.Sensors | Return Air Temperature | 1675 | 65 |  | Views.Summary.Sensors.Sensors | RAT | 1709 | 297
Prop | Templates.HVAC Zone | Return Air Temperature | 1675 | 65 | 7038 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | N/A |  |  |  |  | 10ths | 0 | deg C | 507:62 | [5 empty] | Return Air Temperature |  |  |  | Attr | York RTU.HVAC Zone | 25 | Return Air Temperature | UCBapp.newUCB.RA_T | Present Value | FALSE |  |  |  | AV:29764 | IR:139 | AI:2 |  | Value |  |  | Views.Details.Cooling.Service.Unit | Return Air Temperature | 1675 | 65 |  | Views.Details.Clg.Service.Unit | RAT | 1709 | 297
Prop | Templates.HVAC Zone | Return Air Temperature | 1675 | 65 | 7038 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | N/A |  |  |  |  | 10ths | 0 | deg C | 507:62 | [5 empty] | Return Air Temperature |  |  |  | Attr | York RTU.HVAC Zone | 25 | Return Air Temperature | UCBapp.newUCB.RA_T | Present Value | FALSE |  |  |  | AV:29764 | IR:139 | AI:2 |  | Value |  |  | Views.Details.Heating.Service | Return Air Temperature | 1675 | 65 |  | Views.Details.Htg.Service | RAT | 1709 | 297
Prop | Templates.HVAC Zone | Return Air Temperature | 1675 | 65 | 7038 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | N/A |  |  |  |  | 10ths | 0 | deg C | 507:62 | [5 empty] | Return Air Temperature |  |  |  | Attr | York RTU.HVAC Zone | 25 | Return Air Temperature | UCBapp.newUCB.RA_T | Present Value | FALSE |  |  |  | AV:29764 | IR:139 | AI:2 |  | Value |  |  | Views.Commissioning.Quick Start | Return Air Temperature | 1675 | 65 |  | Views.Commission.Quick Start | RAT | 1709 | 297
Prop | Templates.HVAC Zone | Return Air Temperature Sensor Fault | 1675 | 312 | 7039 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.HVAC Zone | 25 | Return Air Temperature Sensor Fault | UCBapp.newUCB.RA_Temperature_Sensor_Fault | Present Value | FALSE
Prop | Templates.HVAC Zone | Temporary Occupancy Input | 1675 | 329 | 7040 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Disable/Enable | 658 | Disable | [6 empty] | Disable/Enable | 658 | [6 empty] | 658 | 0 = Disable 1 = Enable |  | Attr | York RTU.HVAC Zone | 25 | Temporary Occupancy Input | UCBapp.newUCB.Temporary_Occupancy_Input | Relinquish Default | FALSE |  |  |  | MV:29825 | HR:81 | ADI:4 |  | Value |  |  | Views.Details.Occupancy Status | Temporary Occupancy Input | 1675 | 329 |  | Views.Details.OCC | TempOCC | 1709 | 448
Prop | Templates.HVAC Zone | Space Temperature Cooling Alarm | 1675 | 330 | 7041 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.HVAC Zone | 25 | Space Temperature Cooling Alarm | UCBapp.newUCB.Space_Temp_Cooling_Alarm | Present Value | FALSE
Prop | Templates.HVAC Zone | Space Temperature Heating Alarm | 1675 | 359 | 7042 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.HVAC Zone | 25 | Space Temperature Heating Alarm | UCBapp.newUCB.Space_Temp_Heating_Alarm | Present Value | FALSE
Prop | Templates.HVAC Zone | Load Shed Active | 1675 | 421 | 7043 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Disable | [6 empty] | No/Yes | 854 | [5 empty] | Load Shed Command | 854 | 0 = No 1 = Yes |  | Attr | York RTU.HVAC Zone | 25 | Load Shed Active | UCBapp.newUCB.Loadshed_Setpoints_Enable | Relinquish Default | FALSE |  |  |  | MV:29883 | HR:127 | ADI:110 |  | Value |  |  | Views.Details.Load Shed | Load Shed Active | 1675 | 421 |  | Views.Details.T24LoadShed | LoadShedEnable | 1709 | 528
Prop | Templates.HVAC Zone | Load Shed Rate Limit | 1675 | 422 | 7044 | TRUE | TRUE | FALSE | 4 | Float | 1000ths | 3 | deg F/min | 507:94 | 0.066 | 0 | 1 |  |  | 1000ths | 0 | deg C/min | 507:92 | 0 | 1 | [7 empty] | Attr | York RTU.HVAC Zone | 25 | Load Shed Rate Limit | UCBapp.newUCB.Load_Shed_Rate_Limit | Relinquish Default | FALSE |  |  |  | AV:29884 | HR:71 | ADF:157 |  | Value |  |  | Views.Details.Load Shed | Load Shed Rate Limit | 1675 | 422 |  | Views.Details.T24LoadShed | LoadShedRateLim | 1709 | 529
Prop | Templates.HVAC Zone | Load Shed Adjust | 1675 | 423 | 7045 | TRUE | TRUE | FALSE | 4 | Float | 10ths | 5 | delta deg F | 507:120 | 4 | 0 | 8 |  |  | 10ths | 0 | delta deg C | 507:359 | 0 | 4.4 | [7 empty] | Attr | York RTU.HVAC Zone | 25 | Load Shed Adjust | UCBapp.newUCB.Load_Shed_Adjust | Relinquish Default | FALSE |  |  |  | AV:29885 | HR:72 | ADF:158 |  | Value |  |  | Views.Details.Load Shed | Load Shed Adjust | 1675 | 423 |  | Views.Details.T24LoadShed | LoadShedAdjust | 1709 | 530
Prop | Templates.HVAC Zone | Time to Next Occupancy Period | 1675 | 425 | 7046 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | minutes | 507:72 | 65000 |  |  |  |  | 10ths | 0 | minutes | 507:72 | [9 empty] | Attr | York RTU.HVAC Zone | 25 | Time to Next Occupancy Period | UCBapp.newUCB.TIME_TO_NEXT_EVENT | Present Value | FALSE |  |  | York RTU.HVAC Zone.Occupancy Input Source:Present Value = Local Schedule | AV:29837 | IR:142 | ADF:12
Prop | Templates.HVAC Zone | Operating Mode | 1675 | 426 | 7047 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | OST Warmup Cooldown | 366 | Normal | [6 empty] | OST Warmup Cooldown | 366 | [6 empty] | 366 | 0 = Normal 1 = Warmup 2 = Cooldown 3 = Coast |  | Attr | York RTU.HVAC Zone | 25 | Operating Mode | UCBapp.newUCB.Optimal_Start_Mode | Present Value | FALSE |  |  | York RTU.HVAC Zone.Occupancy Input Source:Present Value = Local Schedule | MV:29838 | IR:299 | ADI:18
Prop | Templates.HVAC Zone | RAT Instead of Space-T | 1675 | 456 | 7058 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Normal | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.HVAC Zone | 25 | RAT Instead of Space-T | UCBapp.newUCB.RAT_Instead_of_Space_T | Present Value | FALSE
Prop | Templates.HVAC Zone | Off During Unoccupied | 1675 | 501 | 7059 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | FALSE | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.HVAC Zone | 25 | Off During Unoccupied | UCBapp.newUCB.Off_During_Unoccupied | Relinquish Default | FALSE |  |  |  | MV:29914 | HR:88 | ADI:19 |  | Value |  |  | Views.Details.Occupancy Status | Off During Unoccupied | 1675 | 501 |  | Views.Details.OCC | OffDurUnocc | 1709 | 633
Prop | Templates.HVAC Zone | Off During Unoccupied | 1675 | 501 | 7059 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | FALSE | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.HVAC Zone | 25 | Off During Unoccupied | UCBapp.newUCB.Off_During_Unoccupied | Relinquish Default | FALSE |  |  |  | MV:29914 | HR:88 | ADI:19 |  | Value |  |  | Views.Clone.Partial Clone 1 | Off During Unoccupied | 1675 | 501 |  |  | OffDurUnocc | 1709 | 633
Prop | Templates.HVAC Zone | Direct Loadshed | 1675 | 497 | 7061 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Stop | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.HVAC Zone | 25 | Direct Loadshed | UCBapp.newUCB.Loadshed | Relinquish Default | FALSE |  |  |  | MV:29910 | HR:128 | ADI:111 |  | Value |  |  | Views.Controller.Network Inputs | Direct Loadshed | 1675 | 497 |  | Views.Controller.NetworkInputs | DirLoadshd | 1709 | 629
Prop | Templates.HVAC Zone | Redline | 1675 | 500 | 7062 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Stop | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.HVAC Zone | 25 | Redline | UCBapp.newUCB.Redline | Relinquish Default | FALSE |  |  |  | MV:29911 | HR:129 | ADI:112 |  | Value |  |  | Views.Controller.Network Inputs | Redline | 1675 | 500 |  | Views.Controller.NetworkInputs | Redline | 1709 | 632
Prop | Templates.HVAC Zone | PID Tuning Reset | 1675 | 631 | 7063 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | False/True | 1701 | No | [6 empty] | False/True | 1701 | [6 empty] | 1701 | 0 = False 1 = True |  | Attr | York RTU.HVAC Zone | 25 | PID Tuning Reset | UCBapp.newUCB.PID_Tuning_Reset | Present Value | FALSE |  |  |  | MV:29919 | HR:130 | ADI:113 |  | Value |  |  | Views.Commissioning.Options | PID Tuning Reset | 1675 | 631 |  | Views.Commission.Options | PIDTunRst | 1709 | 651
Prop | Templates.HVAC Zone | Adaptive Tuning Enable | 1675 | 632 | 7064 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Disable/Enable | 658 | Disable | [6 empty] | Disable/Enable | 658 | [6 empty] | 658 | 0 = Disable 1 = Enable |  | Attr | York RTU.HVAC Zone | 25 | Adaptive Tuning Enable | UCBapp.newUCB.Cooling_Adaptive_Tuning_En | Present Value | FALSE
Prop | Templates.HVAC Zone | Pre Occupancy Purge Enable | 1675 | 1455 | 7065 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Disable/Enable | 658 | Disable | [6 empty] | Disable/Enable | 658 | [6 empty] | 658 | 0 = Disable 1 = Enable |  | Attr | York RTU.HVAC Zone | 25 | Pre Occupancy Purge Enable | UCBapp.newUCB.Pre_Occ_Purge_Enable | Relinquish Default | FALSE | [7 empty] | Value |  |  | Views.Details.Occupancy Status | Pre Occupancy Purge Enable | 1675 | 1455 |  | Views.Details.OCC | PreOccPurgeEna | 1709 | 696
Prop | Templates.HVAC Zone | Pre Occupancy Purge Time | 1675 | 1458 | 7066 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | minutes | 507:72 | 60 | 1 | 120 |  |  | 1s | 0 | minutes | 507:72 | 1 | 120 | [7 empty] | Attr | York RTU.HVAC Zone | 25 | Pre Occupancy Purge Time | UCBapp.newUCB.Pre_Occ_Purge_Time | Relinquish Default | FALSE | [7 empty] | Value |  |  | Views.Details.Occupancy Status | Pre Occupancy Purge Time | 1675 | 1458 |  | Views.Details.OCC | PreOccPurgeTime | 1709 | 698
Prop | Templates.HVAC Zone | Pre Occupancy Purge Upper SAT Setpoint | 1675 | 1459 | 7067 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 90 | 80 | 100 |  |  | 1s | 0 | deg C | 507:62 | 26 | 38 | [7 empty] | Attr | York RTU.HVAC Zone | 25 | Pre Occupancy Purge Upper SAT Setpoint | UCBapp.newUCB.Pre_Occ_Purge_Upper_SAT_SP | Relinquish Default | FALSE | [7 empty] | Value |  |  | Views.Details.Occupancy Status | Pre Occupancy Purge Upper SAT Setpoint | 1675 | 1459 |  | Views.Details.OCC | PreOccUpSAT_SP | 1709 | 699
Prop | Templates.HVAC Zone | Pre Occupancy Purge Lower SAT Setpoint | 1675 | 1460 | 7068 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 45 | 35 | 55 |  |  | 1s | 0 | deg C | 507:62 | 1 | 13 | [7 empty] | Attr | York RTU.HVAC Zone | 25 | Pre Occupancy Purge Lower SAT Setpoint | UCBapp.newUCB.Pre_Occ_Purge_Lower_SAT_SP | Relinquish Default | FALSE | [7 empty] | Value |  |  | Views.Details.Occupancy Status | Pre Occupancy Purge Lower SAT Setpoint | 1675 | 1460 |  | Views.Details.OCC | PreOccLowSAT_SP | 1709 | 700
Prop | Templates.HVAC Zone | Unreliable Sensor Text | 1675 | 1521 | 7069 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | No | [6 empty] | No/Yes | 854 | [5 empty] | Warmer Cooler Adjust Enable | 854 | 0 = No 1 = Yes |  | Attr | York RTU.HVAC Zone | 25 | Unreliable Sensor Text | UCBapp.newUCB.EFF_SPT_OFFSET_REL | Present Value | FALSE
Prop | Templates.HVAC Zone | No Reliable Zone Temp Alarm | 1675 | 1596 | 7070 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.HVAC Zone | 25 | No Reliable Zone Temp Alarm | UCBapp.newUCB.No_Reliable_Zone_Temp_Alarm | Present Value | FALSE | [6 empty] | No_Reliable_Zone_Temp_Alarm
Prop | Templates.HVAC Zone | Network Occupancy Timeout Enable | 1675 | 1597 | 7071 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Disable/Enable | 658 | Disable | [6 empty] | Disable/Enable | 658 | [6 empty] | 658 | 0 = Disable 1 = Enable |  | Attr | York RTU.HVAC Zone | 25 | Network Occupancy Timeout Enable | UCBapp.newUCB.Network_Occ_Timeout_Enable | Relinquish Default | FALSE | [6 empty] | Network_Occ_Timeout_Enable
Prop | Templates.HVAC Zone | Network Occupancy Timeout Time | 1675 | 1598 | 7072 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | minutes | 507:72 | 15 | 5 | 60 |  |  | 1s | 0 | minutes | 507:72 | 5 | 60 | [7 empty] | Attr | York RTU.HVAC Zone | 25 | Network Occupancy Timeout Time | UCBapp.newUCB.Network_Occ_Timeout_Time | Relinquish Default | FALSE | [6 empty] | Network_Occ_Timeout_Time
Prop | Templates.HVAC Zone | Network Occupancy Request Time | 1675 | 1599 | 7073 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | minutes | 507:72 | 20 |  |  |  |  | 10ths | 0 | minutes | 507:72 | [9 empty] | Attr | York RTU.HVAC Zone | 25 | Network Occupancy Request Time | UCBapp.newUCB.Network_Occ_Request_Time | Present Value | FALSE | [6 empty] | Network_Occ_Request_Time
Prop | Templates.HVAC Zone | Common Setpoint | 2596 | 0 | 7074 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 70 | 45 | 98 |  |  | 1s | 0 | deg C | 507:62 | 8 | 36 |  |  |  | Common Setpoint ; Zone Temperature Setpoint |  |  |  | Attr | York RTU.HVAC Zone | 25 | Common Setpoint | UCBapp.newUCB.COMMON_SETPOINT | Relinquish Default | FALSE |  |  | UCBapp.newUCB.Setpoint_Input_Presence:Present Value = Curve 4 | AV:30065 | HR:853 | ADF:189 |  | Value |  |  | Views.Details.Cooling.Setup | Common Setpoint | 2596 | 0 |  | Views.Details.Clg.Setup | Common-SP | 1709 | 702
Prop | Templates.HVAC Zone | Common Setpoint | 2596 | 0 | 7074 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 70 | 45 | 98 |  |  | 1s | 0 | deg C | 507:62 | 8 | 36 |  |  |  | Common Setpoint ; Zone Temperature Setpoint |  |  |  | Attr | York RTU.HVAC Zone | 25 | Common Setpoint | UCBapp.newUCB.COMMON_SETPOINT | Relinquish Default | FALSE |  |  | UCBapp.newUCB.Setpoint_Input_Presence:Present Value = Curve 4 | AV:30065 | HR:853 | ADF:189 |  | Value |  |  | Views.Details.Heating.Setup | Common Setpoint | 2596 | 0 |  | Views.Details.Htg.Setup | Common-SP | 1709 | 702
Prop | Templates.HVAC Zone | Common Setpoint | 2596 | 0 | 7074 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 70 | 45 | 98 |  |  | 1s | 0 | deg C | 507:62 | 8 | 36 |  |  |  | Common Setpoint ; Zone Temperature Setpoint |  |  |  | Attr | York RTU.HVAC Zone | 25 | Common Setpoint | UCBapp.newUCB.COMMON_SETPOINT | Relinquish Default | FALSE |  |  | UCBapp.newUCB.Setpoint_Input_Presence:Present Value = Curve 4 | AV:30065 | HR:853 | ADF:189 |  | Value |  |  | Views.Details.Cooling.Misc | Common Setpoint | 2596 | 0 |  | Views.Details.Clg.Misc | Common-SP | 1709 | 702
Prop | Templates.HVAC Zone | Common Setpoint | 2596 | 0 | 7074 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 70 | 45 | 98 |  |  | 1s | 0 | deg C | 507:62 | 8 | 36 |  |  |  | Common Setpoint ; Zone Temperature Setpoint |  |  |  | Attr | York RTU.HVAC Zone | 25 | Common Setpoint | UCBapp.newUCB.COMMON_SETPOINT | Relinquish Default | FALSE |  |  | UCBapp.newUCB.Setpoint_Input_Presence:Present Value = Curve 4 | AV:30065 | HR:853 | ADF:189 |  | Value |  |  | Views.Clone.Partial Clone 1 | Common Setpoint | 2596 | 0 |  |  | Common-SP | 1709 | 702
Prop | Templates.HVAC Zone | Heat Cool Setpoint Mode | 1714 | 212 | 7075 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Heat Cool Setpoint Mode | 2596 | Individual_Setpoints | [6 empty] | Heat Cool Setpoint Mode | 2596 | [5 empty] | Use Individual Setpoints | 2596 | 0 = Common Setpoint 1 = Individual Setpoints |  | Attr | York RTU.HVAC Zone | 25 | Heat Cool Setpoint Mode | UCBapp.newUCB.HEAT_COOL_SP_MODE | Relinquish Default | FALSE |  |  | UCBapp.newUCB.Variable_Fan_And_SZVAV_Off_PI:Present Value = Inactive | MV:30066 | HR:852 | ADI:188 |  | Value |  |  | Views.Details.Cooling.Setup | Heat Cool Setpoint Mode | 1714 | 212 |  | Views.Details.Clg.Setup | Heat Cool Setpoint Mode | 1714 | 212
Prop | Templates.HVAC Zone | Heat Cool Setpoint Mode | 1714 | 212 | 7075 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Heat Cool Setpoint Mode | 2596 | Individual_Setpoints | [6 empty] | Heat Cool Setpoint Mode | 2596 | [5 empty] | Use Individual Setpoints | 2596 | 0 = Common Setpoint 1 = Individual Setpoints |  | Attr | York RTU.HVAC Zone | 25 | Heat Cool Setpoint Mode | UCBapp.newUCB.HEAT_COOL_SP_MODE | Relinquish Default | FALSE |  |  | UCBapp.newUCB.Variable_Fan_And_SZVAV_Off_PI:Present Value = Inactive | MV:30066 | HR:852 | ADI:188 |  | Value |  |  | Views.Details.Heating.Setup | Heat Cool Setpoint Mode | 1714 | 212 |  | Views.Details.Htg.Setup | Heat Cool Setpoint Mode | 1714 | 212
Prop | Templates.HVAC Zone | Heat Cool Setpoint Mode | 1714 | 212 | 7075 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Heat Cool Setpoint Mode | 2596 | Individual_Setpoints | [6 empty] | Heat Cool Setpoint Mode | 2596 | [5 empty] | Use Individual Setpoints | 2596 | 0 = Common Setpoint 1 = Individual Setpoints |  | Attr | York RTU.HVAC Zone | 25 | Heat Cool Setpoint Mode | UCBapp.newUCB.HEAT_COOL_SP_MODE | Relinquish Default | FALSE |  |  | UCBapp.newUCB.Variable_Fan_And_SZVAV_Off_PI:Present Value = Inactive | MV:30066 | HR:852 | ADI:188 |  | Value |  |  | Views.Clone.Partial Clone 1 | Heat Cool Setpoint Mode | 1714 | 212 |  |  | Heat Cool Setpoint Mode | 1714 | 212
Prop | Templates.HVAC Zone | Auto Changeover | 1675 | 1469 | 7076 | TRUE | TRUE | FALSE | 4 | Float | 10ths | 5 | delta deg F | 507:120 | 3 | 2 | 5 |  |  | 10ths | 0 | delta deg C | 507:359 | 1.1 | 2.8 | [7 empty] | Attr | York RTU.HVAC Zone | 25 | Auto Changeover | UCBapp.newUCB.AUTO_CHANGEOVER | Relinquish Default | FALSE |  |  | UCBapp.newUCB.Setpoint_Input_Presence:Present Value = Curve 4 |  |  |  |  | Value |  |  | Views.Details.Heating.Setup | Auto Changeover | 1675 | 1469 |  | Views.Details.Htg.Setup | Auto Changeover | 1675 | 1469
Prop | Templates.HVAC Zone | Auto Changeover | 1675 | 1469 | 7076 | TRUE | TRUE | FALSE | 4 | Float | 10ths | 5 | delta deg F | 507:120 | 3 | 2 | 5 |  |  | 10ths | 0 | delta deg C | 507:359 | 1.1 | 2.8 | [7 empty] | Attr | York RTU.HVAC Zone | 25 | Auto Changeover | UCBapp.newUCB.AUTO_CHANGEOVER | Relinquish Default | FALSE |  |  | UCBapp.newUCB.Setpoint_Input_Presence:Present Value = Curve 4 |  |  |  |  | Value |  |  | Views.Details.Cooling.Setup | Auto Changeover | 1675 | 1469 |  | Views.Details.Clg.Setup | Auto Changeover | 1675 | 1469
Prop | Templates.HVAC Zone | Auto Changeover | 1675 | 1469 | 7076 | TRUE | TRUE | FALSE | 4 | Float | 10ths | 5 | delta deg F | 507:120 | 3 | 2 | 5 |  |  | 10ths | 0 | delta deg C | 507:359 | 1.1 | 2.8 | [7 empty] | Attr | York RTU.HVAC Zone | 25 | Auto Changeover | UCBapp.newUCB.AUTO_CHANGEOVER | Relinquish Default | FALSE |  |  | UCBapp.newUCB.Setpoint_Input_Presence:Present Value = Curve 4 |  |  |  |  | Value |  |  | Views.Details.Cooling.Misc | Auto Changeover | 1675 | 1469 |  | Views.Details.Clg.Misc | Auto Changeover | 1675 | 1469
Prop | Templates.HVAC Zone | Auto Changeover | 1675 | 1469 | 7076 | TRUE | TRUE | FALSE | 4 | Float | 10ths | 5 | delta deg F | 507:120 | 3 | 2 | 5 |  |  | 10ths | 0 | delta deg C | 507:359 | 1.1 | 2.8 | [7 empty] | Attr | York RTU.HVAC Zone | 25 | Auto Changeover | UCBapp.newUCB.AUTO_CHANGEOVER | Relinquish Default | FALSE |  |  | UCBapp.newUCB.Setpoint_Input_Presence:Present Value = Curve 4 |  |  |  |  | Value |  |  | Views.Clone.Partial Clone 1 | Auto Changeover | 1675 | 1469 |  |  | Auto Changeover | 1675 | 1469
Prop | Templates.HVAC Zone | Netsensor Calibration | 1714 | 266 | 7077 | TRUE | TRUE | FALSE | 4 | Float | 10ths | 5 | delta deg F | 507:120 | 0 | -5 | 5 |  |  | 10ths | 0 | delta deg C | 507:359 | -3 | 3 | [7 empty] | Attr | York RTU.HVAC Zone | 25 | Netsensor Calibration | UCBapp.newUCB.Net_Sensor_Temp_Offset | Relinquish Default | FALSE |  |  | York RTU.HVAC Zone.Space Temperature Source:Present Value = Network Sensor |  |  |  |  | Value |  |  | Views.Summary.Sensors.Sensors | Netsensor Calibration | 1714 | 266 |  | Views.Summary.Sensors.Sensors | NS-Calibration | 1709 | 766
Tmpl | Templates.Weather Information | [31 empty] | Model | York RTU.Weather Information | 26
Prop | Templates.Weather Information | Operational Outdoor Air Temperature | 1675 | 36 | 7000 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | 0 |  |  |  |  | 10ths | 0 | deg C | 507:62 | [5 empty] | Outdoor Air Temperature |  |  |  | Attr | York RTU.Weather Information | 26 | Operational Outdoor Air Temperature | UCBapp.newUCB.Operational_OA_Temp | Present Value | FALSE |  |  |  | AV:29541 | IR:153 | ADF:23 |  | Value |  |  | Views.Summary.Sensors.Operational Mode | Operational Outdoor Air Temperature | 1675 | 36 |  | Views.Summary.Sensors.OprMode | OprOAT | 1709 | 52
Prop | Templates.Weather Information | Operational Outdoor Air Temperature | 1675 | 36 | 7000 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | 0 |  |  |  |  | 10ths | 0 | deg C | 507:62 | [5 empty] | Outdoor Air Temperature |  |  |  | Attr | York RTU.Weather Information | 26 | Operational Outdoor Air Temperature | UCBapp.newUCB.Operational_OA_Temp | Present Value | FALSE |  |  |  | AV:29541 | IR:153 | ADF:23 |  | Value |  |  | Views.Details.Cooling.Service.Unit | Operational Outdoor Air Temperature | 1675 | 36 |  | Views.Details.Clg.Service.Unit | OprOAT | 1709 | 52
Prop | Templates.Weather Information | Operational Outdoor Air Temperature | 1675 | 36 | 7000 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | 0 |  |  |  |  | 10ths | 0 | deg C | 507:62 | [5 empty] | Outdoor Air Temperature |  |  |  | Attr | York RTU.Weather Information | 26 | Operational Outdoor Air Temperature | UCBapp.newUCB.Operational_OA_Temp | Present Value | FALSE |  |  |  | AV:29541 | IR:153 | ADF:23 |  | Value |  |  | Views.Details.Heating.Service | Operational Outdoor Air Temperature | 1675 | 36 |  | Views.Details.Htg.Service | OprOAT | 1709 | 52
Prop | Templates.Weather Information | Operational Outdoor Air Temperature | 1675 | 36 | 7000 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | 0 |  |  |  |  | 10ths | 0 | deg C | 507:62 | [5 empty] | Outdoor Air Temperature |  |  |  | Attr | York RTU.Weather Information | 26 | Operational Outdoor Air Temperature | UCBapp.newUCB.Operational_OA_Temp | Present Value | FALSE |  |  |  | AV:29541 | IR:153 | ADF:23 |  | Value |  |  | Views.Details.Economizer.Service | Operational Outdoor Air Temperature | 1675 | 36 |  | Views.Details.Econ.Service | OprOAT | 1709 | 52
Prop | Templates.Weather Information | Operational Outdoor Air Temperature | 1675 | 36 | 7000 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | 0 |  |  |  |  | 10ths | 0 | deg C | 507:62 | [5 empty] | Outdoor Air Temperature |  |  |  | Attr | York RTU.Weather Information | 26 | Operational Outdoor Air Temperature | UCBapp.newUCB.Operational_OA_Temp | Present Value | FALSE |  |  |  | AV:29541 | IR:153 | ADF:23 |  | Value |  |  | Views.Details.Heat Pump | Operational Outdoor Air Temperature | 1675 | 36 |  | Views.Details.HeatPmp | OprOAT | 1709 | 52
Prop | Templates.Weather Information | Operational Outdoor Air Temperature | 1675 | 36 | 7000 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | 0 |  |  |  |  | 10ths | 0 | deg C | 507:62 | [5 empty] | Outdoor Air Temperature |  |  |  | Attr | York RTU.Weather Information | 26 | Operational Outdoor Air Temperature | UCBapp.newUCB.Operational_OA_Temp | Present Value | FALSE |  |  |  | AV:29541 | IR:153 | ADF:23 |  | Value |  |  | Views.Details.Hot Gas Reheat.Service | Operational Outdoor Air Temperature | 1675 | 36 |  | Views.Details.HGR.Service | OprOAT | 1709 | 52
Prop | Templates.Weather Information | Operational Outdoor Air Temperature | 1675 | 36 | 7000 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | 0 |  |  |  |  | 10ths | 0 | deg C | 507:62 | [5 empty] | Outdoor Air Temperature |  |  |  | Attr | York RTU.Weather Information | 26 | Operational Outdoor Air Temperature | UCBapp.newUCB.Operational_OA_Temp | Present Value | FALSE |  |  |  | AV:29541 | IR:153 | ADF:23 |  | Value |  |  | Views.Details.Mod Hot Gas Reheat.Service | Operational Outdoor Air Temperature | 1675 | 36 |  | Views.Details.ModHGR.Service | OprOAT | 1709 | 52
Prop | Templates.Weather Information | Outdoor Air Temperature Source | 1675 | 37 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Effective Input Source 2 | 1732 | Unreliable | [6 empty] | Effective Input Source 2 | 1732 | [6 empty] | 1732 | 0 = Unreliable 1 = Local Input 2 = Network Sensor 3 = High Priority ... |  | Attr | York RTU.Weather Information | 26 | Outdoor Air Temperature Source | UCBapp.newUCB.Outdoor_Air_Temp_Source | Present Value | FALSE |  |  |  | MV:29542 | IR:300 | ADI:21 |  | Value |  |  | Views.Summary.Sensors.Sensors | Outdoor Air Temperature Source | 1675 | 37 |  | Views.Summary.Sensors.Sensors | OATSrc | 1709 | 53
Prop | Templates.Weather Information | Outdoor Air Temperature Input | 1675 | 38 | 7002 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | 55 |  |  |  |  | 10ths | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Weather Information | 26 | Outdoor Air Temperature Input | UCBapp.newUCB.OA_T | Present Value | FALSE | [7 empty] | Value |  |  | Views.Summary.Sensors.Sensors | Outdoor Air Temperature Input | 1675 | 38 |  | Views.Summary.Sensors.Sensors | OAT | 1709 | 54
Prop | Templates.Weather Information | Outdoor Air Temperature Input | 1675 | 38 | 7002 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | 55 |  |  |  |  | 10ths | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.Weather Information | 26 | Outdoor Air Temperature Input | UCBapp.newUCB.OA_T | Present Value | FALSE | [7 empty] | Value |  |  | Views.Commissioning.Quick Start | Outdoor Air Temperature Input | 1675 | 38 |  | Views.Commission.Quick Start | OAT | 1709 | 54
Prop | Templates.Weather Information | Network Override Outdoor Air Temperature | 1675 | 39 | 7003 | TRUE | TRUE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | 72 | -50 | 125 |  |  | 10ths | 0 | deg C | 507:62 | -18 | 52 |  |  |  | Outdoor Air Temperature Destination |  |  |  | Attr | York RTU.Weather Information | 26 | Network Override Outdoor Air Temperature | UCBapp.newUCB.Network_Override_OA_Temp | Present Value | FALSE |  |  |  | AV:29543 | HR:6 | ADF:24 |  | Value |  |  | Views.Controller.Network Inputs | Network Override Outdoor Air Temperature | 1675 | 39 |  | Views.Controller.NetworkInputs | NetOAT | 1709 | 55
Prop | Templates.Weather Information | Network Override Outdoor Air Temperature | 1675 | 39 | 7003 | TRUE | TRUE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | 72 | -50 | 125 |  |  | 10ths | 0 | deg C | 507:62 | -18 | 52 |  |  |  | Outdoor Air Temperature Destination |  |  |  | Attr | York RTU.Weather Information | 26 | Network Override Outdoor Air Temperature | UCBapp.newUCB.Network_Override_OA_Temp | Present Value | FALSE |  |  |  | AV:29543 | HR:6 | ADF:24 |  | Value |  |  | Views.Clone.Network Override | Network Override Outdoor Air Temperature | 1675 | 39 |  |  | NetOAT | 1709 | 55
Prop | Templates.Weather Information | Operational Outdoor Air Humidity | 1675 | 40 | 7004 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | %RH | 507:29 | 50 |  |  |  |  | 1s | 0 | %RH | 507:29 | [5 empty] | Outdoor Humidity |  |  |  | Attr | York RTU.Weather Information | 26 | Operational Outdoor Air Humidity | EconApp.Econ.Outdoor Air Humidity Src | Present Value | FALSE |  |  | York RTU.System Controllers.Econ Controller:Present Value <> Not Present | AV:29544 | IR:154 | ADF:25 |  | Value |  |  | Views.Summary.Sensors.Operational Mode | Operational Outdoor Air Humidity | 1675 | 40 |  | Views.Summary.Sensors.OprMode | OprOAH | 1709 | 56
Prop | Templates.Weather Information | Outdoor Air Enthalpy | 1675 | 41 | 7005 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | Btu/lb | 507:117 | 27 |  |  |  |  | 1s | 0 | kJ/kg | 507:125 | [9 empty] | Attr | York RTU.Weather Information | 26 | Outdoor Air Enthalpy | UCBapp.newUCB.Outdoor_Air_Enthalpy | Present Value | FALSE |  |  | York RTU.System Controllers.Econ Controller:Present Value <> Not Present | AV:29545 | IR:155 | ADF:26 |  | Value |  |  | Views.Details.Economizer.Service | Outdoor Air Enthalpy | 1675 | 41 |  | Views.Details.Econ.Service | OA-Enth | 1709 | 57
Prop | Templates.Weather Information | Outdoor Air Humidity Source | 1675 | 42 | 7006 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Effective Input Source 2 | 1732 | Unreliable | [6 empty] | Effective Input Source 2 | 1732 | [6 empty] | 1732 | 0 = Unreliable 1 = Local Input 2 = Network Sensor 3 = High Priority ... |  | Attr | York RTU.Weather Information | 26 | Outdoor Air Humidity Source | EconApp.Econ.Eff OA-H State | Present Value | FALSE |  |  | York RTU.System Controllers.Econ Controller:Present Value <> Not Present |  |  |  |  | Value |  |  | Views.Summary.Sensors.Sensors | Outdoor Air Humidity Source | 1675 | 42 |  | Views.Summary.Sensors.Sensors | OAHSrc | 1709 | 58
Prop | Templates.Weather Information | Outdoor Air Humidity Input | 1675 | 43 | 7007 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | %RH | 507:29 | Unreliable |  |  |  |  | 10ths | 0 | %RH | 507:29 | [9 empty] | Attr | York RTU.Weather Information | 26 | Outdoor Air Humidity Input | EconApp.Econ.OA-H | Present Value | FALSE |  |  | York RTU.System Controllers.Econ Controller:Present Value <> Not Present |  |  |  |  | Value |  |  | Views.Summary.Sensors.Sensors | Outdoor Air Humidity Input | 1675 | 43 |  | Views.Summary.Sensors.Sensors | OAH | 1709 | 59
Prop | Templates.Weather Information | Network Override Outdoor Air Humidity | 1675 | 44 | 7008 | TRUE | TRUE | FALSE | 4 | Float | 10ths | 5 | %RH | 507:29 | 0 | 0 | 100 |  |  | 10ths | 0 | %RH | 507:29 | 0 | 100 |  |  |  | Outdoor Humidity Destination |  |  |  | Attr | York RTU.Weather Information | 26 | Network Override Outdoor Air Humidity | EconApp.Econ.OA-H Timed Override | Present Value | FALSE |  |  | York RTU.System Controllers.Econ Controller:Present Value <> Not Present | AV:29546 | HR:7 | ADF:27 |  | Value |  |  | Views.Controller.Network Inputs | Network Override Outdoor Air Humidity | 1675 | 44 |  | Views.Controller.NetworkInputs | NetOAH | 1709 | 60
Prop | Templates.Weather Information | Network Override Outdoor Air Humidity | 1675 | 44 | 7008 | TRUE | TRUE | FALSE | 4 | Float | 10ths | 5 | %RH | 507:29 | 0 | 0 | 100 |  |  | 10ths | 0 | %RH | 507:29 | 0 | 100 |  |  |  | Outdoor Humidity Destination |  |  |  | Attr | York RTU.Weather Information | 26 | Network Override Outdoor Air Humidity | EconApp.Econ.OA-H Timed Override | Present Value | FALSE |  |  | York RTU.System Controllers.Econ Controller:Present Value <> Not Present | AV:29546 | HR:7 | ADF:27 |  | Value |  |  | Views.Clone.Network Override | Network Override Outdoor Air Humidity | 1675 | 44 |  |  | NetOAH | 1709 | 60
Prop | Templates.Weather Information | Operational Outdoor Air Quality | 1675 | 45 | 7009 | TRUE | FALSE | FALSE | 4 | Float | 10s | 7 | ppm | 507:96 | 50 |  |  |  |  | 10s | 0 | ppm | 507:96 | [9 empty] | Attr | York RTU.Weather Information | 26 | Operational Outdoor Air Quality | EconApp.Econ.Outdoor Air Quality Src | Present Value | FALSE |  |  | York RTU.System Controllers.Econ Controller:Present Value <> Not Present | AV:29547 | IR:156 | ADF:28 |  | Value |  |  | Views.Summary.Sensors.Operational Mode | Operational Outdoor Air Quality | 1675 | 45 |  | Views.Summary.Sensors.OprMode | OprOAQ | 1709 | 61
Prop | Templates.Weather Information | Operational Outdoor Air Quality | 1675 | 45 | 7009 | TRUE | FALSE | FALSE | 4 | Float | 10s | 7 | ppm | 507:96 | 50 |  |  |  |  | 10s | 0 | ppm | 507:96 | [9 empty] | Attr | York RTU.Weather Information | 26 | Operational Outdoor Air Quality | EconApp.Econ.Outdoor Air Quality Src | Present Value | FALSE |  |  | York RTU.System Controllers.Econ Controller:Present Value <> Not Present | AV:29547 | IR:156 | ADF:28 |  | Value |  |  | Views.Details.Economizer.Service | Operational Outdoor Air Quality | 1675 | 45 |  | Views.Details.Econ.Service | OprOAQ | 1709 | 61
Prop | Templates.Weather Information | Operational Outdoor Air Quality | 1675 | 45 | 7009 | TRUE | FALSE | FALSE | 4 | Float | 10s | 7 | ppm | 507:96 | 50 |  |  |  |  | 10s | 0 | ppm | 507:96 | [9 empty] | Attr | York RTU.Weather Information | 26 | Operational Outdoor Air Quality | EconApp.Econ.Outdoor Air Quality Src | Present Value | FALSE |  |  | York RTU.System Controllers.Econ Controller:Present Value <> Not Present | AV:29547 | IR:156 | ADF:28 |  | Value |  |  | Views.Details.Demand Ventilation | Operational Outdoor Air Quality | 1675 | 45 |  | Views.Details.DVent | OprOAQ | 1709 | 61
Prop | Templates.Weather Information | Outdoor Air Quality Source | 1675 | 46 | 7010 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Effective Input Source 2 | 1732 | Unreliable | [6 empty] | Effective Input Source 2 | 1732 | [6 empty] | 1732 | 0 = Unreliable 1 = Local Input 2 = Network Sensor 3 = High Priority ... |  | Attr | York RTU.Weather Information | 26 | Outdoor Air Quality Source | EconApp.Econ.Eff OA-Q State | Present Value | FALSE |  |  | York RTU.System Controllers.Econ Controller:Present Value <> Not Present | MV:29548 | IR:301 | ADI:22 |  | Value |  |  | Views.Summary.Sensors.Sensors | Outdoor Air Quality Source | 1675 | 46 |  | Views.Summary.Sensors.Sensors | OAQSrc | 1709 | 62
Prop | Templates.Weather Information | Outdoor Air Quality Input | 1675 | 47 | 7011 | TRUE | FALSE | FALSE | 4 | Float | 10s | 7 | ppm | 507:96 | N/A |  |  |  |  | 10s | 0 | ppm | 507:96 | [9 empty] | Attr | York RTU.Weather Information | 26 | Outdoor Air Quality Input | EconApp.Econ.OAQ-CO2 | Present Value | FALSE |  |  | York RTU.System Controllers.Econ Controller:Present Value <> Not Present |  |  |  |  | Value |  |  | Views.Summary.Sensors.Sensors | Outdoor Air Quality Input | 1675 | 47 |  | Views.Summary.Sensors.Sensors | OAQ | 1709 | 63
Prop | Templates.Weather Information | Outdoor Air Quality Sensor Range | 1675 | 48 | 7012 | TRUE | TRUE | FALSE | 4 | Float | 10s | 7 | ppm | 507:96 |  | 0 | 5000 |  |  | 10s | 0 | ppm | 507:96 | 0 | 5000 | [7 empty] | Attr | York RTU.Weather Information | 26 | Outdoor Air Quality Sensor Range | 8-1/Econ.OAQ-CO2 | Output Range High | FALSE |  |  | York RTU.System Controllers.Econ Controller:Present Value <> Not Present |  |  |  |  | Value |  |  | Views.Details.Economizer.Setup | Outdoor Air Quality Sensor Range | 1675 | 48 |  | Views.Details.Econ.Setup | OAQRange | 1709 | 64
Prop | Templates.Weather Information | Outdoor Air Quality Sensor Range | 1675 | 48 | 7012 | TRUE | TRUE | FALSE | 4 | Float | 10s | 7 | ppm | 507:96 |  | 0 | 5000 |  |  | 10s | 0 | ppm | 507:96 | 0 | 5000 | [7 empty] | Attr | York RTU.Weather Information | 26 | Outdoor Air Quality Sensor Range | 8-1/Econ.OAQ-CO2 | Output Range High | FALSE |  |  | York RTU.System Controllers.Econ Controller:Present Value <> Not Present |  |  |  |  | Value |  |  | Views.Details.Demand Ventilation | Outdoor Air Quality Sensor Range | 1675 | 48 |  | Views.Details.DVent | OAQRange | 1709 | 64
Prop | Templates.Weather Information | Outdoor Air Quality Sensor Range | 1675 | 48 | 7012 | TRUE | TRUE | FALSE | 4 | Float | 10s | 7 | ppm | 507:96 |  | 0 | 5000 |  |  | 10s | 0 | ppm | 507:96 | 0 | 5000 | [7 empty] | Attr | York RTU.Weather Information | 26 | Outdoor Air Quality Sensor Range | 8-1/Econ.OAQ-CO2 | Output Range High | FALSE |  |  | York RTU.System Controllers.Econ Controller:Present Value <> Not Present |  |  |  |  | Value |  |  | Views.Clone.Partial Clone 1 | Outdoor Air Quality Sensor Range | 1675 | 48 |  |  | OAQRange | 1709 | 64
Prop | Templates.Weather Information | Network Override Outdoor Air Quality | 1675 | 49 | 7013 | TRUE | TRUE | FALSE | 4 | Float | 10s | 7 | ppm | 507:96 | 0 | 0 | 5000 |  |  | 10s | 0 | ppm | 507:96 | 0 | 5000 | [7 empty] | Attr | York RTU.Weather Information | 26 | Network Override Outdoor Air Quality | EconApp.Econ.OA-Q Timed Override | Present Value | FALSE |  |  | York RTU.System Controllers.Econ Controller:Present Value <> Not Present | AV:29549 | HR:8 | ADF:29 |  | Value |  |  | Views.Controller.Network Inputs | Network Override Outdoor Air Quality | 1675 | 49 |  | Views.Controller.NetworkInputs | NetOAQ | 1709 | 65
Prop | Templates.Weather Information | Network Override Outdoor Air Quality | 1675 | 49 | 7013 | TRUE | TRUE | FALSE | 4 | Float | 10s | 7 | ppm | 507:96 | 0 | 0 | 5000 |  |  | 10s | 0 | ppm | 507:96 | 0 | 5000 | [7 empty] | Attr | York RTU.Weather Information | 26 | Network Override Outdoor Air Quality | EconApp.Econ.OA-Q Timed Override | Present Value | FALSE |  |  | York RTU.System Controllers.Econ Controller:Present Value <> Not Present | AV:29549 | HR:8 | ADF:29 |  | Value |  |  | Views.Clone.Network Override | Network Override Outdoor Air Quality | 1675 | 49 |  |  | NetOAQ | 1709 | 65
Prop | Templates.Weather Information | Outdoor Air Temperature Sensor Fault | 1675 | 303 | 7014 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Weather Information | 26 | Outdoor Air Temperature Sensor Fault | UCBapp.newUCB.OA_Temperature_Sensor_Fault | Present Value | FALSE
Prop | Templates.Weather Information | Outdoor Air Humidity Sensor Fault | 1675 | 304 | 7015 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | No | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Weather Information | 26 | Outdoor Air Humidity Sensor Fault | EconApp.Econ.OA-H Alarm | Present Value | FALSE
Prop | Templates.Weather Information | Outdoor Air Quality Sensor Fault | 1675 | 305 | 7016 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | No | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Weather Information | 26 | Outdoor Air Quality Sensor Fault | EconApp.Econ.OA-Q Alarm | Present Value | FALSE
Tmpl | Templates.Shutdown Input | [31 empty] | Model | York RTU.Shutdown Input | 27
Prop | Templates.Shutdown Input | Operating Purge Command | 1675 | 258 | 7000 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | False/True | 1701 | Off | [6 empty] | False/True | 1701 | [6 empty] | 1701 | 0 = False 1 = True |  | Attr | York RTU.Shutdown Input | 27 | Operating Purge Command | EconApp.Econ.Purge Src | Present Value | FALSE |  |  | York RTU.System Controllers.Econ Controller:Present Value <> Not Present | MV:29798 | IR:381 | ADI:98 |  | Value |  |  | Views.Status.Smoke Control | Operating Purge Command | 1675 | 258 |  | Views.Status.SmokeCtrl | OprPurgeCmd | 1709 | 332
Prop | Templates.Shutdown Input | Operating Purge Command | 1675 | 258 | 7000 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | False/True | 1701 | Off | [6 empty] | False/True | 1701 | [6 empty] | 1701 | 0 = False 1 = True |  | Attr | York RTU.Shutdown Input | 27 | Operating Purge Command | EconApp.Econ.Purge Src | Present Value | FALSE |  |  | York RTU.System Controllers.Econ Controller:Present Value <> Not Present | MV:29798 | IR:381 | ADI:98 |  | Value |  |  | Views.Summary.Sensors.Operational Mode | Operating Purge Command | 1675 | 258 |  | Views.Summary.Sensors.OprMode | OprPurgeCmd | 1709 | 332
Prop | Templates.Shutdown Input | Purge Command Source | 1675 | 259 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Effective Input Source 2 | 1732 | Unreliable | [6 empty] | Effective Input Source 2 | 1732 | [6 empty] | 1732 | 0 = Unreliable 1 = Local Input 2 = Network Sensor 3 = High Priority ... |  | Attr | York RTU.Shutdown Input | 27 | Purge Command Source | EconApp.Econ.Eff Purge State | Present Value | FALSE |  |  | York RTU.System Controllers.Econ Controller:Present Value <> Not Present | MV:29799 | IR:382 | ADI:99 |  | Value |  |  | Views.Status.Smoke Control | Purge Command Source | 1675 | 259 |  | Views.Status.SmokeCtrl | PurgeCmdSrc | 1709 | 333
Prop | Templates.Shutdown Input | Purge Command Source | 1675 | 259 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Effective Input Source 2 | 1732 | Unreliable | [6 empty] | Effective Input Source 2 | 1732 | [6 empty] | 1732 | 0 = Unreliable 1 = Local Input 2 = Network Sensor 3 = High Priority ... |  | Attr | York RTU.Shutdown Input | 27 | Purge Command Source | EconApp.Econ.Eff Purge State | Present Value | FALSE |  |  | York RTU.System Controllers.Econ Controller:Present Value <> Not Present | MV:29799 | IR:382 | ADI:99 |  | Value |  |  | Views.Summary.Sensors.Sensors | Purge Command Source | 1675 | 259 |  | Views.Summary.Sensors.Sensors | PurgeCmdSrc | 1709 | 333
Prop | Templates.Shutdown Input | Local Purge Command Input | 1675 | 260 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | False/True | 1701 | N/A | [6 empty] | False/True | 1701 | [6 empty] | 1701 | 0 = False 1 = True |  | Attr | York RTU.Shutdown Input | 27 | Local Purge Command Input | EconApp.Econ.PURGE-S | Present Value | FALSE |  |  | York RTU.System Controllers.Econ Controller:Present Value <> Not Present | MV:29800 | IR:383 | ADI:100 |  | Value |  |  | Views.Status.Smoke Control | Local Purge Command Input | 1675 | 260 |  | Views.Status.SmokeCtrl | Purge | 1709 | 334
Prop | Templates.Shutdown Input | Network Override Purge Command | 1675 | 261 | 7003 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | False/True | 1701 | No | [6 empty] | False/True | 1701 | [6 empty] | 1701 | 0 = False 1 = True |  | Attr | York RTU.Shutdown Input | 27 | Network Override Purge Command | EconApp.Econ.Purge Timed Override | Present Value | FALSE |  |  | York RTU.System Controllers.Econ Controller:Present Value <> Not Present | MV:29801 | HR:125 | ADI:101 |  | Value |  |  | Views.Status.Smoke Control | Network Override Purge Command | 1675 | 261 |  | Views.Status.SmokeCtrl | NetPurge | 1709 | 335
Prop | Templates.Shutdown Input | Network Override Purge Command | 1675 | 261 | 7003 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | False/True | 1701 | No | [6 empty] | False/True | 1701 | [6 empty] | 1701 | 0 = False 1 = True |  | Attr | York RTU.Shutdown Input | 27 | Network Override Purge Command | EconApp.Econ.Purge Timed Override | Present Value | FALSE |  |  | York RTU.System Controllers.Econ Controller:Present Value <> Not Present | MV:29801 | HR:125 | ADI:101 |  | Value |  |  | Views.Controller.Network Inputs | Network Override Purge Command | 1675 | 261 |  | Views.Controller.NetworkInputs | NetPurge | 1709 | 335
Prop | Templates.Shutdown Input | Network Override Purge Command | 1675 | 261 | 7003 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | False/True | 1701 | No | [6 empty] | False/True | 1701 | [6 empty] | 1701 | 0 = False 1 = True |  | Attr | York RTU.Shutdown Input | 27 | Network Override Purge Command | EconApp.Econ.Purge Timed Override | Present Value | FALSE |  |  | York RTU.System Controllers.Econ Controller:Present Value <> Not Present | MV:29801 | HR:125 | ADI:101 |  | Value |  |  | Views.Clone.Network Override | Network Override Purge Command | 1675 | 261 |  |  | NetPurge | 1709 | 335
Prop | Templates.Shutdown Input | Shutdown Input/Smoke Detector | 1675 | 262 | 7004 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | N/A | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm |  | Attr | York RTU.Shutdown Input | 27 | Shutdown Input/Smoke Detector | UCBapp.newUCB.SS_S | Present Value | FALSE |  |  |  | MV:29802 | IR:384 | ADI:102 |  | Value |  |  | Views.Status.Smoke Control | Shutdown Input/Smoke Detector | 1675 | 262 |  | Views.Status.SmokeCtrl | SD | 1709 | 336
Prop | Templates.Shutdown Input | Pressurize Instead Of Purge | 1714 | 222 | 7005 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Off | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Shutdown Input | 27 | Pressurize Instead Of Purge | UCBapp.newUCB.Pressurize_Instead_Of_Purge | Relinquish Default | FALSE |  |  |  | MV:30068 | HR:844 | ADI:192 |  | Value |  |  | Views.Commissioning.Options | Pressurize Instead Of Purge | 1714 | 222 |  | Views.Commission.Options | PressurizeNotPurge | 1709 | 709
Tmpl | Templates.System Controllers | [31 empty] | Model | York RTU.System Controllers | 29
Prop | Templates.System Controllers | Language | 1675 | 267 | 7000 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | SE RTU Languages | 1730 | [7 empty] | SE RTU Languages | 1730 | [5 empty] | Language | 1730 | 7 = English 10 = French 28 = Spanish |  | Attr | York RTU.System Controllers | 29 | Language | 8-1/Dictionary | BAS Language | FALSE | [7 empty] | Value |  |  | Views.Controller.Network | Language | 1675 | 267 |  | Views.Controller.Network | Language | 1709 | 337
Prop | Templates.System Controllers | Language | 1675 | 267 | 7000 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | SE RTU Languages | 1730 | [7 empty] | SE RTU Languages | 1730 | [5 empty] | Language | 1730 | 7 = English 10 = French 28 = Spanish |  | Attr | York RTU.System Controllers | 29 | Language | 8-1/Dictionary | BAS Language | FALSE | [7 empty] | Value |  |  | Views.Clone.Partial Clone 1 | Language | 1675 | 267 |  |  | Language | 1709 | 337
Prop | Templates.System Controllers | Language | 1675 | 267 | 7000 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | SE RTU Languages | 1730 | [7 empty] | SE RTU Languages | 1730 | [5 empty] | Language | 1730 | 7 = English 10 = French 28 = Spanish |  | Attr | York RTU.System Controllers | 29 | Language | 8-1/Dictionary | BAS Language | FALSE | [7 empty] | Value |  |  | Views.Controller.Controller Info | Language | 1675 | 267 |  | Views.Controller.Controller Info | Language | 1675 | 267
Prop | Templates.System Controllers | Units | 1675 | 268 | 7001 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Unit Set | 869 | [7 empty] | Unit Set | 869 | [5 empty] | Units | 869 | 0 = IP 1 = SI |  | Attr | York RTU.System Controllers | 29 | Units | UCBapp | BAS Unit System | FALSE | [7 empty] | Value |  |  | Views.Controller.Network | Units | 1675 | 268 |  | Views.Controller.Network | Units | 1709 | 338
Prop | Templates.System Controllers | Units | 1675 | 268 | 7001 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Unit Set | 869 | [7 empty] | Unit Set | 869 | [5 empty] | Units | 869 | 0 = IP 1 = SI |  | Attr | York RTU.System Controllers | 29 | Units | UCBapp | BAS Unit System | FALSE | [7 empty] | Value |  |  | Views.Clone.Partial Clone 1 | Units | 1675 | 268 |  |  | Units | 1709 | 338
Prop | Templates.System Controllers | Units | 1675 | 268 | 7001 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Unit Set | 869 | [7 empty] | Unit Set | 869 | [5 empty] | Units | 869 | 0 = IP 1 = SI |  | Attr | York RTU.System Controllers | 29 | Units | UCBapp | BAS Unit System | FALSE | [7 empty] | Value |  |  | Views.Controller.Controller Info | Units | 1675 | 268 |  | Views.Controller.Controller Info | Units | 1675 | 268
Prop | Templates.System Controllers | Relearn System | 1675 | 269 | 7002 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Relearn | 1793 | [7 empty] | Relearn | 1793 | [5 empty] | Relearn System | 1793 | 0 = False 1 = True |  | Attr | York RTU.System Controllers | 29 | Relearn System | UCBapp | Rediscover Components | FALSE | [7 empty] | Value |  |  | Views.Controller.Network | Relearn System | 1675 | 269 |  | Views.Controller.Network | Relearn | 1709 | 339
Prop | Templates.System Controllers | BAS Communication | 1675 | 270 | 7003 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | BAS Communication | 1724 | [7 empty] | BAS Communication | 1724 | [6 empty] | 1724 | 0 = Not Installed 1 = BACnet 2 = N2 3 = Modbus |  | Attr | York RTU.System Controllers | 29 | BAS Communication | EM Variable: 1 |  | FALSE | [7 empty] | Value |  |  | Views.Clone.Partial Clone 1 | BAS Communication | 1675 | 270 |  |  | BASCom | 1709 | 340
Prop | Templates.System Controllers | Econ Controller | 1675 | 315 | 7004 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | EIO Connection Status | 1662 | Not_Present | [6 empty] | EIO Connection Status | 1662 | [6 empty] | 1662 | 0 = Not Present 1 = Offline 2 = Online |  | Attr | York RTU.System Controllers | 29 | Econ Controller | UCBapp.newUCB.Eff_Econ_Comm_Status | Present Value | TRUE |  |  |  | MV:29813 | IR:385 | ADI:103 |  | Value |  |  | Views.Status.Control | Econ Controller | 1675 | 315 |  | Views.Status.SysCntlrs | EconCntlr | 1709 | 437
Prop | Templates.System Controllers | 4 Stage Controller | 1675 | 316 | 7005 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | EIO Connection Status | 1662 | Not_Present | [6 empty] | EIO Connection Status | 1662 | [6 empty] | 1662 | 0 = Not Present 1 = Offline 2 = Online |  | Attr | York RTU.System Controllers | 29 | 4 Stage Controller | UCBapp.newUCB.Eff_Four_Stage_Comm_Status | Present Value | TRUE |  |  |  | MV:29814 | IR:386 | ADI:104 |  | Value |  |  | Views.Status.Control | 4 Stage Controller | 1675 | 316 |  | Views.Status.SysCntlrs | 4StgCntlr | 1709 | 438
Prop | Templates.System Controllers | FDD Manager Controller | 1675 | 317 | 7006 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | EIO Connection Status | 1662 | Not_Present | [6 empty] | EIO Connection Status | 1662 | [6 empty] | 1662 | 0 = Not Present 1 = Offline 2 = Online |  | Attr | York RTU.System Controllers | 29 | FDD Manager Controller | UCBapp.newUCB.Eff_FDD1_Comm_Status | Present Value | TRUE |  |  |  | MV:29815 | IR:387 | ADI:105 |  | Value |  |  | Views.Status.Control | FDD Manager Controller | 1675 | 317 |  | Views.Status.SysCntlrs | FDDMCntlr | 1709 | 439
Prop | Templates.System Controllers | FDD Subordinate Controller | 1675 | 318 | 7007 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | EIO Connection Status | 1662 | Not_Present | [6 empty] | EIO Connection Status | 1662 | [6 empty] | 1662 | 0 = Not Present 1 = Offline 2 = Online |  | Attr | York RTU.System Controllers | 29 | FDD Subordinate Controller | UCBapp.newUCB.Eff_FDD2_Comm_Status | Present Value | TRUE |  |  |  | MV:29816 | IR:388 | ADI:106 |  | Value |  |  | Views.Status.Control | FDD Subordinate Controller | 1675 | 318 |  | Views.Status.SysCntlrs | FDDSCntlr | 1709 | 440
Prop | Templates.System Controllers | Device Name | 1675 | 326 | 7009 | TRUE | TRUE | FALSE | 7 | String | [17 empty] | 30 | Equipment Name |  |  |  | Attr | York RTU.System Controllers | 29 | Device Name | UCBapp | My Name | FALSE |  |  |  | CSV:29818 |  |  |  | Value |  |  | Views.Commissioning.Network Setup | Device Name | 1675 | 326 |  | Views.Commission.Network Setup | DevName | 1709 | 446
Prop | Templates.System Controllers | Device Name | 1675 | 326 | 7009 | TRUE | TRUE | FALSE | 7 | String | [17 empty] | 30 | Equipment Name |  |  |  | Attr | York RTU.System Controllers | 29 | Device Name | UCBapp | My Name | FALSE |  |  |  | CSV:29818 |  |  |  | Value |  |  | Views.Controller.Network | Device Name | 1675 | 326 |  | Views.Controller.Network | DevName | 1709 | 446
Prop | Templates.System Controllers | Device Name | 1675 | 326 | 7009 | TRUE | TRUE | FALSE | 7 | String | [17 empty] | 30 | Equipment Name |  |  |  | Attr | York RTU.System Controllers | 29 | Device Name | UCBapp | My Name | FALSE |  |  |  | CSV:29818 |  |  |  | Value |  |  | Views.Clone.Full Clone | Device Name | 1675 | 326 |  |  | DevName | 1709 | 446
Prop | Templates.System Controllers | Description | 1675 | 2 | 7010 | TRUE | TRUE | FALSE | 7 | String | [17 empty] | 40 | Equipment Description |  |  |  | Attr | York RTU.System Controllers | 29 | Description | UCBapp | Description | FALSE | [7 empty] | Value |  |  | Views.Controller.Network | Description | 1675 | 2 |  | Views.Controller.Network | Descrip | 1709 | 473
Prop | Templates.System Controllers | Brightness Setting | 1675 | 641 | 7011 | TRUE | TRUE | FALSE | 18 | UnsignedInteger | 1s | 6 |  | 507:95 |  | 3 | 10 |  |  | 1s | 0 |  | 507:95 | 3 | 10 | [7 empty] | Attr | York RTU.System Controllers | 29 | Brightness Setting | UCBapp | Display Contrast | FALSE | [7 empty] | Value |  |  | Views.Controller.Controller Info | Brightness Setting | 1675 | 641 |  | Views.Controller.Controller Info | Brightness Setting | 1675 | 641
Tmpl | Templates.Time | [31 empty] | Model | York RTU.System Controllers.Time | 30
Prop | Templates.Time | Time | 1675 | 271 | 7000 | TRUE | FALSE | FALSE | 11 | Time | [22 empty] | Attr | York RTU.System Controllers.Time | 30 | Time | UCBapp | Local Time | FALSE | [7 empty] | Value |  |  | Views.Controller.Time | Time | 1675 | 271 |  | Views.Controller.Time | Time | 1709 | 342
Prop | Templates.Time | Date | 1675 | 272 | 7001 | TRUE | FALSE | FALSE | 10 | Date | [22 empty] | Attr | York RTU.System Controllers.Time | 30 | Date | UCBapp | Local Date | FALSE | [7 empty] | Value |  |  | Views.Controller.Time | Date | 1675 | 272 |  | Views.Controller.Time | Date | 1709 | 343
Prop | Templates.Time | Time Zone | 1675 | 278 | 7007 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | SE RTU Time Zone | 1731 | [7 empty] | SE RTU Time Zone | 1731 | [6 empty] | 1731 | 51 = Eastern 53 = Central 57 = Mountain 58 = Pacific ... |  | Attr | York RTU.System Controllers.Time | 30 | Time Zone | UCBapp | Default Time Zone | FALSE | [7 empty] | Value |  |  | Views.Controller.Network | Time Zone | 1675 | 278 |  | Views.Controller.Network | TimeZone | 1709 | 349
Prop | Templates.Time | Time Zone | 1675 | 278 | 7007 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | SE RTU Time Zone | 1731 | [7 empty] | SE RTU Time Zone | 1731 | [6 empty] | 1731 | 51 = Eastern 53 = Central 57 = Mountain 58 = Pacific ... |  | Attr | York RTU.System Controllers.Time | 30 | Time Zone | UCBapp | Default Time Zone | FALSE | [7 empty] | Value |  |  | Views.Controller.Time | Time Zone | 1675 | 278 |  | Views.Controller.Time | TimeZone | 1709 | 349
Prop | Templates.Time | Time Zone | 1675 | 278 | 7007 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | SE RTU Time Zone | 1731 | [7 empty] | SE RTU Time Zone | 1731 | [6 empty] | 1731 | 51 = Eastern 53 = Central 57 = Mountain 58 = Pacific ... |  | Attr | York RTU.System Controllers.Time | 30 | Time Zone | UCBapp | Default Time Zone | FALSE | [7 empty] | Value |  |  | Views.Clone.Full Clone | Time Zone | 1675 | 278 |  |  | TimeZone | 1709 | 349
Tmpl | Templates.Network | [31 empty] | Model | York RTU.System Controllers.Network | 31
Prop | Templates.Network | Communication Status | 1675 | 281 | 7000 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | MSTPDL Port Status | 302 | [7 empty] | MSTPDL Port Status | 302 | [6 empty] | 302 | 0 = Not Configured 1 = Active 2 = Waiting For Poll For Manager 3 = Not Received Token For Long ... |  | Attr | York RTU.System Controllers.Network | 31 | Communication Status | 8-1/MSTP Network Port | Port Status | FALSE | [7 empty] | Value |  |  | Views.Controller.Network | Communication Status | 1675 | 281 |  | Views.Controller.Network | Comm-S | 1709 | 341
Prop | Templates.Network | Address | 1675 | 282 | 7001 | TRUE | TRUE | FALSE | 17 | SignedInteger | 1s | 6 |  | 507:95 |  | 4 | 127 |  |  | 1s | 0 |  | 507:95 | 4 | 127 | [7 empty] | Attr | York RTU.System Controllers.Network | 31 | Address | UCBapp | Device Address | FALSE | [7 empty] | Value |  |  | Views.Commissioning.Network Setup | Address | 1675 | 282 |  | Views.Commission.Network Setup | Address | 1709 | 352
Prop | Templates.Network | Address | 1675 | 282 | 7001 | TRUE | TRUE | FALSE | 17 | SignedInteger | 1s | 6 |  | 507:95 |  | 4 | 127 |  |  | 1s | 0 |  | 507:95 | 4 | 127 | [7 empty] | Attr | York RTU.System Controllers.Network | 31 | Address | UCBapp | Device Address | FALSE | [7 empty] | Value |  |  | Views.Controller.Network | Address | 1675 | 282 |  | Views.Controller.Network | Address | 1709 | 352
Prop | Templates.Network | Address | 1675 | 282 | 7001 | TRUE | TRUE | FALSE | 17 | SignedInteger | 1s | 6 |  | 507:95 |  | 4 | 127 |  |  | 1s | 0 |  | 507:95 | 4 | 127 | [7 empty] | Attr | York RTU.System Controllers.Network | 31 | Address | UCBapp | Device Address | FALSE | [7 empty] | Value |  |  | Views.Clone.Full Clone | Address | 1675 | 282 |  |  | Address | 1709 | 352
Prop | Templates.Network | Device OID | 1675 | 283 | 7002 | TRUE | TRUE | FALSE | 2 | UnsignedLong | 1s | 6 |  | 507:95 |  | 0 | 4194302 |  |  | 1s | 0 |  | 507:95 | 0 | 4194302 | [7 empty] | Attr | York RTU.System Controllers.Network | 31 | Device OID | UCBapp | Device Object Identifier | FALSE |  |  |  | AV:29897 |  |  |  | Value |  |  | Views.Commissioning.Network Setup | Device OID | 1675 | 283 |  | Views.Commission.Network Setup | DeviceId | 1709 | 353
Prop | Templates.Network | Device OID | 1675 | 283 | 7002 | TRUE | TRUE | FALSE | 2 | UnsignedLong | 1s | 6 |  | 507:95 |  | 0 | 4194302 |  |  | 1s | 0 |  | 507:95 | 0 | 4194302 | [7 empty] | Attr | York RTU.System Controllers.Network | 31 | Device OID | UCBapp | Device Object Identifier | FALSE |  |  |  | AV:29897 |  |  |  | Value |  |  | Views.Controller.Network | Device OID | 1675 | 283 |  | Views.Controller.Network | DeviceId | 1709 | 353
Prop | Templates.Network | Device OID | 1675 | 283 | 7002 | TRUE | TRUE | FALSE | 2 | UnsignedLong | 1s | 6 |  | 507:95 |  | 0 | 4194302 |  |  | 1s | 0 |  | 507:95 | 0 | 4194302 | [7 empty] | Attr | York RTU.System Controllers.Network | 31 | Device OID | UCBapp | Device Object Identifier | FALSE |  |  |  | AV:29897 |  |  |  | Value |  |  | Views.Clone.Full Clone | Device OID | 1675 | 283 |  |  | DeviceId | 1709 | 353
Prop | Templates.Network | Operating Baud Rate | 1675 | 284 | 7003 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | MSTPDL Baud Rate | 300 | [7 empty] | MSTPDL Baud Rate | 300 | [6 empty] | 300 | 0 = Auto 1 = 1200 2 = 9600 3 = 19200 ... |  | Attr | York RTU.System Controllers.Network | 31 | Operating Baud Rate | 8-1/MSTP Network Port | Active Baud Rate | FALSE |  |  | York RTU.System Controllers.Network.FC Comm Mode:Present Value <> Modbus Field Bus |  |  |  |  | Value |  |  | Views.Controller.Network | Operating Baud Rate | 1675 | 284 |  | Views.Controller.Network | OprBaudRate | 1709 | 354
Prop | Templates.Network | Baud Rate | 1675 | 285 | 7004 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | MSTPDL Baud Rate | 300 | [7 empty] | MSTPDL Baud Rate | 300 | [6 empty] | 300 | 0 = Auto 1 = 1200 2 = 9600 3 = 19200 ... |  | Attr | York RTU.System Controllers.Network | 31 | Baud Rate | 8-1/MSTP Network Port | Baud Rate Selection | FALSE |  |  | York RTU.System Controllers.Network.FC Comm Mode:Present Value <> Modbus Field Bus |  |  |  |  | Value |  |  | Views.Commissioning.Network Setup | Baud Rate | 1675 | 285 |  | Views.Commission.Network Setup | BaudRate | 1709 | 355
Prop | Templates.Network | Baud Rate | 1675 | 285 | 7004 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | MSTPDL Baud Rate | 300 | [7 empty] | MSTPDL Baud Rate | 300 | [6 empty] | 300 | 0 = Auto 1 = 1200 2 = 9600 3 = 19200 ... |  | Attr | York RTU.System Controllers.Network | 31 | Baud Rate | 8-1/MSTP Network Port | Baud Rate Selection | FALSE |  |  | York RTU.System Controllers.Network.FC Comm Mode:Present Value <> Modbus Field Bus |  |  |  |  | Value |  |  | Views.Controller.Network | Baud Rate | 1675 | 285 |  | Views.Controller.Network | BaudRate | 1709 | 355
Prop | Templates.Network | FC Comm Mode | 1675 | 496 | 7007 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | FC Bus Mode | 1222 | [7 empty] | FC Bus Mode | 1222 | [6 empty] | 1222 | 0 = Wired Field Bus 1 = Wireless Field Bus 2 = N2 Subordinate Field Bus 3 = Modbus Field Bus ... |  | Attr | York RTU.System Controllers.Network | 31 | FC Comm Mode | UCBapp | FC Bus Communication Mode | TRUE | [7 empty] | Value |  |  | Views.Commissioning.Network Setup | FC Comm Mode | 1675 | 496 |  | Views.Commission.Network Setup | FcBusMode | 1709 | 628
Prop | Templates.Network | FC Comm Mode | 1675 | 496 | 7007 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | FC Bus Mode | 1222 | [7 empty] | FC Bus Mode | 1222 | [6 empty] | 1222 | 0 = Wired Field Bus 1 = Wireless Field Bus 2 = N2 Subordinate Field Bus 3 = Modbus Field Bus ... |  | Attr | York RTU.System Controllers.Network | 31 | FC Comm Mode | UCBapp | FC Bus Communication Mode | TRUE | [7 empty] | Value |  |  | Views.Controller.Network | FC Comm Mode | 1675 | 496 |  | Views.Controller.Network | FcBusMode | 1709 | 628
Prop | Templates.Network | BACnet Encoding Type | 1675 | 847 | 7008 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | BACnet Encoding | 575 | [7 empty] | BACnet Encoding | 575 | [6 empty] | 575 | 0 = ISO 10646 (UCS-2) 1 = ANSI X3.4 (US-ASCII) 2 = Microsoft DBCS code page 932 (Japanese Shift JIS) 3 = ISO 10646 (UTF-8) |  | Attr | York RTU.System Controllers.Network | 31 | BACnet Encoding Type | UCBapp | BACnet Encoding Type | FALSE |  |  |  | MV:29934 |  |  |  | Value |  |  | Views.Commissioning.Network Setup | BACnet Encoding Type | 1675 | 847 |  | Views.Commission.Network Setup | EncodeType | 1709 | 668
Prop | Templates.Network | BACnet Encoding Type | 1675 | 847 | 7008 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | BACnet Encoding | 575 | [7 empty] | BACnet Encoding | 575 | [6 empty] | 575 | 0 = ISO 10646 (UCS-2) 1 = ANSI X3.4 (US-ASCII) 2 = Microsoft DBCS code page 932 (Japanese Shift JIS) 3 = ISO 10646 (UTF-8) |  | Attr | York RTU.System Controllers.Network | 31 | BACnet Encoding Type | UCBapp | BACnet Encoding Type | FALSE |  |  |  | MV:29934 |  |  |  | Value |  |  | Views.Controller.Network | BACnet Encoding Type | 1675 | 847 |  | Views.Controller.Network | EncodeType | 1709 | 668
Prop | Templates.Network | Radio Code Version | 1714 | 202 | 7009 | TRUE | FALSE | FALSE | 7 | String | [17 empty] | 30 |  |  |  |  | Attr | York RTU.System Controllers.Network | 31 | Radio Code Version | 8-1/ZIGBEE | Coprocessor Version | FALSE |  |  | UCBapp:FC Bus Communication Mode = Wireless Field Bus |  |  |  |  | Value |  |  | Views.Controller.Network | Radio Code Version | 1714 | 202 |  | Views.Controller.Network | Radio Code Version | 1714 | 202
Prop | Templates.Network | Active Channel | 1714 | 203 | 7010 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 |  | 507:95 | [5 empty] | 1s | 0 |  | 507:95 | [9 empty] | Attr | York RTU.System Controllers.Network | 31 | Active Channel | 8-1/ZIGBEE | Active Channel | FALSE |  |  | UCBapp:FC Bus Communication Mode = Wireless Field Bus |  |  |  |  | Value |  |  | Views.Controller.Network | Active Channel | 1714 | 203 |  | Views.Controller.Network | Active Channel | 1714 | 203
Prop | Templates.Network | Signal Strength | 1714 | 204 | 7011 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Wireless Signal Strength | 1223 | [7 empty] | Wireless Signal Strength | 1223 | [5 empty] | Signal Strength | 1223 | 0 = None 1 = Weak 2 = Average 3 = Strong |  | Attr | York RTU.System Controllers.Network | 31 | Signal Strength | 8-1/ZIGBEE | RSSI Value | FALSE |  |  | UCBapp:FC Bus Communication Mode = Wireless Field Bus |  |  |  |  | Value |  |  | Views.Controller.Network | Signal Strength | 1714 | 204 |  | Views.Controller.Network | Signal Strength | 1714 | 204
Prop | Templates.Network | Connection Status | 1714 | 205 | 7012 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Radio Status | 1236 | [7 empty] | Radio Status | 1236 | [6 empty] | 1236 | 0 = Offline 1 = Not Associated 2 = Online 3 = Radio Processor Fault |  | Attr | York RTU.System Controllers.Network | 31 | Connection Status | 8-1/ZIGBEE | Radio Reliability | FALSE |  |  | UCBapp:FC Bus Communication Mode = Wireless Field Bus |  |  |  |  | Value |  |  | Views.Controller.Network | Connection Status | 1714 | 205 |  | Views.Controller.Network | Connection Status | 1714 | 205
Prop | Templates.Network | Network State | 1714 | 206 | 7013 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Wireless Status | 2513 | [7 empty] | Wireless Status | 2513 | [5 empty] | Network Status | 2513 | 0 = Normal 1 = Lost Coordinator 2 = Network Reforming 3 = Single Neighbor ... |  | Attr | York RTU.System Controllers.Network | 31 | Network State | 8-1/ZIGBEE | Network Status | FALSE |  |  | UCBapp:FC Bus Communication Mode = Wireless Field Bus |  |  |  |  | Value |  |  | Views.Controller.Network | Network State | 1714 | 206 |  | Views.Controller.Network | Network State | 1714 | 206
Prop | Templates.Network | IEEE Address | 1714 | 207 | 7014 | TRUE | FALSE | FALSE | 6 | OctetString | [22 empty] | Attr | York RTU.System Controllers.Network | 31 | IEEE Address | 8-1/ZIGBEE | IEEE Extended Address | FALSE |  |  | UCBapp:FC Bus Communication Mode = Wireless Field Bus
Prop | Templates.Network | Short Address | 1714 | 208 | 7015 | TRUE | FALSE | FALSE | 2 | UnsignedLong | 1s | 6 |  | 507:95 | [5 empty] | 1s | 0 |  | 507:95 | [9 empty] | Attr | York RTU.System Controllers.Network | 31 | Short Address | 8-1/ZIGBEE | JCI MAC Address | FALSE |  |  | UCBapp:FC Bus Communication Mode = Wireless Field Bus |  |  |  |  | Value |  |  | Views.Controller.Network | Short Address | 1714 | 208 |  | Views.Controller.Network | Short Address | 1714 | 208
Prop | Templates.Network | Lost Coordinator Counter | 1714 | 209 | 7016 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 |  | 507:95 | [5 empty] | 1s | 0 |  | 507:95 | [9 empty] | Attr | York RTU.System Controllers.Network | 31 | Lost Coordinator Counter | 8-1/ZIGBEE | Channels Scanned | FALSE |  |  | UCBapp:FC Bus Communication Mode = Wireless Field Bus
Prop | Templates.Network | Low Memory Counter | 1714 | 210 | 7017 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 |  | 507:95 | [5 empty] | 1s | 0 |  | 507:95 | [9 empty] | Attr | York RTU.System Controllers.Network | 31 | Low Memory Counter | 8-1/ZIGBEE | Received Dropped No Memory | FALSE |  |  | UCBapp:FC Bus Communication Mode = Wireless Field Bus
Prop | Templates.Network | Dropped Message Counter | 1714 | 211 | 7018 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 |  | 507:95 | [5 empty] | 1s | 0 |  | 507:95 | [9 empty] | Attr | York RTU.System Controllers.Network | 31 | Dropped Message Counter | 8-1/ZIGBEE | No ACK Count | FALSE |  |  | UCBapp:FC Bus Communication Mode = Wireless Field Bus
Prop | Templates.Network | Baud Rate | 1675 | 285 | 7019 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Baud Rate | 121 | [7 empty] | Baud Rate | 121 | [6 empty] | 121 | 0 = 9600 1 = 19200 2 = 38400 3 = 57600 4 = 115200 | The is actually the MODBUS baud rate | Attr | York RTU.System Controllers.Network | 31 | Baud Rate | 8-1/247_1 | Baud Rate | FALSE |  |  | York RTU.System Controllers.Network.FC Comm Mode:Present Value = Modbus Field Bus |  |  |  |  | Value |  |  | Views.Controller.Network | Baud Rate | 1675 | 285 |  | Views.Controller.Network | BaudRate | 1709 | 355
Prop | Templates.Network | Parity | 1675 | 1594 | 7020 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Pager Parity | 430 | [7 empty] | Pager Parity | 430 | [6 empty] | 430 | 0 = None 1 = Odd 2 = Even 3 = Mark 4 = Space | The is actually the MODBUS Parity | Attr | York RTU.System Controllers.Network | 31 | Parity | 8-1/247_1 | Parity | FALSE |  |  | York RTU.System Controllers.Network.FC Comm Mode:Present Value = Modbus Field Bus |  |  |  |  | Value |  |  | Views.Controller.Network | Parity | 1675 | 1594 |  | Views.Controller.Network | Parity | 1709 | 703
Prop | Templates.Network | Stop Bits | 1675 | 1595 | 7021 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Stopbits | 124 | [7 empty] | Stopbits | 124 | [6 empty] | 124 | 0 = 1 1 = 1.5 2 = 2 | The is actually the MODBUS Stop Bits | Attr | York RTU.System Controllers.Network | 31 | Stop Bits | 8-1/247_1 | Stop Bits | FALSE |  |  | York RTU.System Controllers.Network.FC Comm Mode:Present Value = Modbus Field Bus |  |  |  |  | Value |  |  | Views.Controller.Network | Stop Bits | 1675 | 1595 |  | Views.Controller.Network | StopBits | 1709 | 704
Tmpl | Templates.Control Board | [31 empty] | Model | York RTU.System Controllers.UCB | 32
Prop | Templates.Control Board | Firmware Main Version | 1675 | 287 | 7000 | TRUE | FALSE | FALSE | 7 | String | [17 empty] | 30 |  |  |  |  | Attr | York RTU.System Controllers.UCB | 32 | Firmware Main Version | UCBapp | Firmware Version | FALSE | [7 empty] | Value |  |  | Views.Controller.Firmware.UCB | Firmware Main Version | 1675 | 287 |  | Views.Controller.Firm.UCB | UCBMainVer | 1709 | 357
Prop | Templates.Control Board | Application Version | 1675 | 288 | 7001 | TRUE | FALSE | FALSE | 7 | String | [17 empty] | 30 |  |  |  |  | Attr | York RTU.System Controllers.UCB | 32 | Application Version | 8-1/Matlab Interface | Application SW Revision | FALSE | [7 empty] | Value |  |  | Views.Controller.Firmware.UCB | Application Version | 1675 | 288 |  | Views.Controller.Firm.UCB | UCBAppVer | 1709 | 358
Prop | Templates.Control Board | Board Communication Status | 1675 | 289 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | EIO Connection Status | 1662 | [7 empty] | EIO Connection Status | 1662 | [6 empty] | 1662 | 0 = Not Present 1 = Offline 2 = Online |  | Attr | York RTU.System Controllers.UCB | 32 | Board Communication Status | EM Variable: 2 |  | FALSE
Prop | Templates.Control Board | Hardware Version | 1675 | 290 | 7003 | TRUE | FALSE | FALSE | 7 | String | [17 empty] | 30 |  |  |  |  | Attr | York RTU.System Controllers.UCB | 32 | Hardware Version | UCBapp | Hardware Version | FALSE | [7 empty] | Value |  |  | Views.Controller.Firmware.UCB | Hardware Version | 1675 | 290 |  | Views.Controller.Firm.UCB | UCBHardVer | 1709 | 360
Prop | Templates.Control Board | Calibration Data Fault | 1675 | 328 | 7004 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Yes/No | 1698 | [7 empty] | Yes/No | 1698 | [6 empty] | 1698 | 0 = Yes 1 = No |  | Attr | York RTU.System Controllers.UCB | 32 | Calibration Data Fault | 8-1/HARDWARE MANAGER | Calibration | FALSE
Tmpl | Templates.Control Board | [31 empty] | Model | York RTU.System Controllers.Econ | 33 | [6 empty] | York RTU.System Controllers.Econ Controller:Present Value <> Not Present
Prop | Templates.Control Board | Firmware Main Version | 1675 | 287 | 7000 | TRUE | FALSE | FALSE | 7 | String | [17 empty] | 30 |  |  |  |  | Attr | York RTU.System Controllers.Econ | 33 | Firmware Main Version | EconApp | Firmware Version | FALSE | [7 empty] | Value |  |  | Views.Controller.Firmware.Economizer | Firmware Main Version | 1675 | 287 |  | Views.Controller.Firm.Econ | EconMainVer | 1709 | 361
Prop | Templates.Control Board | Application Version | 1675 | 288 | 7001 | TRUE | FALSE | FALSE | 7 | String | [17 empty] | 30 |  |  |  |  | Attr | York RTU.System Controllers.Econ | 33 | Application Version | SE-ECO1001-0/Matlab Interface | Application SW Revision | FALSE | [7 empty] | Value |  |  | Views.Controller.Firmware.Economizer | Application Version | 1675 | 288 |  | Views.Controller.Firm.Econ | EconAppVer | 1709 | 362
Prop | Templates.Control Board | Board Communication Status | 1675 | 289 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | EIO Connection Status | 1662 | Not_Present | [6 empty] | EIO Connection Status | 1662 | [6 empty] | 1662 | 0 = Not Present 1 = Offline 2 = Online |  | Attr | York RTU.System Controllers.Econ | 33 | Board Communication Status | UCBapp.newUCB.Econ_Comm_Status | Present Value | FALSE
Prop | Templates.Control Board | Hardware Version | 1675 | 290 | 7003 | TRUE | FALSE | FALSE | 7 | String | [17 empty] | 30 |  |  |  |  | Attr | York RTU.System Controllers.Econ | 33 | Hardware Version | EconApp | Hardware Version | FALSE | [7 empty] | Value |  |  | Views.Controller.Firmware.Economizer | Hardware Version | 1675 | 290 |  | Views.Controller.Firm.Econ | EconHardVer | 1709 | 364
Prop | Templates.Control Board | Calibration Data Fault | 1675 | 328 | 7004 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Yes/No | 1698 | [7 empty] | Yes/No | 1698 | [6 empty] | 1698 | 0 = Yes 1 = No |  | Attr | York RTU.System Controllers.Econ | 33 | Calibration Data Fault | 8-1/Econ Hardware Manager | Calibration | FALSE
Tmpl | Templates.Control Board | [31 empty] | Model | York RTU.System Controllers.4Stage | 34 | [6 empty] | York RTU.System Controllers.4 Stage Controller:Present Value <> Not Present
Prop | Templates.Control Board | Firmware Main Version | 1675 | 287 | 7000 | TRUE | FALSE | FALSE | 7 | String | [17 empty] | 30 |  |  |  |  | Attr | York RTU.System Controllers.4Stage | 34 | Firmware Main Version | FourStageApp | Firmware Version | FALSE | [7 empty] | Value |  |  | Views.Controller.Firmware.4 Stage | Firmware Main Version | 1675 | 287 |  | Views.Controller.Firm.4 Stage | 4StgMainVer | 1709 | 365
Prop | Templates.Control Board | Application Version | 1675 | 288 | 7001 | TRUE | FALSE | FALSE | 7 | String | [17 empty] | 30 |  |  |  |  | Attr | York RTU.System Controllers.4Stage | 34 | Application Version | SE-SPU1004-07/Matlab Interface | Application SW Revision | FALSE | [7 empty] | Value |  |  | Views.Controller.Firmware.4 Stage | Application Version | 1675 | 288 |  | Views.Controller.Firm.4 Stage | 4StgAppVer | 1709 | 366
Prop | Templates.Control Board | Board Communication Status | 1675 | 289 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | EIO Connection Status | 1662 | Not_Present | [6 empty] | EIO Connection Status | 1662 | [6 empty] | 1662 | 0 = Not Present 1 = Offline 2 = Online |  | Attr | York RTU.System Controllers.4Stage | 34 | Board Communication Status | UCBapp.newUCB.Four_Stage_Comm_Status | Present Value | FALSE
Prop | Templates.Control Board | Hardware Version | 1675 | 290 | 7003 | TRUE | FALSE | FALSE | 7 | String | [17 empty] | 30 |  |  |  |  | Attr | York RTU.System Controllers.4Stage | 34 | Hardware Version | FourStageApp | Hardware Version | FALSE | [7 empty] | Value |  |  | Views.Controller.Firmware.4 Stage | Hardware Version | 1675 | 290 |  | Views.Controller.Firm.4 Stage | 4StgHardVer | 1709 | 368
Prop | Templates.Control Board | Calibration Data Fault | 1675 | 328 | 7004 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Yes/No | 1698 | [7 empty] | Yes/No | 1698 | [6 empty] | 1698 | 0 = Yes 1 = No |  | Attr | York RTU.System Controllers.4Stage | 34 | Calibration Data Fault | 8-1/4 Stage Hardware Manager | Calibration | FALSE
Tmpl | Templates.Control Board | [31 empty] | Model | York RTU.System Controllers.FDD Master | 35 | [6 empty] | York RTU.System Controllers.FDD Manager Controller:Present Value <> Not Present
Prop | Templates.Control Board | Firmware Main Version | 1675 | 287 | 7000 | TRUE | FALSE | FALSE | 7 | String | [17 empty] | 30 |  |  |  |  | Attr | York RTU.System Controllers.FDD Master | 35 | Firmware Main Version | FDDApp | Firmware Version | FALSE | [7 empty] | Value |  |  | Views.Controller.Firmware.FDD Manager | Firmware Main Version | 1675 | 287 |  | Views.Controller.Firm.FDD Manager | FDDMMainVer | 1709 | 369
Prop | Templates.Control Board | Application Version | 1675 | 288 | 7001 | TRUE | FALSE | FALSE | 7 | String | [17 empty] | 30 |  |  |  |  | Attr | York RTU.System Controllers.FDD Master | 35 | Application Version | SE-FDD1001-05/Matlab Interface | Application SW Revision | FALSE | [7 empty] | Value |  |  | Views.Controller.Firmware.FDD Manager | Application Version | 1675 | 288 |  | Views.Controller.Firm.FDD Manager | FDDMAppVer | 1709 | 370
Prop | Templates.Control Board | Board Communication Status | 1675 | 289 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | EIO Connection Status | 1662 | Not_Present | [6 empty] | EIO Connection Status | 1662 | [6 empty] | 1662 | 0 = Not Present 1 = Offline 2 = Online |  | Attr | York RTU.System Controllers.FDD Master | 35 | Board Communication Status | UCBapp.newUCB.FDD_Master_Comm_Status | Present Value | FALSE
Prop | Templates.Control Board | Hardware Version | 1675 | 290 | 7003 | TRUE | FALSE | FALSE | 7 | String | [17 empty] | 30 |  |  |  |  | Attr | York RTU.System Controllers.FDD Master | 35 | Hardware Version | FDDApp | Hardware Version | FALSE | [7 empty] | Value |  |  | Views.Controller.Firmware.FDD Manager | Hardware Version | 1675 | 290 |  | Views.Controller.Firm.FDD Manager | FDDMHardVer | 1709 | 372
Prop | Templates.Control Board | Calibration Data Fault | 1675 | 328 | 7004 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Yes/No | 1698 | [7 empty] | Yes/No | 1698 | [6 empty] | 1698 | 0 = Yes 1 = No |  | Attr | York RTU.System Controllers.FDD Master | 35 | Calibration Data Fault | 8-1/FDD Hardware Manager | Calibration | FALSE
Tmpl | Templates.Control Board | [31 empty] | Model | York RTU.System Controllers.FDD Slave | 36 | [6 empty] | York RTU.System Controllers.FDD Subordinate Controller:Present Value <> Not Present
Prop | Templates.Control Board | Firmware Main Version | 1675 | 287 | 7000 | TRUE | FALSE | FALSE | 7 | String | [17 empty] | 30 |  |  |  |  | Attr | York RTU.System Controllers.FDD Slave | 36 | Firmware Main Version | FDDsApp | Firmware Version | FALSE | [7 empty] | Value |  |  | Views.Controller.Firmware.FDD Subordinate | Firmware Main Version | 1675 | 287 |  | Views.Controller.Firm.FDD Subordinate | FDDSMainVer | 1709 | 373
Prop | Templates.Control Board | Application Version | 1675 | 288 | 7001 | TRUE | FALSE | FALSE | 7 | String | [17 empty] | 30 |  |  |  |  | Attr | York RTU.System Controllers.FDD Slave | 36 | Application Version | SE-FDD1001-06/Matlab Interface | Application SW Revision | FALSE | [7 empty] | Value |  |  | Views.Controller.Firmware.FDD Subordinate | Application Version | 1675 | 288 |  | Views.Controller.Firm.FDD Subordinate | FDDSAppVer | 1709 | 374
Prop | Templates.Control Board | Board Communication Status | 1675 | 289 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | EIO Connection Status | 1662 | Not_Present | [6 empty] | EIO Connection Status | 1662 | [6 empty] | 1662 | 0 = Not Present 1 = Offline 2 = Online |  | Attr | York RTU.System Controllers.FDD Slave | 36 | Board Communication Status | UCBapp.newUCB.FDD_Slave_Comm_Status | Present Value | FALSE
Prop | Templates.Control Board | Hardware Version | 1675 | 290 | 7003 | TRUE | FALSE | FALSE | 7 | String | [17 empty] | 30 |  |  |  |  | Attr | York RTU.System Controllers.FDD Slave | 36 | Hardware Version | FDDsApp | Hardware Version | FALSE | [7 empty] | Value |  |  | Views.Controller.Firmware.FDD Subordinate | Hardware Version | 1675 | 290 |  | Views.Controller.Firm.FDD Subordinate | FDDSHardVer | 1709 | 376
Prop | Templates.Control Board | Calibration Data Fault | 1675 | 328 | 7004 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Yes/No | 1698 | [7 empty] | Yes/No | 1698 | [6 empty] | 1698 | 0 = Yes 1 = No |  | Attr | York RTU.System Controllers.FDD Slave | 36 | Calibration Data Fault | 8-1/FDDS Hardware Manager | Calibration | FALSE
Tmpl | Templates.Heat Pump Control | [31 empty] | Model | York RTU.Heat Pump Control | 38
Prop | Templates.Heat Pump Control | Number of Heat Pump Stages Installed | 1675 | 380 | 7000 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 |  | 507:95 | 0 | 0 | 2 |  |  | 1s | 0 |  | 507:95 | 0 | 2 |  |  |  | Number of Heat Pump Stages |  |  |  | Attr | York RTU.Heat Pump Control | 38 | Number of Heat Pump Stages Installed | UCBapp.newUCB.Heat_Pump_Stages | Relinquish Default | TRUE |  |  |  | AV:29898 | HR:434 | ADF:185 |  | Value |  |  | Views.Commissioning.Options | Number of Heat Pump Stages Installed | 1675 | 380 |  | Views.Commission.Options | #HtPumpStgs | 1709 | 491
Prop | Templates.Heat Pump Control | Number of Heat Pump Stages Installed | 1675 | 380 | 7000 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 |  | 507:95 | 0 | 0 | 2 |  |  | 1s | 0 |  | 507:95 | 0 | 2 |  |  |  | Number of Heat Pump Stages |  |  |  | Attr | York RTU.Heat Pump Control | 38 | Number of Heat Pump Stages Installed | UCBapp.newUCB.Heat_Pump_Stages | Relinquish Default | TRUE |  |  |  | AV:29898 | HR:434 | ADF:185 |  | Value |  |  | Views.Details.Heat Pump | Number of Heat Pump Stages Installed | 1675 | 380 |  | Views.Details.HeatPmp | #HtPumpStgs | 1709 | 491
Prop | Templates.Heat Pump Control | Number of Heat Pump Stages Installed | 1675 | 380 | 7000 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 |  | 507:95 | 0 | 0 | 2 |  |  | 1s | 0 |  | 507:95 | 0 | 2 |  |  |  | Number of Heat Pump Stages |  |  |  | Attr | York RTU.Heat Pump Control | 38 | Number of Heat Pump Stages Installed | UCBapp.newUCB.Heat_Pump_Stages | Relinquish Default | TRUE |  |  |  | AV:29898 | HR:434 | ADF:185 |  | Value |  |  | Views.Commissioning.Quick Start | Number of Heat Pump Stages Installed | 1675 | 380 |  | Views.Commission.Quick Start | #HtPumpStgs | 1709 | 491
Prop | Templates.Heat Pump Control | Test Defrost Enable | 1675 | 382 | 7002 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | False/True | 1701 | Disable | [6 empty] | False/True | 1701 | [6 empty] | 1701 | 0 = False 1 = True |  | Attr | York RTU.Heat Pump Control | 38 | Test Defrost Enable | UCBapp.newUCB.Test_Defrost_Enable | Relinquish Default | FALSE | [7 empty] | Value |  |  | Views.Details.Heat Pump | Test Defrost Enable | 1675 | 382 |  | Views.Details.HeatPmp | TestDefrostEnable | 1709 | 493
Prop | Templates.Heat Pump Control | Compressor Delay Enable | 1675 | 383 | 7003 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | False/True | 1701 | FALSE | [6 empty] | False/True | 1701 | [6 empty] | 1701 | 0 = False 1 = True |  | Attr | York RTU.Heat Pump Control | 38 | Compressor Delay Enable | UCBapp.newUCB.Compressor_Delay_Enable | Relinquish Default | FALSE |  |  | York RTU.Heat Pump Control.Dual Fuel HP Enable:Present Value <> Enable |  |  |  |  | Value |  |  | Views.Details.Heat Pump | Compressor Delay Enable | 1675 | 383 |  | Views.Details.HeatPmp | CompDelayEnable | 1709 | 494
Prop | Templates.Heat Pump Control | Defrost Curve Selection | 1675 | 384 | 7004 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | SE RTU Defrost Curves | 1665 | Curve_1 | [6 empty] | SE RTU Defrost Curves | 1665 | [6 empty] | 1665 | 0 = Curve 1 1 = Curve 2 2 = Curve 3 3 = Curve 4 ... |  | Attr | York RTU.Heat Pump Control | 38 | Defrost Curve Selection | UCBapp.newUCB.Defrost_Curve_Selection | Relinquish Default | FALSE |  |  |  | MV:29899 | HR:117 | ADI:81 |  | Value |  |  | Views.Details.Heat Pump | Defrost Curve Selection | 1675 | 384 |  | Views.Details.HeatPmp | DefrostCurveSel | 1709 | 495
Prop | Templates.Heat Pump Control | Defrost State | 1675 | 385 | 7005 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Defrost State | 1645 | Defrost_Off | [6 empty] | Defrost State | 1645 | [6 empty] | 1645 | 0 = Defrost Off 1 = Normal Defrost 2 = Test Defrost 3 = Comp Delay Exit Defrost ... |  | Attr | York RTU.Heat Pump Control | 38 | Defrost State | UCBapp.newUCB.Defrost_State | Present Value | FALSE |  |  |  | MV:29920
Prop | Templates.Heat Pump Control | Defrost Terminate Curve 6 | 1675 | 386 | 7006 | TRUE | TRUE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | 50 | 30 | 80 |  |  | 10ths | 0 | deg C | 507:62 | -1 | 27 | [7 empty] | Attr | York RTU.Heat Pump Control | 38 | Defrost Terminate Curve 6 | UCBapp.newUCB.Defrost_Terminate_Curve_6 | Relinquish Default | FALSE
Prop | Templates.Heat Pump Control | Initiate Curve 6 | 1675 | 387 | 7007 | TRUE | TRUE | FALSE | 4 | Float | 1000ths | 3 |  | 507:95 | 0.856 | 0.25 | 1.5 |  |  | 1000ths | 0 |  | 507:95 | 0.25 | 1.5 | [7 empty] | Attr | York RTU.Heat Pump Control | 38 | Initiate Curve 6 | UCBapp.newUCB.Initiate_Curve_6 | Relinquish Default | FALSE
Prop | Templates.Heat Pump Control | Initiate Curve Intercept 6 | 1675 | 388 | 7008 | TRUE | TRUE | FALSE | 4 | Float | 1000ths | 3 |  | 507:95 | -5.593 | -12 | 12 |  |  | 1000ths | 0 |  | 507:95 | -12 | 12 | [7 empty] | Attr | York RTU.Heat Pump Control | 38 | Initiate Curve Intercept 6 | UCBapp.newUCB.Initiate_Curve_Intercept_6 | Relinquish Default | FALSE
Prop | Templates.Heat Pump Control | Defrost Inhibit Time 6 | 1675 | 389 | 7009 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | minutes | 507:72 | 30 | 30 | 120 |  |  | 1s | 0 | minutes | 507:72 | 30 | 120 | [7 empty] | Attr | York RTU.Heat Pump Control | 38 | Defrost Inhibit Time 6 | UCBapp.newUCB.Defrost_Inhibit_Time_6 | Relinquish Default | FALSE
Prop | Templates.Heat Pump Control | Max Defrost Cycle Time 6 | 1675 | 390 | 7010 | TRUE | TRUE | FALSE | 4 | Float | 10ths | 5 | minutes | 507:72 | 10 | 6 | 15 |  |  | 10ths | 0 | minutes | 507:72 | 6 | 15 | [7 empty] | Attr | York RTU.Heat Pump Control | 38 | Max Defrost Cycle Time 6 | UCBapp.newUCB.Max_Defrost_Cycle_Time_6 | Relinquish Default | FALSE
Prop | Templates.Heat Pump Control | Reversing Valve | 1675 | 482 | 7011 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [6 empty] | 647 | 0 = Off 1 = On |  | Attr | York RTU.Heat Pump Control | 38 | Reversing Valve | UCBapp.newUCB.HTG1ORRVLV_C | Present Value | FALSE |  |  |  | MV:29900 | IR:366 | BO:13 |  | Value |  |  | Views.Details.Heat Pump | Reversing Valve | 1675 | 482 |  | Views.Details.HeatPmp | RevVlv | 1709 | 613
Prop | Templates.Heat Pump Control | Auxiliary Heat | 1675 | 483 | 7012 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Off/On | 647 | N/A | [6 empty] | Off/On | 647 | [5 empty] | Supplemental Heat Stage 1 | 647 | 0 = Off 1 = On |  | Attr | York RTU.Heat Pump Control | 38 | Auxiliary Heat | UCBapp.newUCB.HTG2ORAUX_C | Present Value | FALSE |  |  |  | MV:29901 | IR:367 | BO:14 |  | Value |  |  | Views.Details.Heat Pump | Auxiliary Heat | 1675 | 483 |  | Views.Details.HeatPmp | AuxHtg | 1709 | 614
Prop | Templates.Heat Pump Control | Mode | 1675 | 484 | 7013 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Heating/Cooling | 350 | N/A | [6 empty] | Heating/Cooling | 350 | [6 empty] | 350 | 0 = Heating 1 = Cooling |  | Attr | York RTU.Heat Pump Control | 38 | Mode | UCBapp.newUCB.HTG1ORRVLV_C | Present Value | FALSE |  |  |  | MV:29902 | IR:368 | ADI:83 |  | Value |  |  | Views.Details.Heat Pump | Mode | 1675 | 484 |  | Views.Details.HeatPmp | Mode | 1709 | 615
Prop | Templates.Heat Pump Control | Max Defrost Cycle Time 6 | 1675 | 390 | 7014 | TRUE | TRUE | FALSE | 4 | Float | 10ths | 5 | deg F | 507:64 | 55 | 0 | 99 |  |  | 10ths | 0 | deg C | 507:62 | -18 | 37 | [7 empty] | Attr | York RTU.Heat Pump Control | 38 | Max Defrost Cycle Time 6 | UCBapp.newUCB.Def_Termination_Max_Curve_6 | Relinquish Default | FALSE
Prop | Templates.Heat Pump Control | OAT Defrost Permission | 1714 | 227 | 7015 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 50 | 45 | 60 |  |  | 1s | 0 | deg C | 507:62 | 7 | 16 | [7 empty] | Attr | York RTU.Heat Pump Control | 38 | OAT Defrost Permission | UCBapp.newUCB.Defrost_OAT_Inhibit | Relinquish Default | FALSE | [7 empty] | Value |  |  | Views.Details.Heat Pump | OAT Defrost Permission | 1714 | 227 |  | Views.Details.HeatPmp | OATDefPerm | 1709 | 724
Prop | Templates.Heat Pump Control | Defrost | 1675 | 1529 | 7016 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Normal/Alarm | 374 | Normal | [6 empty] | Normal/Alarm | 374 | [6 empty] | 374 | 0 = Normal 1 = Alarm | No Defrost Alarm | Attr | York RTU.Heat Pump Control | 38 | Defrost | UCBapp.newUCB.No_Defrost_Alarm | Present Value | FALSE
Prop | Templates.Heat Pump Control | OAT Heat Pump Cutout | 1714 | 273 | 7017 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 20 | -20 | 50 |  |  | 1s | 0 | deg C | 507:62 | -29 | 10 | [7 empty] | Attr | York RTU.Heat Pump Control | 38 | OAT Heat Pump Cutout | UCBapp.newUCB.OAT_Heat_Pump_Cutout | Relinquish Default | FALSE |  |  | York RTU.Heat Pump Control.Dual Fuel HP Enable:Present Value <> Enable | AV:30132 | HR:882 | ADF:216 |  | Value |  |  | Views.Details.Heat Pump | OAT Heat Pump Cutout | 1714 | 273 |  | Views.Details.HeatPmp | OATHPCutout | 1709 | 780
Prop | Templates.Heat Pump Control | Dual Fuel HP Enable | 1714 | 283 | 7018 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Disable/Enable | 658 | Disable | [6 empty] | Disable/Enable | 658 | [6 empty] | 658 | 0 = Disable 1 = Enable |  | Attr | York RTU.Heat Pump Control | 38 | Dual Fuel HP Enable | UCBapp.newUCB.Dual_Fuel_HP_Enable | Relinquish Default | TRUE |  |  | York RTU.Dual Fuel HP Enable:Present Value = Enable |  |  |  |  | Value |  |  | Views.Details.Heat Pump | Dual Fuel HP Enable | 1714 | 283 |  | Views.Details.HeatPmp | DualFuelHP-En | 1709 | 794
Prop | Templates.Heat Pump Control | Dual Fuel OAT HP Cutout | 1714 | 285 | 7019 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 40 | 0 | 65 |  |  | 1s | 0 | deg C | 507:62 | -18 | 18 | [7 empty] | Attr | York RTU.Heat Pump Control | 38 | Dual Fuel OAT HP Cutout | UCBapp.newUCB.Dual_Fuel_HP_Balance_Point | Relinquish Default | FALSE |  |  | York RTU.Heat Pump Control.Dual Fuel HP Enable:Present Value = Enable | AV:30151 | HR:896 | ADF:230 |  | Value |  |  | Views.Details.Heat Pump | Dual Fuel OAT HP Cutout | 1714 | 285 |  | Views.Details.HeatPmp | DualFuelOATHPCutout | 1709 | 796
Prop | Templates.Heat Pump Control | Reversing Valve Delay | 1714 | 284 | 7020 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | seconds | 507:73 | 0 | 0 | 60 |  |  | 1s | 0 | seconds | 507:73 | 0 | 60 | [7 empty] | Attr | York RTU.Heat Pump Control | 38 | Reversing Valve Delay | UCBapp.newUCB.Reversing_Valve_Delay | Relinquish Default | FALSE |  |  | York RTU.Heat Pump Control.Dual Fuel HP Enable:Present Value = Enable |  |  |  |  | Value |  |  | Views.Details.Heat Pump | Reversing Valve Delay | 1714 | 284 |  | Views.Details.HeatPmp | RevVlvDelay | 1709 | 795
Prop | Templates.Heat Pump Control | Reversing Valve Delay | 1714 | 284 | 7021 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | seconds | 507:73 | 0 | 0 | 60 |  |  | 1s | 0 | seconds | 507:73 | 0 | 60 | [7 empty] | Attr | York RTU.Heat Pump Control | 38 | Reversing Valve Delay | UCBapp.newUCB.Reversing_Valve_Delay | Relinquish Default | FALSE
Tmpl | Templates.CCS | [31 empty] | Model | York RTU.CCS | 39 | [6 empty] | York RTU.CCS Online:Present Value = Yes
Prop | Templates.CCS | Warmer/Cooler Adjust Enable | 1675 | 457 | 7000 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Disable | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.CCS | 39 | Warmer/Cooler Adjust Enable | UCBapp.newUCB.WarmerCooler_Adjust_Enable | Relinquish Default | FALSE
Prop | Templates.CCS | Heat Cool Mode | 1675 | 458 | 7001 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Heat Cool Mode | 1243 | Off | [6 empty] | Heat Cool Mode | 1243 | [6 empty] | 1243 | 0 = Heat 1 = Cool 2 = Fan Only 3 = Balancing ... |  | Attr | York RTU.CCS | 39 | Heat Cool Mode | UCBapp.newUCB.HeatCool_Mode | Relinquish Default | FALSE
Prop | Templates.CCS | Operating State | 1675 | 459 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Heat Cool Mode | 1243 | Heat | [6 empty] | Heat Cool Mode | 1243 | [6 empty] | 1243 | 0 = Heat 1 = Cool 2 = Fan Only 3 = Balancing ... |  | Attr | York RTU.CCS | 39 | Operating State | UCBapp.newUCB.Operating_Status | Present Value | FALSE | [7 empty] | Value |  |  | Views.Details.Verasys | Operating State | 1675 | 459 |  | Views.Details.Verasys | Operating State | 1675 | 459
Prop | Templates.CCS | Effective Y4 Call | 1675 | 460 | 7003 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Off | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.CCS | 39 | Effective Y4 Call | UCBapp.newUCB.Y4 | Present Value | FALSE
Prop | Templates.CCS | Effective W3 Call | 1675 | 461 | 7004 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Off | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.CCS | 39 | Effective W3 Call | UCBapp.newUCB.W3 | Present Value | FALSE
Prop | Templates.CCS | Emergency Heat Only | 1675 | 463 | 7006 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | No | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.CCS | 39 | Emergency Heat Only | UCBapp.newUCB.Emergency_Heat_Only | Present Value | FALSE
Prop | Templates.CCS | Active Mode | 1675 | 464 | 7007 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Heating/Cooling | 350 | Heating | [6 empty] | Heating/Cooling | 350 | [5 empty] | Active Mode | 350 | 0 = Heating 1 = Cooling |  | Attr | York RTU.CCS | 39 | Active Mode | UCBapp.newUCB.Active_Mode | Present Value | FALSE
Prop | Templates.CCS | Control Mode | 1675 | 465 | 7008 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Control Mode | 1241 | Auto | [6 empty] | Control Mode | 1241 | [5 empty] | System Mode | 1241 | 0 = Heat 1 = Cool 2 = Fan Only 3 = Auto 4 = Off |  | Attr | York RTU.CCS | 39 | Control Mode | UCBapp.newUCB.Control_Mode | Relinquish Default | FALSE
Prop | Templates.CCS | Standby Cooling Setpoint | 1675 | 468 | 7011 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 74 | 45 | 98 |  |  | 1s | 0 | deg C | 507:62 | 7 | 36 |  |  |  | Standby Cooling Setpoint |  |  |  | Attr | York RTU.CCS | 39 | Standby Cooling Setpoint | UCBapp.newUCB.Standby_Cooling_Setpoint | Relinquish Default | FALSE
Prop | Templates.CCS | Standby Heating Setpoint | 1675 | 469 | 7012 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 66 | 45 | 98 |  |  | 1s | 0 | deg C | 507:62 | 7 | 36 |  |  |  | Standby Heating Setpoint |  |  |  | Attr | York RTU.CCS | 39 | Standby Heating Setpoint | UCBapp.newUCB.Standby_Heating_Setpoint | Relinquish Default | FALSE
Prop | Templates.CCS | CCS Temp Occ Status | 1675 | 470 | 7013 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Occupied | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.CCS | 39 | CCS Temp Occ Status | UCBapp.newUCB.CCS_Temp_Occ_Status | Relinquish Default | FALSE
Prop | Templates.CCS | Fan Speed High | 1675 | 471 | 7014 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 100 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.CCS | 39 | Fan Speed High | EconApp.Econ.Fan Speed High | Relinquish Default | FALSE |  |  | York RTU.System Controllers.Econ Controller:Present Value <> Not Present
Prop | Templates.CCS | Fan Speed Low | 1675 | 472 | 7015 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 50 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.CCS | 39 | Fan Speed Low | EconApp.Econ.Fan Speed Low | Relinquish Default | FALSE |  |  | York RTU.System Controllers.Econ Controller:Present Value <> Not Present
Prop | Templates.CCS | Power Fail Restart Enable | 1675 | 473 | 7016 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Enable | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.CCS | 39 | Power Fail Restart Enable | UCBapp.newUCB.Power_Fail_Restart_Enable | Relinquish Default | FALSE
Prop | Templates.CCS | VFD Econ Min Pos Reset | 1675 | 474 | 7017 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Yes | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.CCS | 39 | VFD Econ Min Pos Reset | EconApp.Econ.VFD Econ Min Pos Reset | Relinquish Default | FALSE |  |  | York RTU.System Controllers.Econ Controller:Present Value <> Not Present
Prop | Templates.CCS | Plug and Play Occupancy Request | 1675 | 475 | 7018 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Occ Sensor | 344 | Occupied | [6 empty] | Occ Sensor | 344 | [6 empty] | 344 | 0 = Occupied 1 = UnOccupied 2 = Not Set |  | Attr | York RTU.CCS | 39 | Plug and Play Occupancy Request | UCBapp.newUCB.NSPNP_OCC_REQ | Present Value | FALSE
Prop | Templates.CCS | CCS Fan Request | 1675 | 476 | 7019 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | Off | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.CCS | 39 | CCS Fan Request | UCBapp.newUCB.Eff_Fan_Call_High_Priority_In | Relinquish Default | FALSE
Prop | Templates.CCS | COBP Supply Air Temperature Setpoint | 1675 | 601 | 7020 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 110 | 40 | 180 |  |  | 1s | 0 | deg C | 507:62 | 4 | 82 | [7 empty] | Attr | York RTU.CCS | 39 | COBP Supply Air Temperature Setpoint | UCBapp.newUCB.COBP_SAT_SP | Relinquish Default | FALSE
Prop | Templates.CCS | VZC Online | 1675 | 1689 | 7021 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | No | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.CCS | 39 | VZC Online | UCBapp.newUCB.CCS | Present Value | FALSE | [7 empty] | Value |  |  | Views.Details.Verasys | VZC Online | 1675 | 1689 |  | Views.Details.Verasys | VZC Online | 1675 | 1689
Prop | Templates.CCS | COBP Mode | 1709 | 778 | 7022 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | Heat Cool Mode | 1243 | Off | [6 empty] | Heat Cool Mode | 1243 | [6 empty] | 1243 | 0 = Heat 1 = Cool 2 = Fan Only 3 = Balancing ... |  | Attr | York RTU.CCS | 39 | COBP Mode | UCBapp.newUCB.HeatCool_Mode | Present Value | FALSE |  |  | York RTU.Rooftop Controller Type:Present Value = Changeover Bypass |  |  |  |  | Value |  |  | Views.Details.Verasys | COBP Mode | 1709 | 778 |  | Views.Details.Verasys | COBP Mode | 1709 | 778
Prop | Templates.CCS | COBP Supply Air Temperature Setpoint | 1675 | 601 | 7023 | TRUE | FALSE | FALSE | 4 | Float | 1s | 6 | deg F | 507:64 | 110 |  |  |  |  | 1s | 0 | deg C | 507:62 | [9 empty] | Attr | York RTU.CCS | 39 | COBP Supply Air Temperature Setpoint | UCBapp.newUCB.COBP_SAT_SP | Present Value | FALSE |  |  | York RTU.Rooftop Controller Type:Present Value = Changeover Bypass |  |  |  |  | Value |  |  | Views.Details.Verasys | COBP Supply Air Temperature Setpoint | 1675 | 601 |  | Views.Details.Verasys | COBP SAT SP | 1709 | 779
Tmpl | Templates.PV | [30 empty] | This area is used to store values which must be persisted through a provisioning process. | Model | York RTU.PV | 40
Prop | Templates.PV | Temperature Sensor 1 | 1675 | 688 | 7000 | TRUE | TRUE | FALSE | 4 | Float | 1000ths | 3 | Custom | 507:272 |  | 0 | 1000000 |  |  | 1000ths | 0 | Custom | 507:272 | 0 | 1000000 | [6 empty] | Used for Optimal Start parameter | Attr | York RTU.PV | 40 | Temperature Sensor 1 | 8-1/SE_RTU2_Optimal_Start_Override.Enable.pMaxClg11 | Relinquish Default | FALSE
Prop | Templates.PV | Temperature Sensor 2 | 1675 | 689 | 7001 | TRUE | TRUE | FALSE | 4 | Float | 1000ths | 3 | Custom | 507:272 |  | 0 | 1000000 |  |  | 1000ths | 0 | Custom | 507:272 | 0 | 1000000 | [6 empty] | Used for Optimal Start parameter | Attr | York RTU.PV | 40 | Temperature Sensor 2 | 8-1/SE_RTU2_Optimal_Start_Override.Enable.pMaxClg12 | Relinquish Default | FALSE
Prop | Templates.PV | Temperature Sensor 3 | 1675 | 690 | 7002 | TRUE | TRUE | FALSE | 4 | Float | 1000ths | 3 | Custom | 507:272 |  | 0 | 1000000 |  |  | 1000ths | 0 | Custom | 507:272 | 0 | 1000000 | [6 empty] | Used for Optimal Start parameter | Attr | York RTU.PV | 40 | Temperature Sensor 3 | 8-1/SE_RTU2_Optimal_Start_Override.Enable.pMaxClg22 | Relinquish Default | FALSE
Prop | Templates.PV | Temperature Sensor 4 | 1675 | 691 | 7003 | TRUE | TRUE | FALSE | 4 | Float | 1000ths | 3 | Custom | 507:272 |  | 0 | 1000000 |  |  | 1000ths | 0 | Custom | 507:272 | 0 | 1000000 | [6 empty] | Used for Optimal Start parameter | Attr | York RTU.PV | 40 | Temperature Sensor 4 | 8-1/SE_RTU2_Optimal_Start_Override.Enable.wClg1 | Relinquish Default | FALSE
Prop | Templates.PV | Temperature Sensor 5 | 1675 | 692 | 7004 | TRUE | TRUE | FALSE | 4 | Float | 1000ths | 3 | Custom | 507:272 |  | 0 | 1000000 |  |  | 1000ths | 0 | Custom | 507:272 | 0 | 1000000 | [6 empty] | Used for Optimal Start parameter | Attr | York RTU.PV | 40 | Temperature Sensor 5 | 8-1/SE_RTU2_Optimal_Start_Override.Enable.wClg2 | Relinquish Default | FALSE
Prop | Templates.PV | Temperature Sensor 6 | 1675 | 693 | 7005 | TRUE | TRUE | FALSE | 4 | Float | 1000ths | 3 | Custom | 507:272 |  | 0 | 1000000 |  |  | 1000ths | 0 | Custom | 507:272 | 0 | 1000000 | [6 empty] | Used for Optimal Start parameter | Attr | York RTU.PV | 40 | Temperature Sensor 6 | 8-1/SE_RTU2_Optimal_Start_Override.Enable.pMatHtg11 | Relinquish Default | FALSE
Prop | Templates.PV | Temperature Sensor 7 | 1675 | 694 | 7006 | TRUE | TRUE | FALSE | 4 | Float | 1000ths | 3 | Custom | 507:272 |  | 0 | 1000000 |  |  | 1000ths | 0 | Custom | 507:272 | 0 | 1000000 | [6 empty] | Used for Optimal Start parameter | Attr | York RTU.PV | 40 | Temperature Sensor 7 | 8-1/SE_RTU2_Optimal_Start_Override.Enable.pMatHtg12 | Relinquish Default | FALSE
Prop | Templates.PV | Temperature Sensor 8 | 1675 | 695 | 7007 | TRUE | TRUE | FALSE | 4 | Float | 1000ths | 3 | Custom | 507:272 |  | 0 | 1000000 |  |  | 1000ths | 0 | Custom | 507:272 | 0 | 1000000 | [6 empty] | Used for Optimal Start parameter | Attr | York RTU.PV | 40 | Temperature Sensor 8 | 8-1/SE_RTU2_Optimal_Start_Override.Enable.pMatHtg22 | Relinquish Default | FALSE
Prop | Templates.PV | Temperature Sensor 9 | 1675 | 696 | 7008 | TRUE | TRUE | FALSE | 4 | Float | 1000ths | 3 | Custom | 507:272 |  | 0 | 1000000 |  |  | 1000ths | 0 | Custom | 507:272 | 0 | 1000000 | [6 empty] | Used for Optimal Start parameter | Attr | York RTU.PV | 40 | Temperature Sensor 9 | 8-1/SE_RTU2_Optimal_Start_Override.Enable.wHtg1 | Relinquish Default | FALSE
Prop | Templates.PV | Temperature Sensor 10 | 1675 | 697 | 7009 | TRUE | TRUE | FALSE | 4 | Float | 1000ths | 3 | Custom | 507:272 |  | 0 | 1000000 |  |  | 1000ths | 0 | Custom | 507:272 | 0 | 1000000 | [6 empty] | Used for Optimal Start parameter | Attr | York RTU.PV | 40 | Temperature Sensor 10 | 8-1/SE_RTU2_Optimal_Start_Override.Enable.wHtg2 | Relinquish Default | FALSE
Prop | Templates.PV | Temperature Sensor 11 | 1675 | 698 | 7010 | TRUE | TRUE | FALSE | 4 | Float | 1000ths | 3 | Custom | 507:272 |  | 0 | 1000000 |  |  | 1000ths | 0 | Custom | 507:272 | 0 | 1000000 | [6 empty] | Used for Optimal Start parameter | Attr | York RTU.PV | 40 | Temperature Sensor 11 | 8-1/SE_RTU2_Optimal_Start_Override.Enable.timeAtStartup | Relinquish Default | FALSE
Prop | Templates.PV | Temperature Sensor 12 | 1675 | 699 | 7011 | TRUE | TRUE | FALSE | 4 | Float | 1000ths | 3 | Custom | 507:272 |  | 0 | 1000000 |  |  | 1000ths | 0 | Custom | 507:272 | 0 | 1000000 | [6 empty] | Used for Optimal Start parameter | Attr | York RTU.PV | 40 | Temperature Sensor 12 | 8-1/SE_RTU2_Optimal_Start_Override.Enable.roomTempAtStartup | Relinquish Default | FALSE
Prop | Templates.PV | Temperature Sensor 13 | 1675 | 700 | 7012 | TRUE | TRUE | FALSE | 4 | Float | 1000ths | 3 | Custom | 507:272 |  | 0 | 1000000 |  |  | 1000ths | 0 | Custom | 507:272 | 0 | 1000000 | [6 empty] | Used for Optimal Start parameter | Attr | York RTU.PV | 40 | Temperature Sensor 13 | 8-1/SE_RTU2_Optimal_Start_Override.Enable.uHtgEWMA | Relinquish Default | FALSE
Prop | Templates.PV | Temperature Sensor 14 | 1675 | 701 | 7013 | TRUE | TRUE | FALSE | 4 | Float | 1000ths | 3 | Custom | 507:272 |  | 0 | 1000000 |  |  | 1000ths | 0 | Custom | 507:272 | 0 | 1000000 | [6 empty] | Used for Optimal Start parameter | Attr | York RTU.PV | 40 | Temperature Sensor 14 | 8-1/SE_RTU2_Optimal_Start_Override.Enable.uClgEWMA | Relinquish Default | FALSE
Prop | Templates.PV | Temperature Sensor 15 | 1675 | 702 | 7014 | TRUE | TRUE | FALSE | 4 | Float | 1000ths | 3 | Custom | 507:272 |  | 0 | 1000000 |  |  | 1000ths | 0 | Custom | 507:272 | 0 | 1000000 | [6 empty] | Used for Optimal Start parameter | Attr | York RTU.PV | 40 | Temperature Sensor 15 | 8-1/SE_RTU2_Optimal_Start_Override.Enable.nHtgEWMA | Relinquish Default | FALSE
Prop | Templates.PV | Temperature Sensor 16 | 1675 | 703 | 7015 | TRUE | TRUE | FALSE | 4 | Float | 1000ths | 3 | Custom | 507:272 |  | 0 | 1000000 |  |  | 1000ths | 0 | Custom | 507:272 | 0 | 1000000 | [6 empty] | Used for Optimal Start parameter | Attr | York RTU.PV | 40 | Temperature Sensor 16 | 8-1/SE_RTU2_Optimal_Start_Override.Enable.nClgEWMA | Relinquish Default | FALSE
Prop | Templates.PV | Temperature Sensor 17 | 1675 | 704 | 7016 | TRUE | TRUE | FALSE | 4 | Float | 1000ths | 3 | Custom | 507:272 |  | 0 | 1000000 |  |  | 1000ths | 0 | Custom | 507:272 | 0 | 1000000 | [6 empty] | Used for Optimal Start parameter | Attr | York RTU.PV | 40 | Temperature Sensor 17 | 8-1/SE_RTU2_Optimal_Start_Override.Enable.predErrClg | Relinquish Default | FALSE
Prop | Templates.PV | Temperature Sensor 18 | 1675 | 705 | 7017 | TRUE | TRUE | FALSE | 4 | Float | 1000ths | 3 | Custom | 507:272 |  | 0 | 1000000 |  |  | 1000ths | 0 | Custom | 507:272 | 0 | 1000000 | [6 empty] | Used for Optimal Start parameter | Attr | York RTU.PV | 40 | Temperature Sensor 18 | 8-1/SE_RTU2_Optimal_Start_Override.Enable.predErrHtg | Relinquish Default | FALSE
Prop | Templates.PV | Temperature Sensor 19 | 1675 | 706 | 7018 | TRUE | TRUE | FALSE | 4 | Float | 1000ths | 3 | Custom | 507:272 |  | 0 | 1000000 |  |  | 1000ths | 0 | Custom | 507:272 | 0 | 1000000 | [6 empty] | Used for Optimal Start parameter | Attr | York RTU.PV | 40 | Temperature Sensor 19 | 8-1/SE_RTU2_Optimal_Start_Override.Enable.nHtg | Relinquish Default | FALSE
Prop | Templates.PV | Temperature Sensor 20 | 1675 | 707 | 7019 | TRUE | TRUE | FALSE | 4 | Float | 1000ths | 3 | Custom | 507:272 |  | 0 | 1000000 |  |  | 1000ths | 0 | Custom | 507:272 | 0 | 1000000 | [6 empty] | Used for Optimal Start parameter | Attr | York RTU.PV | 40 | Temperature Sensor 20 | 8-1/SE_RTU2_Optimal_Start_Override.Enable.nClg | Relinquish Default | FALSE
Prop | Templates.PV | Temperature Sensor 21 | 1675 | 708 | 7020 | TRUE | TRUE | FALSE | 1 | Boolean | [21 empty] | Used for Optimal Start parameter | Attr | York RTU.PV | 40 | Temperature Sensor 21 | 8-1/SE_RTU2_Optimal_Start_Override.Enable.unoccupiedIsActive | Relinquish Default | FALSE
Prop | Templates.PV | Temperature Sensor 22 | 1675 | 709 | 7021 | TRUE | TRUE | FALSE | 1 | Boolean | [21 empty] | Used for Optimal Start parameter | Attr | York RTU.PV | 40 | Temperature Sensor 22 | 8-1/SE_RTU2_Optimal_Start_Override.Enable.warmupIsActive | Relinquish Default | FALSE
Prop | Templates.PV | Temperature Sensor 23 | 1675 | 710 | 7022 | TRUE | TRUE | FALSE | 1 | Boolean | [21 empty] | Used for Optimal Start parameter | Attr | York RTU.PV | 40 | Temperature Sensor 23 | 8-1/SE_RTU2_Optimal_Start_Override.Enable.cooldownIsActive | Relinquish Default | FALSE
Prop | Templates.PV | Temperature Sensor 24 | 1675 | 711 | 7023 | TRUE | TRUE | FALSE | 1 | Boolean | [21 empty] | Used for Optimal Start parameter | Attr | York RTU.PV | 40 | Temperature Sensor 24 | 8-1/SE_RTU2_Optimal_Start_Override.Enable.normalIsActive | Relinquish Default | FALSE
Prop | Templates.PV | Temperature Sensor 25 | 1675 | 712 | 7024 | TRUE | TRUE | FALSE | 1 | Boolean | [21 empty] | Used for Optimal Start parameter | Attr | York RTU.PV | 40 | Temperature Sensor 25 | 8-1/SE_RTU2_Optimal_Start_Override.Enable.previousOccupied | Relinquish Default | FALSE
Prop | Templates.PV | Temperature Sensor 26 | 1675 | 713 | 7025 | TRUE | TRUE | FALSE | 1 | Boolean | [21 empty] | Used for Optimal Start parameter | Attr | York RTU.PV | 40 | Temperature Sensor 26 | 8-1/SE_RTU2_Optimal_Start_Override.Enable.onTimeStart | Relinquish Default | FALSE
Tmpl | Templates.Commissioning | [31 empty] | Model | York RTU.Commissioning | 41
Prop | Templates.Commissioning | Commissioning Mode | 1675 | 1244 | 7000 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Disable/Enable | 658 | Disable | [6 empty] | Disable/Enable | 658 | [6 empty] | 658 | 0 = Disable 1 = Enable |  | Attr | York RTU.Commissioning | 41 | Commissioning Mode | UCBapp.newUCB.COMMISH_MODE_EN | Present Value | FALSE | [7 empty] | Value |  |  | Views.Commissioning.Commissioning Mode | Commissioning Mode | 1675 | 1244 |  | Views.Commission.Commissioning Mode | Commissioning Mode | 1675 | 1244
Prop | Templates.Commissioning | Commissioning Time Remaining | 2644 | 447 | 7001 | TRUE | FALSE | FALSE | 4 | Float | 10ths | 5 | minutes | 507:72 | 0 | 0 | 100 |  |  | 10ths | 0 | minutes | 507:72 | 0 | 100 | [7 empty] | Attr | York RTU.Commissioning | 41 | Commissioning Time Remaining | UCBapp.newUCB.Commissioning Time Remaining | Present Value | FALSE | [7 empty] | Value |  |  | Views.Commissioning.Commissioning Mode | Commissioning Time Remaining | 2644 | 447 |  | Views.Commission.Commissioning Mode | CommishTimeRemaining | 2645 | 428
Prop | Templates.Commissioning | Extend Commissioning Time | 2644 | 448 | 7002 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | No | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Commissioning | 41 | Extend Commissioning Time | UCBapp.newUCB.COMMISH_EXTEND_TIME | Present Value | FALSE | [7 empty] | Value |  |  | Views.Commissioning.Commissioning Mode | Extend Commissioning Time | 2644 | 448 |  | Views.Commission.Commissioning Mode | ExtendCommishTime | 2645 | 429
Prop | Templates.Commissioning | Unit Enable | 1675 | 462 | 7003 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Shutdown/Enable | 349 | Enable | [6 empty] | Shutdown/Enable | 349 | [6 empty] | 349 | 0 = Shutdown 1 = Enable |  | Attr | York RTU.Commissioning | 41 | Unit Enable | UCBapp.newUCB.UNITEN_MODE | Relinquish Default | FALSE | [7 empty] | Value |  |  | Views.Commissioning.Commissioning Mode | Unit Enable | 1675 | 462 |  | Views.Commission.Commissioning Mode | UnitEn | 1709 | 641
Prop | Templates.Commissioning | Supply Fan Command | 2644 | 208 | 7004 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Off/On | 647 | Off | [6 empty] | Off/On | 647 | [6 empty] | 647 | 0 = Off 1 = On |  | Attr | York RTU.Commissioning | 41 | Supply Fan Command | UCBapp.newUCB.COMMISH_SF_C | Present Value | FALSE | [7 empty] | Value |  |  | Views.Commissioning.Commissioning Mode | Supply Fan Command | 2644 | 208 |  | Views.Commission.Commissioning Mode | Fan | 1709 | 79
Prop | Templates.Commissioning | Fan % Command | 1675 | 169 | 7005 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 0 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Commissioning | 41 | Fan % Command | UCBapp.newUCB.COMMISH_SF_O | Present Value | FALSE |  |  | UCBapp.newUCB.SF_TYPE:Present Value >= Fixed Variable |  |  |  |  | Value |  |  | Views.Commissioning.Commissioning Mode | Fan % Command | 1675 | 169 |  | Views.Commission.Commissioning Mode | FanVFD | 1709 | 67
Prop | Templates.Commissioning | Compressor Stage Command 1 | 1714 | 145 | 7006 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Off/On | 647 | Off | [6 empty] | Off/On | 647 | [6 empty] | 647 | 0 = Off 1 = On |  | Attr | York RTU.Commissioning | 41 | Compressor Stage Command 1 | UCBapp.newUCB.COMMISH_CLG1_C | Present Value | FALSE |  |  | UCBapp.newUCB.Max_Cooling_Stages:Present Value >= 1 |  |  |  |  | Value |  |  | Views.Commissioning.Commissioning Mode | Compressor Stage Command 1 | 1714 | 145 |  | Views.Commission.Commissioning Mode | C1 | 1709 | 127
Prop | Templates.Commissioning | Compressor Stage Command 2 | 1714 | 146 | 7007 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Off/On | 647 | Off | [6 empty] | Off/On | 647 | [6 empty] | 647 | 0 = Off 1 = On |  | Attr | York RTU.Commissioning | 41 | Compressor Stage Command 2 | UCBapp.newUCB.COMMISH_CLG2_C | Present Value | FALSE |  |  | York RTU.Cooling Control.Cooling Stages Available:Present Value > 1 |  |  |  |  | Value |  |  | Views.Commissioning.Commissioning Mode | Compressor Stage Command 2 | 1714 | 146 |  | Views.Commission.Commissioning Mode | C2 | 1709 | 128
Prop | Templates.Commissioning | Compressor Stage Command 3 | 1714 | 147 | 7008 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Off/On | 647 | Off | [6 empty] | Off/On | 647 | [6 empty] | 647 | 0 = Off 1 = On |  | Attr | York RTU.Commissioning | 41 | Compressor Stage Command 3 | UCBapp.newUCB.COMMISH_CLG3_C | Present Value | FALSE |  |  | York RTU.Cooling Control.Cooling Stages Available:Present Value > 2 |  |  |  |  | Value |  |  | Views.Commissioning.Commissioning Mode | Compressor Stage Command 3 | 1714 | 147 |  | Views.Commission.Commissioning Mode | C3 | 1709 | 129
Prop | Templates.Commissioning | Compressor Stage Command 4 | 1714 | 148 | 7009 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Off/On | 647 | Off | [6 empty] | Off/On | 647 | [6 empty] | 647 | 0 = Off 1 = On |  | Attr | York RTU.Commissioning | 41 | Compressor Stage Command 4 | UCBapp.newUCB.COMMISH_CLG4_C | Present Value | FALSE |  |  | York RTU.Cooling Control.Cooling Stages Available:Present Value > 3 |  |  |  |  | Value |  |  | Views.Commissioning.Commissioning Mode | Compressor Stage Command 4 | 1714 | 148 |  | Views.Commission.Commissioning Mode | C4 | 1709 | 130
Prop | Templates.Commissioning | Condenser Fan 1 | 1675 | 128 | 7010 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Off/On | 647 | Off | [6 empty] | Off/On | 647 | [6 empty] | 647 | 0 = Off 1 = On |  | Attr | York RTU.Commissioning | 41 | Condenser Fan 1 | UCBapp.newUCB.COMMISH_CF1_C | Present Value | FALSE | [7 empty] | Value |  |  | Views.Commissioning.Commissioning Mode | Condenser Fan 1 | 1675 | 128 |  | Views.Commission.Commissioning Mode | CN-Fan | 1709 | 109
Prop | Templates.Commissioning | Condenser Fan 2 | 1675 | 129 | 7011 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Off/On | 647 | Off | [6 empty] | Off/On | 647 | [6 empty] | 647 | 0 = Off 1 = On |  | Attr | York RTU.Commissioning | 41 | Condenser Fan 2 | UCBapp.newUCB.COMMISH_CF2_C | Present Value | FALSE | [7 empty] | Value |  |  | Views.Commissioning.Commissioning Mode | Condenser Fan 2 | 1675 | 129 |  | Views.Commission.Commissioning Mode | CF2 | 1709 | 110
Prop | Templates.Commissioning | Heating Stage Command 1 | 1714 | 149 | 7012 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Off/On | 647 | Off | [6 empty] | Off/On | 647 | [6 empty] | 647 | 0 = Off 1 = On |  | Attr | York RTU.Commissioning | 41 | Heating Stage Command 1 | UCBapp.newUCB.COMMISH_HTG1_C | Present Value | FALSE |  |  | UCBapp.newUCB.Max_Heating_Stages:Present Value >= 1 |  |  |  |  | Value |  |  | Views.Commissioning.Commissioning Mode | Heating Stage Command 1 | 1714 | 149 |  | Views.Commission.Commissioning Mode | H1 | 1709 | 251
Prop | Templates.Commissioning | Heating Stage Command 2 | 1714 | 150 | 7013 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Off/On | 647 | Off | [6 empty] | Off/On | 647 | [6 empty] | 647 | 0 = Off 1 = On |  | Attr | York RTU.Commissioning | 41 | Heating Stage Command 2 | UCBapp.newUCB.COMMISH_HTG2_C | Present Value | FALSE |  |  | UCBapp.newUCB.Max_Heating_Stages:Present Value >= 2 |  |  |  |  | Value |  |  | Views.Commissioning.Commissioning Mode | Heating Stage Command 2 | 1714 | 150 |  | Views.Commission.Commissioning Mode | H2 | 1709 | 252
Prop | Templates.Commissioning | Heating Stage Command 3 | 1714 | 151 | 7014 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Off/On | 647 | Off | [6 empty] | Off/On | 647 | [6 empty] | 647 | 0 = Off 1 = On |  | Attr | York RTU.Commissioning | 41 | Heating Stage Command 3 | UCBapp.newUCB.COMMISH_HTG3_C | Present Value | FALSE |  |  | UCBapp.newUCB.Max_Heating_Stages:Present Value >= 3 |  |  |  |  | Value |  |  | Views.Commissioning.Commissioning Mode | Heating Stage Command 3 | 1714 | 151 |  | Views.Commission.Commissioning Mode | H3 | 1709 | 253
Prop | Templates.Commissioning | Hot Gas Reheat | 1714 | 13 | 7015 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Off/On | 647 | Off | [6 empty] | Off/On | 647 | [6 empty] | 647 | 0 = Off 1 = On |  | Attr | York RTU.Commissioning | 41 | Hot Gas Reheat | UCBapp.newUCB.COMMISH_REHEAT_C | Present Value | FALSE |  |  | UCBapp.newUCB.Equipment_Configuration:Present Value < 2 Stage Cir1 With Single Cir2 |  |  |  |  | Value |  |  | Views.Commissioning.Commissioning Mode | Hot Gas Reheat | 1714 | 13 |  | Views.Commission.Commissioning Mode | HGR | 1709 | 324
Prop | Templates.Commissioning | Economizer Damper % Command | 1675 | 51 | 7016 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 0 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Commissioning | 41 | Economizer Damper % Command | EconApp.Econ.COMMISH_OAD_O | Present Value | FALSE |  |  | UCBapp.newUCB.Damper_Installed:Present Value = Active |  |  |  |  | Value |  |  | Views.Commissioning.Commissioning Mode | Economizer Damper % Command | 1675 | 51 |  | Views.Commission.Commissioning Mode | Econ | 1709 | 282
Prop | Templates.Commissioning | Exhaust Fan Command | 1675 | 235 | 7017 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Off/On | 647 | Off | [6 empty] | Off/On | 647 | [6 empty] | 647 | 0 = Off 1 = On |  | Attr | York RTU.Commissioning | 41 | Exhaust Fan Command | EconApp.Econ.COMMISH_EF_C | Present Value | FALSE |  |  | EconApp.Econ.Exhaust Setup:Present Value <> None |  |  |  |  | Value |  |  | Views.Commissioning.Commissioning Mode | Exhaust Fan Command | 1675 | 235 |  | Views.Commission.Commissioning Mode | ExFan | 1709 | 309
Prop | Templates.Commissioning | Exhaust Fan VFD % Command | 1675 | 236 | 7018 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 0 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Commissioning | 41 | Exhaust Fan VFD % Command | EconApp.Econ.COMMISH_EF_O | Present Value | FALSE |  |  | EconApp.Econ.Exhaust Setup:Present Value = Variable Frequency Fan |  |  |  |  | Value |  |  | Views.Commissioning.Commissioning Mode | Exhaust Fan VFD % Command | 1675 | 236 |  | Views.Commission.Commissioning Mode | ExFanVFD | 1709 | 310
Prop | Templates.Commissioning | Cancel ASCD Timers | 1675 | 336 | 7019 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | No/Yes | 854 | No | [6 empty] | No/Yes | 854 | [6 empty] | 854 | 0 = No 1 = Yes |  | Attr | York RTU.Commissioning | 41 | Cancel ASCD Timers | UCBapp.newUCB.COMMISH_ASCD_Ovr | Present Value | FALSE | [7 empty] | Value |  |  | Views.Commissioning.Commissioning Mode | Cancel ASCD Timers | 1675 | 336 |  | Views.Commission.Commissioning Mode | Cancel ASCD Timers | 1675 | 336
Prop | Templates.Commissioning | Exhaust Damper % Command | 1675 | 242 | 7020 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 0 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Commissioning | 41 | Exhaust Damper % Command | EconApp.Econ.COMMISH_EF_O | Present Value | FALSE |  |  | EconApp.Econ.Exhaust Setup:Present Value = Modulating Damper |  |  |  |  | Value |  |  | Views.Commissioning.Commissioning Mode | Exhaust Damper % Command | 1675 | 242 |  | Views.Commission.Commissioning Mode | EAD-O | 1709 | 316
Prop | Templates.Commissioning | Hot Gas Reheat | 1714 | 13 | 7021 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 0 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Commissioning | 41 | Hot Gas Reheat | FourStageApp.FourStage.COMMISH_MOD_HGR_O | Present Value | FALSE |  |  | UCBapp.newUCB.Equipment_Configuration:Present Value >= 2 Stage Cir1 With Single Cir2 |  |  |  |  | Value |  |  | Views.Commissioning.Commissioning Mode | Hot Gas Reheat | 1714 | 13 |  | Views.Commission.Commissioning Mode | HGR | 1709 | 324
Prop | Templates.Commissioning | Hot Gas Reheat Bleed Valve Command | 2644 | 238 | 7022 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Close/Open | 939 | Open | [6 empty] | Close/Open | 939 | [6 empty] | 939 | 0 = Close 1 = Open |  | Attr | York RTU.Commissioning | 41 | Hot Gas Reheat Bleed Valve Command | FourStageApp.FourStage.COMMISH_BLEED_C | Present Value | FALSE |  |  | UCBapp.newUCB.Equipment_Configuration:Present Value >= 2 Stage Cir1 With Single Cir2 |  |  |  |  | Value |  |  | Views.Commissioning.Commissioning Mode | Hot Gas Reheat Bleed Valve Command | 2644 | 238 |  | Views.Commission.Commissioning Mode | Hot Gas Reheat Bleed Valve Command | 2644 | 238
Prop | Templates.Commissioning | Modulating Compressor Output | 2644 | 292 | 7023 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 0 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Commissioning | 41 | Modulating Compressor Output | UCBapp.newUCB.COMMISH_CLG1_O | Present Value | FALSE |  |  | York RTU.Unique Equipment Identifier:Present Value > 5 |  |  |  |  | Value |  |  | Views.Commissioning.Commissioning Mode | Modulating Compressor Output | 2644 | 292 |  | Views.Commission.Commissioning Mode | ModCompOut | 2645 | 311
Prop | Templates.Commissioning | Modulating Condenser Fan 1 Output | 2644 | 293 | 7024 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 0 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Commissioning | 41 | Modulating Condenser Fan 1 Output | UCBapp.newUCB.COMMISH_CF1_O | Present Value | FALSE |  |  | York RTU.Cooling Control.Circuit 1 Modulating Condenser Fan Installed:Present Value = Yes |  |  |  |  | Value |  |  | Views.Commissioning.Commissioning Mode | Modulating Condenser Fan 1 Output | 2644 | 293 |  | Views.Commission.Commissioning Mode | ModCondFan1Out | 2645 | 312
Prop | Templates.Commissioning | Modulating Condenser Fan 2 Output | 2644 | 294 | 7025 | TRUE | TRUE | FALSE | 4 | Float | 1s | 6 | % | 507:98 | 0 | 0 | 100 |  |  | 1s | 0 | % | 507:98 | 0 | 100 | [7 empty] | Attr | York RTU.Commissioning | 41 | Modulating Condenser Fan 2 Output | UCBapp.newUCB.COMMISH_CF2_O | Present Value | FALSE |  |  | York RTU.Cooling Control.Circuit 2 Modulating Condenser Fan Installed:Present Value = Yes |  |  |  |  | Value |  |  | Views.Commissioning.Commissioning Mode | Modulating Condenser Fan 2 Output | 2644 | 294 |  | Views.Commission.Commissioning Mode | ModCondFan2Out | 2645 | 313
Tmpl | Templates.Bluetooth | [31 empty] | Model | York RTU.Bluetooth | 22
Prop | Templates.Bluetooth | BLE Connection Status | 1675 | 1683 | 7000 | TRUE | FALSE | FALSE | 9 | MultiState |  |  | BLE Connection Status | 40548 | [7 empty] | BLE Connection Status | 40548 | [6 empty] | 40548 | 0 = Not Connected 1 = Waiting for Connection 2 = Connected 3 = Disabled 4 = Error |  | Attr | York RTU.Bluetooth | 22 | BLE Connection Status | 8-1/Bluetooth | BLE Connection Status | FALSE | [7 empty] | Value |  |  | Views.Controller.Bluetooth | BLE Connection Status | 1675 | 1683 |  | Views.Controller.Bluetooth | BT-Status | 1709 | 772
Prop | Templates.Bluetooth | Initiate Connection | 1675 | 1684 | 7001 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | BLE Initiate Connection | 40549 | [7 empty] | BLE Initiate Connection | 40549 | [6 empty] | 40549 | 0 = Start 1 = Stop 2 = Started 3 = Stopped |  | Attr | York RTU.Bluetooth | 22 | Initiate Connection | 8-1/Bluetooth | Initiate Connection | FALSE | [7 empty] | Value |  |  | Views.Controller.Bluetooth | Initiate Connection | 1675 | 1684 |  | Views.Controller.Bluetooth | BT-Command | 1709 | 773
Prop | Templates.Bluetooth | PIN | 1675 | 1685 | 7002 | TRUE | FALSE | FALSE | 7 | String | [17 empty] | -1 |  |  |  |  | Attr | York RTU.Bluetooth | 22 | PIN | 8-1/Bluetooth | PIN | FALSE | [7 empty] | Value |  |  | Views.Controller.Bluetooth | PIN | 1675 | 1685 |  | Views.Controller.Bluetooth | PIN | 1709 | 774
Prop | Templates.Bluetooth | BLE Device Name | 1675 | 1686 | 7003 | TRUE | FALSE | FALSE | 7 | String | [17 empty] | -1 |  |  |  |  | Attr | York RTU.Bluetooth | 22 | BLE Device Name | 8-1/Bluetooth | BLE Device Name | FALSE | [7 empty] | Value |  |  | Views.Controller.Bluetooth | BLE Device Name | 1675 | 1686 |  | Views.Controller.Bluetooth | BT-Name | 1709 | 775
Prop | Templates.Bluetooth | Bluetooth Firmware Version | 1675 | 1687 | 7004 | TRUE | FALSE | FALSE | 7 | String | [17 empty] | -1 |  |  |  |  | Attr | York RTU.Bluetooth | 22 | Bluetooth Firmware Version | 8-1/Bluetooth | Bluetooth Firmware Version | FALSE | [7 empty] | Value |  |  | Views.Controller.Bluetooth | Bluetooth Firmware Version | 1675 | 1687 |  | Views.Controller.Bluetooth | BT-Version | 1709 | 776
Prop | Templates.Bluetooth | Status | 1675 | 1688 | 7005 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | Object Status | 505 | [7 empty] | Object Status | 505 | [6 empty] | 505 | 0 = Normal 1 = Inactive 2 = Monitor Only Mode Active 5 = Battery Alarm ... |  | Attr | York RTU.Bluetooth | 22 | Status | 8-1/Bluetooth | Status | TRUE
Prop | Templates.Bluetooth | Bluetooth Enabled | 1675 | 1691 | 7006 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | False/True | 1701 | [7 empty] | False/True | 1701 | [6 empty] | 1701 | 0 = False 1 = True |  | Attr | York RTU.Bluetooth | 22 | Bluetooth Enabled | 8-1/Bluetooth | Bluetooth Enabled | FALSE | [7 empty] | Value |  |  | Views.Controller.Bluetooth | Bluetooth Enabled | 1675 | 1691 |  | Views.Controller.Bluetooth | BT-Ena | 1709 | 784
Prop | Templates.Bluetooth | Clear Bluetooth Connections | 1675 | 1692 | 7007 | TRUE | TRUE | FALSE | 9 | MultiState |  |  | False/True | 1701 | [7 empty] | False/True | 1701 | [6 empty] | 1701 | 0 = False 1 = True |  | Attr | York RTU.Bluetooth | 22 | Clear Bluetooth Connections | 8-1/Bluetooth | Clear Bluetooth Connection Info | FALSE | [7 empty] | Value |  |  | Views.Controller.Bluetooth | Clear Bluetooth Connections | 1675 | 1692 |  | Views.Controller.Bluetooth | BT-ClrInfo | 1709 | 785
[33 empty] | Schedule |  | 10133 | Schedule | 8-1/19_6 | Present Value | [8 empty] | Schedule |  |  | Views.Set Schedule | Occupancy Schedule | 1667 | 2 |  | Views.Schedule | Occupancy Schedule | 1667 | 2
[33 empty] | Trend |  | 101010 | ST_Trend | York RTU.HVAC Zone.Space Temperature Input | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Sensors | Space Temperature Input | 1675 | 164 |  |  | ST | 1709 | 32
[33 empty] | Trend |  | 101011 | Unit-S_Trend | York RTU.Unit Status | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Status | Unit Status | 1675 | 0 |  |  | Unit-S | 1709 | 0
[33 empty] | Trend |  | 101012 | Y1-Tstat_Trend | York RTU.Thermostat Control.Y1 - Thermostat | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Cooling.Stage 1 | Y1 - Thermostat | 1675 | 150 |  |  | Y1-Tstat | 1709 | 11
[33 empty] | Trend |  | 101013 | Y2-Tstat_Trend | York RTU.Thermostat Control.Y2 - Thermostat | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Cooling.Stage 2 | Y2 - Thermostat | 1675 | 151 |  |  | Y2-Tstat | 1709 | 12
[33 empty] | Trend |  | 101014 | Y3-Tstat_Trend | York RTU.Thermostat Control.Y3 - Thermostat | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Cooling.Stage 3 | Y3 - Thermostat | 1675 | 152 |  |  | Y3-Tstat | 1709 | 13
[33 empty] | Trend |  | 101015 | Y4-Tstat_Trend | York RTU.Thermostat Control.Y4 - Thermostat | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Cooling.Stage 4 | Y4 - Thermostat | 1675 | 153 |  |  | Y4-Tstat | 1709 | 14
[33 empty] | Trend |  | 101016 | W1-Tstat_Trend | York RTU.Thermostat Control.W1 - Thermostat | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Heating.Stage 1 | W1 - Thermostat | 1675 | 154 |  |  | W1-Tstat | 1709 | 15
[33 empty] | Trend |  | 101017 | W2-Tstat_Trend | York RTU.Thermostat Control.W2 - Thermostat | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Heating.Stage 2 | W2 - Thermostat | 1675 | 155 |  |  | W2-Tstat | 1709 | 16
[33 empty] | Trend |  | 101018 | W3-Tstat_Trend | York RTU.Thermostat Control.W3 - Thermostat | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Heating.Stage 3 | W3 - Thermostat | 1675 | 156 |  |  | W3-Tstat | 1709 | 17
[33 empty] | Trend |  | 101019 | G-Tstat_Trend | York RTU.Thermostat Control.G - Thermostat | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Fan.Indoor Fan | G - Thermostat | 1675 | 157 |  |  | G-Tstat | 1709 | 18
[33 empty] | Trend |  | 101020 | X-Out_Trend | York RTU.Thermostat Control.X-OUT | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Fault.Misc | X-OUT | 1675 | 159 |  |  | X-Out | 1709 | 20
[33 empty] | Trend |  | 101021 | OprOcc_Trend | York RTU.HVAC Zone.Operational Occupancy | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Status | Operational Occupancy | 1675 | 10 |  |  | OprOcc | 1709 | 23
[33 empty] | Trend |  | 101022 | OprST_Trend | York RTU.HVAC Zone.Operational Space Temperature | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Status | Operational Space Temperature | 1675 | 15 |  |  | OprST | 1709 | 28
[33 empty] | Trend |  | 101022 | OprST_Trend | York RTU.HVAC Zone.Operational Space Temperature | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Sensors | Operational Space Temperature | 1675 | 15 |  |  | OprST | 1709 | 28
[33 empty] | Trend |  | 101023 | OprIAQ_Trend | York RTU.HVAC Zone.Operational Indoor Air Quality | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Sensors | Operational Indoor Air Quality | 1675 | 165 |  |  | OprIAQ | 1709 | 34
[33 empty] | Trend |  | 101024 | OprSH_Trend | York RTU.HVAC Zone.Operational Space Humidity | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Sensors | Operational Space Humidity | 1675 | 23 |  |  | OprSH | 1709 | 39
[33 empty] | Trend |  | 101025 | OprOAT _Trend | York RTU.Weather Information.Operational Outdoor Air Temperature | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Status | Operational Outdoor Air Temperature | 1675 | 36 |  |  | OprOAT | 1709 | 52
[33 empty] | Trend |  | 101025 | OprOAT _Trend | York RTU.Weather Information.Operational Outdoor Air Temperature | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Sensors | Operational Outdoor Air Temperature | 1675 | 36 |  |  | OprOAT | 1709 | 52
[33 empty] | Trend |  | 101026 | OprOAQ_Trend | York RTU.Weather Information.Operational Outdoor Air Quality | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Sensors | Operational Outdoor Air Quality | 1675 | 45 |  |  | OprOAQ | 1709 | 61
[33 empty] | Trend |  | 101027 | Fan-S_Trend | York RTU.Fan Control.Fan Status | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Status | Fan Status | 1675 | 168 |  |  | Fan-S | 1709 | 66
[33 empty] | Trend |  | 101027 | Fan-S_Trend | York RTU.Fan Control.Fan Status | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Fan.Indoor Fan | Fan Status | 1675 | 168 |  |  | Fan-S | 1709 | 66
[33 empty] | Trend |  | 101028 | FanVFD_Trend | York RTU.Fan Control.Fan % Command | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Fan.Indoor Fan | Fan % Command | 1675 | 169 |  |  | FanVFD | 1709 | 67
[33 empty] | Trend |  | 101029 | APS_Trend | York RTU.Fan Control.Air Proving Switch | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Fan.Indoor Fan | Air Proving Switch | 1675 | 175 |  |  | APS | 1709 | 73
[33 empty] | Trend |  | 101030 | DFS_Trend | York RTU.Fan Control.Dirty Filter Switch | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Fault.Misc | Dirty Filter Switch | 1675 | 180 |  |  | DFS | 1709 | 78
[33 empty] | Trend |  | 101031 | Fan_Trend | York RTU.Fan Control.Fan Command | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Fan.Indoor Fan | Fan Command | 1675 | 181 |  |  | Fan | 1709 | 79
[33 empty] | Trend |  | 101032 | SAT_Trend | York RTU.Fan Control.Supply Air Temperature | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Status | Supply Air Temperature | 1675 | 182 |  |  | SAT | 1709 | 80
[33 empty] | Trend |  | 101032 | SAT_Trend | York RTU.Fan Control.Supply Air Temperature | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Cooling.Status | Supply Air Temperature | 1675 | 182 |  |  | SAT | 1709 | 80
[33 empty] | Trend |  | 101032 | SAT_Trend | York RTU.Fan Control.Supply Air Temperature | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Heating.Status | Supply Air Temperature | 1675 | 182 |  |  | SAT | 1709 | 80
[33 empty] | Trend |  | 101032 | SAT_Trend | York RTU.Fan Control.Supply Air Temperature | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Sensors | Supply Air Temperature | 1675 | 182 |  |  | SAT | 1709 | 80
[33 empty] | Trend |  | 101033 | DctPrs_Trend | York RTU.Fan Control.Duct Static Pressure | Present Value |  | 300 | 300
[33 empty] | Trend |  | 101034 | DctPrs-Sp _Trend | York RTU.Fan Control.Duct Pressure Setpoint | Present Value |  | 100 | 900
[33 empty] | Trend |  | 101035 | Clg-S_Trend | York RTU.Cooling Control.Cooling Status | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Status | Cooling Status | 1675 | 69 |  |  | Clg-S | 1709 | 93
[33 empty] | Trend |  | 101035 | Clg-S_Trend | York RTU.Cooling Control.Cooling Status | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Cooling.Status | Cooling Status | 1675 | 69 |  |  | Clg-S | 1709 | 93
[33 empty] | Trend |  | 101036 | CN-Fan_Trend | York RTU.Cooling Control.Condenser Fan 1 | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Fan.Condenser Fans | Condenser Fan 1 | 1675 | 128 |  |  | CN-Fan | 1709 | 109
[33 empty] | Trend |  | 101037 | CF2_Trend | York RTU.Cooling Control.Condenser Fan 2 | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Fan.Condenser Fans | Condenser Fan 2 | 1675 | 129 |  |  | CF2 | 1709 | 110
[33 empty] | Trend |  | 101039 | OprClg-Sp_Trend | York RTU.Cooling Control.CV Operating Cooling Setpoint | Present Value |  | 100 | 900 | [5 empty] | Trend |  |  | Views.Trend.Cooling.Status | Operating Cooling Setpoint | 1675 | 1176 |  |  | OprClg-Sp | 2645 | 440
[33 empty] | Trend |  | 101040 | C1_Trend | York RTU.Cooling Control.DX Cooling Circuit 1.Compressor Stage Command | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Cooling.Stage 1 | Compressor Stage Command 1 | 1714 | 145 |  |  | Compressor Stage Command 1 | 1714 | 145
[33 empty] | Trend |  | 101041 | C1-S_Trend | York RTU.Cooling Control.DX Cooling Circuit 1.Compressor Stage Status | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Cooling.Stage 1 | Compressor Stage 1 Status | 1714 | 39 |  |  | Compressor Stage 1 Status | 1714 | 39
[33 empty] | Trend |  | 101042 | HPS1_Trend | York RTU.Cooling Control.DX Cooling Circuit 1.High Pressure Limit | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Fault.Cooling Stage 1 | High Pressure Limit | 1675 | 93 |  |  | HPS1 | 1709 | 156
[33 empty] | Trend |  | 101043 | HPS1-LO_Trend | York RTU.Cooling Control.DX Cooling Circuit 1.High Pressure Lockout | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Fault.Cooling Stage 1 | High Pressure Lockout | 1675 | 94 |  |  | HPS1-LO | 1709 | 160
[33 empty] | Trend |  | 101044 | LPS1_Trend | York RTU.Cooling Control.DX Cooling Circuit 1.Low Pressure Limit | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Fault.Cooling Stage 1 | Low Pressure Limit | 1675 | 95 |  |  | LPS1 | 1709 | 164
[33 empty] | Trend |  | 101045 | LPS1-LO_Trend | York RTU.Cooling Control.DX Cooling Circuit 1.Low Pressure Lockout | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Fault.Cooling Stage 1 | Low Pressure Lockout | 1675 | 96 |  |  | LPS1-LO | 1709 | 168
[33 empty] | Trend |  | 101046 | FS1_Trend | York RTU.Cooling Control.DX Cooling Circuit 1.Freeze Condition | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Fault.Cooling Stage 1 | Freeze Condition | 1675 | 97 |  |  | FS1 | 1709 | 172
[33 empty] | Trend |  | 101047 | FS1-LO_Trend | York RTU.Cooling Control.DX Cooling Circuit 1.Freeze Condition Lockout | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Fault.Cooling Stage 1 | Freeze Condition Lockout | 1675 | 98 |  |  | FS1-LO | 1709 | 176
[33 empty] | Trend |  | 101048 | EC1_Trend | York RTU.Cooling Control.DX Cooling Circuit 1.Evaporator Coil Temp | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Fault.Cooling Stage 1 | Evaporator Coil Temp | 1675 | 100 |  |  | EC1 | 1709 | 180
[33 empty] | Trend |  | 101049 | CC1_Trend | York RTU.Cooling Control.DX Cooling Circuit 1.Condenser Coil Temp | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Fault.Cooling Stage 1 | Condenser Coil Temp | 1675 | 102 |  |  | CC1 | 1709 | 184
[33 empty] | Trend |  | 101050 | C2_Trend | York RTU.Cooling Control.DX Cooling Circuit 2.Compressor Stage Command | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Cooling.Stage 2 | Compressor Stage Command 2 | 1714 | 146 |  |  | Compressor Stage Command 2 | 1714 | 146
[33 empty] | Trend |  | 101051 | C2-S_Trend | York RTU.Cooling Control.DX Cooling Circuit 2.Compressor Stage Status | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Cooling.Stage 2 | Compressor Stage 2 Status | 1714 | 55 |  |  | Compressor Stage 2 Status | 1714 | 55
[33 empty] | Trend |  | 101052 | HPS2_Trend | York RTU.Cooling Control.DX Cooling Circuit 2.High Pressure Limit | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Fault.Cooling Stage 2 | High Pressure Limit | 1675 | 93 |  |  | HPS2 | 1709 | 157
[33 empty] | Trend |  | 101053 | HPS2-LO_Trend | York RTU.Cooling Control.DX Cooling Circuit 2.High Pressure Lockout | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Fault.Cooling Stage 2 | High Pressure Lockout | 1675 | 94 |  |  | HPS2-LO | 1709 | 161
[33 empty] | Trend |  | 101054 | LPS2_Trend | York RTU.Cooling Control.DX Cooling Circuit 2.Low Pressure Limit | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Fault.Cooling Stage 2 | Low Pressure Limit | 1675 | 95 |  |  | LPS2 | 1709 | 165
[33 empty] | Trend |  | 101055 | LPS2-LO_Trend | York RTU.Cooling Control.DX Cooling Circuit 2.Low Pressure Lockout | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Fault.Cooling Stage 2 | Low Pressure Lockout | 1675 | 96 |  |  | LPS2-LO | 1709 | 169
[33 empty] | Trend |  | 101056 | FS2_Trend | York RTU.Cooling Control.DX Cooling Circuit 2.Freeze Condition | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Fault.Cooling Stage 2 | Freeze Condition | 1675 | 97 |  |  | FS2 | 1709 | 173
[33 empty] | Trend |  | 101057 | FS2-LO_Trend | York RTU.Cooling Control.DX Cooling Circuit 2.Freeze Condition Lockout | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Fault.Cooling Stage 2 | Freeze Condition Lockout | 1675 | 98 |  |  | FS2-LO | 1709 | 177
[33 empty] | Trend |  | 101058 | EC2_Trend | York RTU.Cooling Control.DX Cooling Circuit 2.Evaporator Coil Temp | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Fault.Cooling Stage 2 | Evaporator Coil Temp | 1675 | 100 |  |  | EC2 | 1709 | 181
[33 empty] | Trend |  | 101059 | CC2_Trend | York RTU.Cooling Control.DX Cooling Circuit 2.Condenser Coil Temp | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Fault.Cooling Stage 2 | Condenser Coil Temp | 1675 | 102 |  |  | CC2 | 1709 | 185
[33 empty] | Trend |  | 101060 | C3_Trend | York RTU.Cooling Control.DX Cooling Circuit 3.Compressor Stage Command | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Cooling.Stage 3 | Compressor Stage Command 3 | 1714 | 147 |  |  | Compressor Stage Command 3 | 1714 | 147
[33 empty] | Trend |  | 101061 | C3-S_Trend | York RTU.Cooling Control.DX Cooling Circuit 3.Compressor Stage Status | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Cooling.Stage 3 | Compressor Stage 3 Status | 1714 | 71 |  |  | Compressor Stage 3 Status | 1714 | 71
[33 empty] | Trend |  | 101062 | HPS3_Trend | York RTU.Cooling Control.DX Cooling Circuit 3.High Pressure Limit | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Fault.Cooling Stage 3 | High Pressure Limit | 1675 | 93 |  |  | HPS3 | 1709 | 158
[33 empty] | Trend |  | 101063 | HPS3-LO_Trend | York RTU.Cooling Control.DX Cooling Circuit 3.High Pressure Lockout | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Fault.Cooling Stage 3 | High Pressure Lockout | 1675 | 94 |  |  | HPS3-LO | 1709 | 162
[33 empty] | Trend |  | 101064 | LPS3_Trend | York RTU.Cooling Control.DX Cooling Circuit 3.Low Pressure Limit | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Fault.Cooling Stage 3 | Low Pressure Limit | 1675 | 95 |  |  | LPS3 | 1709 | 166
[33 empty] | Trend |  | 101065 | LPS3-LO_Trend | York RTU.Cooling Control.DX Cooling Circuit 3.Low Pressure Lockout | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Fault.Cooling Stage 3 | Low Pressure Lockout | 1675 | 96 |  |  | LPS3-LO | 1709 | 170
[33 empty] | Trend |  | 101066 | FS3_Trend | York RTU.Cooling Control.DX Cooling Circuit 3.Freeze Condition | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Fault.Cooling Stage 3 | Freeze Condition | 1675 | 97 |  |  | FS3 | 1709 | 174
[33 empty] | Trend |  | 101067 | FS3-LO_Trend | York RTU.Cooling Control.DX Cooling Circuit 3.Freeze Condition Lockout | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Fault.Cooling Stage 3 | Freeze Condition Lockout | 1675 | 98 |  |  | FS3-LO | 1709 | 178
[33 empty] | Trend |  | 101068 | EC3_Trend | York RTU.Cooling Control.DX Cooling Circuit 3.Evaporator Coil Temp | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Fault.Cooling Stage 3 | Evaporator Coil Temp | 1675 | 100 |  |  | EC3 | 1709 | 182
[33 empty] | Trend |  | 101069 | CC3_Trend | York RTU.Cooling Control.DX Cooling Circuit 3.Condenser Coil Temp | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Fault.Cooling Stage 3 | Condenser Coil Temp | 1675 | 102 |  |  | CC3 | 1709 | 186
[33 empty] | Trend |  | 101070 | C4_Trend | York RTU.Cooling Control.DX Cooling Circuit 4.Compressor Stage Command | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Cooling.Stage 4 | Compressor Stage Command 4 | 1714 | 148 |  |  | Compressor Stage Command 4 | 1714 | 148
[33 empty] | Trend |  | 101071 | C4-S_Trend | York RTU.Cooling Control.DX Cooling Circuit 4.Compressor Stage Status | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Cooling.Stage 4 | Compressor Stage 4 Status | 1714 | 87 |  |  | Compressor Stage 4 Status | 1714 | 87
[33 empty] | Trend |  | 101072 | HPS4_Trend | York RTU.Cooling Control.DX Cooling Circuit 4.High Pressure Limit | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Fault.Cooling Stage 4 | High Pressure Limit | 1675 | 93 |  |  | HPS4 | 1709 | 159
[33 empty] | Trend |  | 101073 | HPS4-LO_Trend | York RTU.Cooling Control.DX Cooling Circuit 4.High Pressure Lockout | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Fault.Cooling Stage 4 | High Pressure Lockout | 1675 | 94 |  |  | HPS4-LO | 1709 | 163
[33 empty] | Trend |  | 101074 | LPS4_Trend | York RTU.Cooling Control.DX Cooling Circuit 4.Low Pressure Limit | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Fault.Cooling Stage 4 | Low Pressure Limit | 1675 | 95 |  |  | LPS4 | 1709 | 167
[33 empty] | Trend |  | 101075 | LPS4-LO_Trend | York RTU.Cooling Control.DX Cooling Circuit 4.Low Pressure Lockout | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Fault.Cooling Stage 4 | Low Pressure Lockout | 1675 | 96 |  |  | LPS4-LO | 1709 | 171
[33 empty] | Trend |  | 101076 | FS4_Trend | York RTU.Cooling Control.DX Cooling Circuit 4.Freeze Condition | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Fault.Cooling Stage 4 | Freeze Condition | 1675 | 97 |  |  | FS4 | 1709 | 175
[33 empty] | Trend |  | 101077 | FS4-LO_Trend | York RTU.Cooling Control.DX Cooling Circuit 4.Freeze Condition Lockout | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Fault.Cooling Stage 4 | Freeze Condition Lockout | 1675 | 98 |  |  | FS4-LO | 1709 | 179
[33 empty] | Trend |  | 101078 | EC4_Trend | York RTU.Cooling Control.DX Cooling Circuit 4.Evaporator Coil Temp | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Fault.Cooling Stage 4 | Evaporator Coil Temp | 1675 | 100 |  |  | EC4 | 1709 | 183
[33 empty] | Trend |  | 101079 | CC4_Trend | York RTU.Cooling Control.DX Cooling Circuit 4.Condenser Coil Temp | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Fault.Cooling Stage 4 | Condenser Coil Temp | 1675 | 102 |  |  | CC4 | 1709 | 187
[33 empty] | Trend |  | 101080 | SLP1_Trend | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Suction Pressure | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Diagnostics.Cooling Stage 1 | Suction Pressure | 1675 | 194 |  |  | SLP-1 | 1709 | 188
[33 empty] | Trend |  | 101081 | LLP1_Trend | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Liquid Pressure | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Diagnostics.Cooling Stage 1 | Liquid Pressure | 1675 | 195 |  |  | LLP-1 | 1709 | 192
[33 empty] | Trend |  | 101082 | SLT1_Trend | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Suction Temperature | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Diagnostics.Cooling Stage 1 | Suction Temperature | 1675 | 196 |  |  | SLT-1 | 1709 | 196
[33 empty] | Trend |  | 101083 | LLT1_Trend | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Liquid Temperature | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Diagnostics.Cooling Stage 1 | Liquid Temperature | 1675 | 197 |  |  | LLT-1 | 1709 | 200
[33 empty] | Trend |  | 101089 | SLP2_Trend | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Suction Pressure | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Diagnostics.Cooling Stage 2 | Suction Pressure | 1675 | 194 |  |  | SLP-2 | 1709 | 189
[33 empty] | Trend |  | 101090 | LLP2_Trend | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Liquid Pressure | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Diagnostics.Cooling Stage 2 | Liquid Pressure | 1675 | 195 |  |  | LLP-2 | 1709 | 193
[33 empty] | Trend |  | 101091 | SLT2_Trend | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Suction Temperature | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Diagnostics.Cooling Stage 2 | Suction Temperature | 1675 | 196 |  |  | SLT-2 | 1709 | 197
[33 empty] | Trend |  | 101092 | LLT2_Trend | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Liquid Temperature | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Diagnostics.Cooling Stage 2 | Liquid Temperature | 1675 | 197 |  |  | LLT-2 | 1709 | 201
[33 empty] | Trend |  | 101098 | SLP3_Trend | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics.Suction Pressure | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Diagnostics.Cooling Stage 3 | Suction Pressure | 1675 | 194 |  |  | SLP-3 | 1709 | 190
[33 empty] | Trend |  | 101099 | LLP3_Trend | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics.Liquid Pressure | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Diagnostics.Cooling Stage 3 | Liquid Pressure | 1675 | 195 |  |  | LLP-3 | 1709 | 194
[33 empty] | Trend |  | 101100 | SLT3_Trend | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics.Suction Temperature | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Diagnostics.Cooling Stage 3 | Suction Temperature | 1675 | 196 |  |  | SLT-3 | 1709 | 198
[33 empty] | Trend |  | 101101 | LLT3_Trend | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics.Liquid Temperature | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Diagnostics.Cooling Stage 3 | Liquid Temperature | 1675 | 197 |  |  | LLT-3 | 1709 | 202
[33 empty] | Trend |  | 101107 | SLP4_Trend | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics.Suction Pressure | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Diagnostics.Cooling Stage 4 | Suction Pressure | 1675 | 194 |  |  | SLP-4 | 1709 | 191
[33 empty] | Trend |  | 101108 | LLP4_Trend | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics.Liquid Pressure | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Diagnostics.Cooling Stage 4 | Liquid Pressure | 1675 | 195 |  |  | LLP-4 | 1709 | 195
[33 empty] | Trend |  | 101109 | SLT4_Trend | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics.Suction Temperature | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Diagnostics.Cooling Stage 4 | Suction Temperature | 1675 | 196 |  |  | SLT-4 | 1709 | 199
[33 empty] | Trend |  | 101110 | LLT4_Trend | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics.Liquid Temperature | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Diagnostics.Cooling Stage 4 | Liquid Temperature | 1675 | 197 |  |  | LLT-4 | 1709 | 203
[33 empty] | Trend |  | 101116 | Htg-S_Trend | York RTU.Heating Control.Heating Status | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Status | Heating Status | 1675 | 106 |  |  | Htg-S | 1709 | 225
[33 empty] | Trend |  | 101116 | Htg-S_Trend | York RTU.Heating Control.Heating Status | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Heating.Status | Heating Status | 1675 | 106 |  |  | Htg-S | 1709 | 225
[33 empty] | Trend |  | 101117 | Limit_Trend | York RTU.Heating Control.Heat Limit1 Switch | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Fault.Heating Stage 1 | Heat Limit1 Switch | 1675 | 121 |  |  | Limit | 1709 | 233
[33 empty] | Trend |  | 101118 | LimitLO_Trend | York RTU.Heating Control.Heat Limit1 Switch Lockout | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Fault.Heating Stage 1 | Heat Limit1 Switch Lockout | 1675 | 122 |  |  | LimitLO | 1709 | 234
[33 empty] | Trend |  | 101119 | Lim2_Trend | York RTU.Heating Control.Heat Limit2 Switch | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Fault.Heating Stage 2 | Heat Limit2 Switch | 1675 | 123 |  |  | Lim2 | 1709 | 235
[33 empty] | Trend |  | 101120 | Lim2LO_Trend | York RTU.Heating Control.Heat Limit2 Switch Lockout | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Fault.Heating Stage 2 | Heat Limit2 Switch Lockout | 1675 | 124 |  |  | Lim2LO | 1709 | 236
[33 empty] | Trend |  | 101121 | Lim3_Trend | York RTU.Heating Control.Heat Limit3 Switch | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Fault.Heating Stage 3 | Heat Limit3 Switch | 1675 | 125 |  |  | Lim3 | 1709 | 237
[33 empty] | Trend |  | 101122 | Lim3LO_Trend | York RTU.Heating Control.Heat Limit3 Switch Lockout | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Fault.Heating Stage 3 | Heat Limit3 Switch Lockout | 1675 | 126 |  |  | Lim3LO | 1709 | 238
[33 empty] | Trend |  | 101124 | OprHtg-Sp_Trend | York RTU.Heating Control.CV Operating Heating Setpoint | Present Value |  | 100 | 900 | [5 empty] | Trend |  |  | Views.Trend.Heating.Status | Operating Heating Setpoint | 1675 | 1175 |  |  | OprHtg-Sp | 2645 | 441
[33 empty] | Trend |  | 101125 | H1_Trend | York RTU.Heating Control.Staged Heat Control.Heating Stage 1.Heat Stage Command | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Heating.Stage 1 | Heating Stage Command 1 | 1714 | 149 |  |  | Heating Stage Command 1 | 1714 | 149
[33 empty] | Trend |  | 101126 | H1-S_Trend | York RTU.Heating Control.Staged Heat Control.Heating Stage 1.Heat Stage Status | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Heating.Stage 1 | Heating Stage 1 Enabled | 1714 | 104 |  |  | Heating Stage 1 Enabled | 1714 | 104
[33 empty] | Trend |  | 101127 | H2_Trend | York RTU.Heating Control.Staged Heat Control.Heating Stage 2.Heat Stage Command | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Heating.Stage 2 | Heating Stage Command 2 | 1714 | 150 |  |  | Heating Stage Command 2 | 1714 | 150
[33 empty] | Trend |  | 101128 | H2-S_Trend | York RTU.Heating Control.Staged Heat Control.Heating Stage 2.Heat Stage Status | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Heating.Stage 2 | Heating Stage 2 Status | 1714 | 109 |  |  | Heating Stage 2 Status | 1714 | 109
[33 empty] | Trend |  | 101129 | H3_Trend | York RTU.Heating Control.Staged Heat Control.Heating Stage 3.Heat Stage Command | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Heating.Stage 3 | Heating Stage Command 3 | 1714 | 151 |  |  | Heating Stage Command 3 | 1714 | 151
[33 empty] | Trend |  | 101130 | H3-S_Trend | York RTU.Heating Control.Staged Heat Control.Heating Stage 3.Heat Stage Status | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Heating.Stage 3 | Heating Stage 3 Status | 1714 | 115 |  |  | Heating Stage 3 Status | 1714 | 115
[33 empty] | Trend |  | 101131 | RevVlv_Trend | York RTU.Heat Pump Control.Reversing Valve | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Misc.Heat Pump | Reversing Valve | 1675 | 482 |  |  | RevVlv | 1709 | 613
[33 empty] | Trend |  | 101132 | Econ_Trend | York RTU.Economizer.Economizer Damper % Command | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Economizer | Economizer Damper % Command | 1675 | 51 |  |  | Econ | 1709 | 282
[33 empty] | Trend |  | 101133 | Econ-Free_Trend | York RTU.Economizer.Econ Free Cooling Available | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Economizer | Econ Free Cooling Available | 1675 | 52 |  |  | Econ-Free | 1709 | 283
[33 empty] | Trend |  | 101134 | Econ-S_Trend | York RTU.Economizer.Economizer Status | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Status | Economizer Status | 1675 | 53 |  |  | Econ-S | 1709 | 284
[33 empty] | Trend |  | 101134 | Econ-S_Trend | York RTU.Economizer.Economizer Status | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Economizer | Economizer Status | 1675 | 53 |  |  | Econ-S | 1709 | 284
[33 empty] | Trend |  | 101135 | MAT_Trend | York RTU.Economizer.Mixed Air Temperature | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Status | Mixed Air Temperature | 1675 | 62 |  |  | MAT | 1709 | 293
[33 empty] | Trend |  | 101135 | MAT_Trend | York RTU.Economizer.Mixed Air Temperature | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Sensors | Mixed Air Temperature | 1675 | 62 |  |  | MAT | 1709 | 293
[33 empty] | Trend |  | 101137 | RA-Enth_Trend | York RTU.Economizer.Return Air Enthalpy | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Economizer | Return Air Enthalpy | 1675 | 64 |  |  | RA-Enth | 1709 | 296
[33 empty] | Trend |  | 101138 | ExFan_Trend | York RTU.Exhaust Fan Control.Exhaust Fan Command | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Fan.Exhaust Fan | Exhaust Fan Command | 1675 | 235 |  |  | ExFan | 1709 | 309
[33 empty] | Trend |  | 101139 | ExFanVFD_Trend | York RTU.Exhaust Fan Control.Exhaust Fan VFD % Command | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Fan.Exhaust Fan | Exhaust Fan VFD % Command | 1675 | 236 |  |  | ExFanVFD | 1709 | 310
[33 empty] | Trend |  | 101140 | Bldg-Sp_Trend | York RTU.Exhaust Fan Control.Building Pressure Setpoint | Present Value |  | 100 | 900 | [5 empty] | Trend |  |  | Views.Trend.Economizer | Building Pressure Setpoint | 1675 | 240 |  |  | Bldg-Sp | 1709 | 314
[33 empty] | Trend |  | 101141 | BldgPres _Trend | York RTU.Exhaust Fan Control.Building Static Pressure | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Economizer | Building Static Pressure | 1675 | 241 |  |  | BldgPres | 1709 | 315
[33 empty] | Trend |  | 101142 | HGR_Trend | York RTU.Hot Gas Reheat.Hot Gas Reheat Command | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Misc.Hot Gas Reheat | Hot Gas Reheat Command | 1675 | 250 |  |  | HGR | 1709 | 324
[33 empty] | Trend |  | 101143 | HGR-S_Trend | York RTU.Hot Gas Reheat.Hot Gas Reheat Status | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Status | Hot Gas Reheat Status | 1675 | 251 |  |  | HGR-S | 1709 | 325
[33 empty] | Trend |  | 101143 | HGR-S_Trend | York RTU.Hot Gas Reheat.Hot Gas Reheat Status | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Misc.Hot Gas Reheat | Hot Gas Reheat Status | 1675 | 251 |  |  | HGR-S | 1709 | 325
[33 empty] | Trend |  | 101144 | HGRHum-Sp_Trend | York RTU.Hot Gas Reheat.Hot Gas Reheat Humidity Setpoint | Present Value |  | 100 | 900 | [5 empty] | Trend |  |  | Views.Trend.Misc.Hot Gas Reheat | Hot Gas Reheat Humidity Setpoint | 1675 | 252 |  |  | HGRHum-Sp | 1709 | 326
[33 empty] | Trend |  | 101145 | MOAFlow-Sp_Trend | York RTU.Air Monitor Station.Fresh Air Intake Setpoint | Present Value |  | 100 | 900 | [5 empty] | Trend |  |  | Views.Trend.Misc.Demand Ventilation | Fresh Air Intake Setpoint | 1675 | 255 |  |  | MOAFlow-Sp | 1709 | 329
[33 empty] | Trend |  | 101146 | Fr Air_Trend | York RTU.Air Monitor Station.Fresh Air Intake Value | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Misc.Demand Ventilation | Fresh Air Intake Value | 1675 | 256 |  |  | Fr Air | 1709 | 330
[33 empty] | Trend |  | 101147 | RAT_Trend | York RTU.HVAC Zone.Return Air Temperature | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Status | Return Air Temperature | 1675 | 65 |  |  | RAT | 1709 | 297
[33 empty] | Trend |  | 101149 | OprSZVAVOprClg-Sp_Trend | York RTU.Cooling Control.SZ VAV Operating Cooling Setpoint | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Cooling.Status | SZ VAV Operating Cooling Setpoint | 1675 | 648 |  |  | OprSZVAVClg-Sp | 1709 | 660
[33 empty] | Trend |  | 101150 | ModCondFan1Out_Trend | York RTU.Cooling Control.Modulating Condenser Fan 1 Output | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Fan.Condenser Fans | Modulating Condenser Fan 1 Output | 2644 | 293 |  |  | ModCondFan1Out | 2645 | 312
[33 empty] | Trend |  | 101151 | ModCondFan2Out_Trend | York RTU.Cooling Control.Modulating Condenser Fan 2 Output | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Fan.Condenser Fans | Modulating Condenser Fan 2 Output | 2644 | 294 |  |  | ModCondFan2Out | 2645 | 313
[33 empty] | Trend |  | 101152 | ModCompOut_Trend | York RTU.Cooling Control.Modulating Compressor Output | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Cooling.Stage 1 | Modulating Compressor Output | 2644 | 292 |  |  | ModCompOut | 2645 | 311
[33 empty] | Trend |  | 101153 | DLP-1_Trend | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Discharge Line Pressure | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Diagnostics.Cooling Stage 1 | Discharge Line Pressure 1 | 2644 | 378 |  |  | DLP1 | 2645 | 386
[33 empty] | Trend |  | 101154 | DLT-1_Trend | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Discharge Line Temperature | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Diagnostics.Cooling Stage 1 | Discharge Line Temperature 1 | 2644 | 380 |  |  | DLT1 | 2645 | 388
[33 empty] | Trend |  | 101155 | DLP-2_Trend | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Discharge Line Pressure | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Diagnostics.Cooling Stage 2 | Discharge Line Pressure 2 | 2644 | 379 |  |  | DLP2 | 2645 | 387
[33 empty] | Trend |  | 101156 | DLT-2_Trend | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Discharge Line Temperature | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Diagnostics.Cooling Stage 2 | Discharge Line Temperature 2 | 2644 | 381 |  |  | DLT2 | 2645 | 389
[33 empty] | Trend |  | 101157 | OprHGRTempSp_Trend | York RTU.Hot Gas Reheat.Operational HGR Temperature Sp | Present Value |  | 300 | 300
[33 empty] | Trend |  | 101158 | OprEvapTempSp_Trend | York RTU.Hot Gas Reheat.Operational Evap Temperature Sp | Present Value |  | 300 | 300
[33 empty] | Trend |  | 101159 | ModHGR_Trend | York RTU.Hot Gas Reheat.Hot Gas Reheat Command | Present Value |  | 300 | 300
[33 empty] | Trend |  | 101160 | EvapCoilTemp_Trend | York RTU.Hot Gas Reheat.Evaporator Coil Temp | Present Value |  | 300 | 300
[33 empty] | Trend |  | 101161 | EconDampPos_Trend | York RTU.Economizer.Economizer Damper Position | Present Value |  | 300 | 300
[33 empty] | Trend |  | 101162 | HWV_Trend | York RTU.Heating Control.Hydronic Heat Control.Hydronic Heat Valve % Command | Present Value |  | 300 | 300
[33 empty] | Trend |  | 101163 | OprOAH_Trend | York RTU.Weather Information.Operational Outdoor Air Humidity | Present Value |  | 300 | 300
[33 empty] | Trend |  | 101164 | SucSuperheat1_Trend | York RTU.Cooling Control.Suction Superheat 1 | Present Value |  | 300 | 300 | [5 empty] | Trend |  |  | Views.Trend.Diagnostics.Cooling Stage 1 | Suction Superheat 1 | 2644 | 366 |  |  | SucSuperheat1 | 2645 | 374
[33 empty] | Trend |  | 101165 | A2LAlarm_Trend | York RTU.Cooling Control.A2L Leak Detector Alarm | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Fault.Misc | A2L Leak Detector Alarm | 1714 | 276 |  |  | A2LLeakAlarm | 1709 | 787
[33 empty] | Trend |  | 101166 | A2LAlarmLO_Trend | York RTU.Cooling Control.A2L Leak Detector Alarm-Lockout | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Fault.Misc | A2L Leak Detector Alarm-Lockout | 1714 | 280 |  |  | A2LLeakAlarm-LO | 1709 | 791
[33 empty] | Trend |  | 101167 | COS_Trend | York RTU.Cooling Control.Condensate Overflow Switch | Present Value |  | 25 | 0 | [5 empty] | Trend |  |  | Views.Trend.Fault.Misc | Condensate Overflow Switch | 1714 | 277 |  |  | COS | 1709 | 788
[47 empty] | View | FALSE |  | Status |  | 1712 | 0 |  | Status |  | 1708 | 25
[47 empty] | Group |  | TRUE | Views.Status.Thermostat |  | 1714 | 36 |  | Views.Status.Thermostat |  | 1709 | 415
[47 empty] | Group |  | TRUE | Views.Status.Smoke Control |  | 1714 | 30 |  | Views.Status.SmokeCtrl |  | 1709 | 409
[47 empty] | Group |  | TRUE | Views.Status.Status |  | 1714 | 35 |  | Views.Status.Status |  | 1709 | 414
[47 empty] | Group |  | TRUE | Views.Status.Control |  | 1714 | 5 |  | Views.Status.SysCntlrs |  | 1709 | 466
[47 empty] | View | FALSE |  | Summary |  | 1712 | 1 |  | Summary |  | 1708 | 27
[47 empty] | Group |  | FALSE | Views.Summary.Sensors |  | 1714 | 26 |  | Views.Summary.Sensors |  | 1709 | 405
[47 empty] | Group |  | TRUE | Views.Summary.Sensors.Operational Mode |  | 1675 | 855 |  | Views.Summary.Sensors.OprMode |  | 1709 | 539
[47 empty] | Group |  | TRUE | Views.Summary.Sensors.Sensors |  | 1714 | 26 |  | Views.Summary.Sensors.Sensors |  | 1709 | 405
[47 empty] | Group |  | FALSE | Views.Summary.Unit |  | 1714 | 153 |  | Views.Summary.Unit |  | 1709 | 472
[47 empty] | View | FALSE |  | Commissioning |  | 1712 | 2 |  | Commission |  | 1708 | 28
[47 empty] | Group |  | FALSE | Views.Commissioning.Quick Start |  | 1714 | 223 |  | Views.Commission.Quick Start |  | 1709 | 720
[47 empty] | Group |  | FALSE | Views.Commissioning.Standard |  | 1709 | 610 |  | Views.Commission.Standard |  | 1709 | 610
[47 empty] | Group |  | FALSE | Views.Commissioning.Options |  | 1712 | 44 |  | Views.Commission.Options |  | 1712 | 44
[47 empty] | Group |  | FALSE | Views.Commissioning.Network Setup |  | 1712 | 15 |  | Views.Commission.Network Setup |  | 1712 | 15
[47 empty] | Group |  | FALSE | Views.Commissioning.Commissioning Mode |  | 1675 | 1244 |  | Views.Commission.Commissioning Mode |  | 1675 | 1244
[47 empty] | View | FALSE |  | Controller |  | 1712 | 3 |  | Controller |  | 1708 | 29
[47 empty] | Group |  | FALSE | Views.Controller.Network |  | 1714 | 19 |  | Views.Controller.Network |  | 1709 | 398
[47 empty] | Group |  | FALSE | Views.Controller.Firmware |  | 1714 | 11 |  | Views.Controller.Firm |  | 1709 | 391
[47 empty] | Group |  | TRUE | Views.Controller.Firmware.UCB |  | 1714 | 154 |  | Views.Controller.Firm.UCB |  | 1709 | 467
[47 empty] | Group |  | TRUE | Views.Controller.Firmware.Economizer |  | 1714 | 8 |  | Views.Controller.Firm.Econ |  | 1709 | 282 | York RTU.System Controllers.Econ Controller:Present Value <> Not Present
[47 empty] | Group |  | TRUE | Views.Controller.Firmware.4 Stage |  | 1714 | 155 |  | Views.Controller.Firm.4 Stage |  | 1714 | 155 | York RTU.System Controllers.4 Stage Controller:Present Value <> Not Present
[47 empty] | Group |  | TRUE | Views.Controller.Firmware.FDD Manager |  | 1714 | 156 |  | Views.Controller.Firm.FDD Manager |  | 1714 | 156 | York RTU.System Controllers.FDD Manager Controller:Present Value <> Not Present
[47 empty] | Group |  | TRUE | Views.Controller.Firmware.FDD Subordinate |  | 1714 | 157 |  | Views.Controller.Firm.FDD Subordinate |  | 1714 | 157 | York RTU.System Controllers.FDD Subordinate Controller:Present Value <> Not Present
[47 empty] | Group |  | FALSE | Views.Controller.Bluetooth |  | 1714 | 271 |  | Views.Controller.Bluetooth |  | 1709 | 771 | York RTU.Bluetooth.Status:Present Value = Normal
[47 empty] | Group |  | FALSE | Views.Controller.Network Inputs |  | 1714 | 20 |  | Views.Controller.NetworkInputs |  | 1709 | 399
[47 empty] | Group |  | FALSE | Views.Controller.FDD |  | 1714 | 179 |  | Views.Controller.FDD |  | 1709 | 611
[47 empty] | Group |  | FALSE | Views.Controller.Time |  | 1675 | 271 |  | Views.Controller.Time |  | 1709 | 342
[47 empty] | Group |  | FALSE | Views.Controller.Description |  | 1675 | 2 |  | Views.Controller.Descrip |  | 1709 | 473
[47 empty] | Group |  | FALSE | Views.Controller.Controller Info |  | 1712 | 26 |  | Views.Controller.Controller Info |  | 1712 | 26
[47 empty] | View | FALSE |  | Details |  | 1712 | 4 |  | Details |  | 1708 | 31
[47 empty] | Group |  | FALSE | Views.Details.Occupancy Status |  | 1675 | 757 |  | Views.Details.OCC |  | 1709 | 380
[47 empty] | Group |  | FALSE | Views.Details.Cooling |  | 1714 | 6 |  | Views.Details.Clg |  | 1709 | 388
[47 empty] | Group |  | FALSE | Views.Details.Cooling.Setup |  | 1714 | 29 |  | Views.Details.Clg.Setup |  | 1709 | 408
[47 empty] | Group |  | FALSE | Views.Details.Cooling.Service |  | 1714 | 27 |  | Views.Details.Clg.Service |  | 1709 | 406
[47 empty] | Group |  | TRUE | Views.Details.Cooling.Service.Unit |  | 1714 | 153 |  | Views.Details.Clg.Service.Unit |  | 1709 | 472
[47 empty] | Group |  | TRUE | Views.Details.Cooling.Service.Stage 1 |  | 1714 | 31 |  | Views.Details.Clg.Service.Stage 1 |  | 1709 | 410
[47 empty] | Group |  | TRUE | Views.Details.Cooling.Service.Stage 2 |  | 1714 | 32 |  | Views.Details.Clg.Service.Stage 2 |  | 1709 | 411 | York RTU.Cooling Control.Cooling Stages Available:Present Value > 1
[47 empty] | Group |  | TRUE | Views.Details.Cooling.Service.Stage 3 |  | 1714 | 33 |  | Views.Details.Clg.Service.Stage 3 |  | 1709 | 412 | York RTU.Cooling Control.Cooling Stages Available:Present Value > 2
[47 empty] | Group |  | TRUE | Views.Details.Cooling.Service.Stage 4 |  | 1714 | 34 |  | Views.Details.Clg.Service.Stage 4 |  | 1709 | 413 | York RTU.Cooling Control.Cooling Stages Available:Present Value > 3
[47 empty] | Group |  | FALSE | Views.Details.Cooling.Sensors |  | 1714 | 26 |  | Views.Details.Clg.Sensors |  | 1709 | 405
[47 empty] | Group |  | FALSE | Views.Details.Cooling.Safeties |  | 1714 | 25 |  | Views.Details.Clg.Safeties |  | 1709 | 404
[47 empty] | Group |  | FALSE | Views.Details.Cooling.Misc |  | 1714 | 18 |  | Views.Details.Clg.Misc |  | 1709 | 397
[47 empty] | Group |  | FALSE | Views.Details.Heating |  | 1714 | 12 |  | Views.Details.Htg |  | 1709 | 392
[47 empty] | Group |  | FALSE | Views.Details.Heating.Setup |  | 1714 | 29 |  | Views.Details.Htg.Setup |  | 1709 | 408
[47 empty] | Group |  | FALSE | Views.Details.Heating.Service |  | 1714 | 27 |  | Views.Details.Htg.Service |  | 1709 | 406
[47 empty] | Group |  | FALSE | Views.Details.Heating.Safeties |  | 1714 | 25 |  | Views.Details.Htg.Safeties |  | 1709 | 404
[47 empty] | Group |  | FALSE | Views.Details.Heating.Proportional |  | 1714 | 194 |  | Views.Details.Htg.Prop |  | 1709 | 637 | York RTU.Heating Control Type:Present Value = Proportional
[47 empty] | Group |  | TRUE | Views.Details.Heating.Proportional.Setup |  | 1714 | 29 |  | Views.Details.Htg.Prop.Setup |  | 1709 | 408
[47 empty] | Group |  | TRUE | Views.Details.Heating.Proportional.Service |  | 1714 | 27 |  | Views.Details.Htg.Prop.Service |  | 1709 | 406
[47 empty] | Group |  | FALSE | Views.Details.Indoor Fan |  | 1714 | 16 |  | Views.Details.Fan |  | 1709 | 79
[47 empty] | Group |  | TRUE | Views.Details.Indoor Fan.Setup |  | 1714 | 29 |  | Views.Details.Fan.Setup |  | 1709 | 408
[47 empty] | Group |  | TRUE | Views.Details.Indoor Fan.Service |  | 1714 | 27 |  | Views.Details.Fan.Service |  | 1709 | 406
[47 empty] | Group |  | FALSE | Views.Details.Economizer |  | 1714 | 8 |  | Views.Details.Econ |  | 1709 | 282 | York RTU.System Controllers.Econ Controller:Present Value <> Not Present
[47 empty] | Group |  | TRUE | Views.Details.Economizer.Setup |  | 1714 | 29 |  | Views.Details.Econ.Setup |  | 1709 | 408
[47 empty] | Group |  | TRUE | Views.Details.Economizer.Service |  | 1714 | 27 |  | Views.Details.Econ.Service |  | 1709 | 406
[47 empty] | Group |  | FALSE | Views.Details.Demand Ventilation |  | 1714 | 7 |  | Views.Details.DVent |  | 1709 | 389 | York RTU.System Controllers.Econ Controller:Present Value <> Not Present
[47 empty] | Group |  | FALSE | Views.Details.Air Monitor Station |  | 1714 | 0 |  | Views.Details.AirMonStation |  | 1709 | 382 | York RTU.System Controllers.Econ Controller:Present Value <> Not Present
[47 empty] | Group |  | FALSE | Views.Details.Power Exhaust |  | 1714 | 23 |  | Views.Details.PowerEx |  | 1709 | 402 | York RTU.System Controllers.Econ Controller:Present Value <> Not Present
[47 empty] | Group |  | TRUE | Views.Details.Power Exhaust.Setup |  | 1714 | 29 |  | Views.Details.PowerEx.Setup |  | 1709 | 408
[47 empty] | Group |  | TRUE | Views.Details.Power Exhaust.Service |  | 1714 | 27 |  | Views.Details.PowerEx.Service |  | 1709 | 406
[47 empty] | Group |  | FALSE | Views.Details.FanVFD |  | 1709 | 67 |  | Views.Details.FanVFD |  | 1709 | 67
[47 empty] | Group |  | TRUE | Views.Details.FanVFD.Setup |  | 1714 | 29 |  | Views.Details.FanVFD.Setup |  | 1709 | 408
[47 empty] | Group |  | TRUE | Views.Details.FanVFD.Service |  | 1714 | 27 |  | Views.Details.FanVFD.Service |  | 1709 | 406
[47 empty] | Group |  | FALSE | Views.Details.Single Zone VAV |  | 1714 | 195 |  | Views.Details.SZ VAV |  | 1709 | 638 | York RTU.SZ VAV Enabled:Present Value <> Off
[47 empty] | Group |  | TRUE | Views.Details.Single Zone VAV.Setup |  | 1714 | 29 |  | Views.Details.SZ VAV.Setup |  | 1709 | 408
[47 empty] | Group |  | TRUE | Views.Details.Single Zone VAV.Service |  | 1714 | 27 |  | Views.Details.SZ VAV.Service |  | 1709 | 406
[47 empty] | Group |  | FALSE | Views.Details.Hot Gas Reheat |  | 1714 | 13 |  | Views.Details.HGR |  | 1709 | 324 | York RTU.Hot Gas Reheat.HGR-Inst:Present Value = 1
[47 empty] | Group |  | TRUE | Views.Details.Hot Gas Reheat.Setup |  | 1714 | 29 |  | Views.Details.HGR.Setup |  | 1709 | 408
[47 empty] | Group |  | TRUE | Views.Details.Hot Gas Reheat.Service |  | 1714 | 27 |  | Views.Details.HGR.Service |  | 1709 | 406
[47 empty] | Group |  | FALSE | Views.Details.Mod Hot Gas Reheat |  | 1714 | 252 |  | Views.Details.ModHGR |  | 1709 | 737 | York RTU.Hot Gas Reheat.HGR-Inst:Present Value > 1
[47 empty] | Group |  | TRUE | Views.Details.Mod Hot Gas Reheat.Setup |  | 1714 | 29 |  | Views.Details.ModHGR.Setup |  | 1709 | 408
[47 empty] | Group |  | TRUE | Views.Details.Mod Hot Gas Reheat.Service |  | 1714 | 27 |  | Views.Details.ModHGR.Service |  | 1709 | 406
[47 empty] | Group |  | FALSE | Views.Details.Heat Pump |  | 1714 | 180 |  | Views.Details.HeatPmp |  | 1709 | 618 | York RTU.Heat Pump Control.Number of Heat Pump Stages Installed:Present Value > 0
[47 empty] | Group |  | FALSE | Views.Details.ERV |  | 1675 | 1016 |  | Views.Details.ERV |  | 1675 | 1016 | York RTU.System Controllers.Econ Controller:Present Value <> Not Present
[47 empty] | Group |  | FALSE | Views.Details.Load Shed |  | 1714 | 162 |  | Views.Details.T24LoadShed |  | 1709 | 532
[47 empty] | Group |  | FALSE | Views.Details.Verasys |  | 1675 | 1690 |  | Views.Details.Verasys |  | 1675 | 1690 | York RTU.CCS Online:Present Value = Yes
[47 empty] | View | TRUE |  | Clone |  | 1712 | 5
[47 empty] | Group |  | FALSE | Views.Clone.Full Clone |  | 1712 | 6 |  |  |  | 1708 | 7
[47 empty] | Group |  | FALSE | Views.Clone.Partial Clone 1 |  | 1712 | 7 |  |  |  | 1708 | 8
[47 empty] | Group |  | FALSE | Views.Clone.Network Override |  | 1712 | 9 |  |  |  | 1712 | 9
[47 empty] | View | TRUE |  | BACnet Objects |  | 1712 | 8
[47 empty] | View | FALSE |  | Trend |  | 1712 | 24
[47 empty] | Group |  | FALSE | Views.Trend.Status |  | 1712 | 0 |  |  |  | 1712 | 0
[47 empty] | Group |  | FALSE | Views.Trend.Cooling |  | 1714 | 6 |  |  |  | 1714 | 6
[47 empty] | Group |  | FALSE | Views.Trend.Cooling.Status |  | 1712 | 0 |  |  |  | 1712 | 0
[47 empty] | Group |  | FALSE | Views.Trend.Cooling.Stage 1 |  | 1714 | 31 |  |  |  | 1714 | 31
[47 empty] | Group |  | FALSE | Views.Trend.Cooling.Stage 2 |  | 1714 | 32 |  |  |  | 1714 | 32 | York RTU.Cooling Control.Number of Cooling Stages Installed:Present Value > 1
[47 empty] | Group |  | FALSE | Views.Trend.Cooling.Stage 3 |  | 1714 | 33 |  |  |  | 1714 | 33 | York RTU.Cooling Control.Number of Cooling Stages Installed:Present Value > 2
[47 empty] | Group |  | FALSE | Views.Trend.Cooling.Stage 4 |  | 1714 | 34 |  |  |  | 1714 | 34 | York RTU.Cooling Control.Number of Cooling Stages Installed:Present Value > 3
[47 empty] | Group |  | FALSE | Views.Trend.Heating |  | 1714 | 12 |  |  |  | 1714 | 12
[47 empty] | Group |  | FALSE | Views.Trend.Heating.Status |  | 1712 | 0 |  |  |  | 1712 | 0
[47 empty] | Group |  | FALSE | Views.Trend.Heating.Stage 1 |  | 1714 | 31 |  |  |  | 1714 | 31 | York RTU.Heating Control.Staged Heat Control.Number of Heating Stages Installed:Present Value > 0
[47 empty] | Group |  | FALSE | Views.Trend.Heating.Stage 2 |  | 1714 | 32 |  |  |  | 1714 | 32 | York RTU.Heating Control.Staged Heat Control.Number of Heating Stages Installed:Present Value > 1
[47 empty] | Group |  | FALSE | Views.Trend.Heating.Stage 3 |  | 1714 | 33 |  |  |  | 1714 | 33 | York RTU.Heating Control.Staged Heat Control.Number of Heating Stages Installed:Present Value > 2
[47 empty] | Group |  | FALSE | Views.Trend.Fan |  | 1714 | 10 |  |  |  | 1714 | 10
[47 empty] | Group |  | FALSE | Views.Trend.Fan.Indoor Fan |  | 1714 | 16 |  |  |  | 1714 | 16
[47 empty] | Group |  | FALSE | Views.Trend.Fan.Exhaust Fan |  | 1790 | 0 |  |  |  | 1790 | 0 | York RTU.Exhaust Type:Present Value <> None
[47 empty] | Group |  | FALSE | Views.Trend.Fan.Condenser Fans |  | 1714 | 213 |  |  |  | 1714 | 213
[47 empty] | Group |  | FALSE | Views.Trend.Sensors |  | 1714 | 26 |  |  |  | 1714 | 26
[47 empty] | Group |  | FALSE | Views.Trend.Economizer |  | 1714 | 8 |  |  |  | 1714 | 8 | York RTU.System Controllers.Econ Controller:Present Value <> Not Present
[47 empty] | Group |  | FALSE | Views.Trend.Misc |  | 1714 | 18 |  |  |  | 1714 | 18
[47 empty] | Group |  | FALSE | Views.Trend.Misc.Heat Pump |  | 1714 | 180 |  |  |  | 1714 | 180 | York RTU.Heat Pump Control.Number of Heat Pump Stages Installed:Present Value > 0
[47 empty] | Group |  | FALSE | Views.Trend.Misc.Hot Gas Reheat |  | 1714 | 13 |  |  |  | 1714 | 13 | York RTU.Hot Gas Reheat.Hot Gas Reheat Enabled For Operation:Present Value = Yes
[47 empty] | Group |  | FALSE | Views.Trend.Misc.Demand Ventilation |  | 1714 | 7 |  |  |  | 1714 | 7
[47 empty] | Group |  | FALSE | Views.Trend.Fault |  | 1714 | 214 |  |  |  | 1714 | 214
[47 empty] | Group |  | FALSE | Views.Trend.Fault.Misc |  | 1714 | 18 |  |  |  | 1714 | 18
[47 empty] | Group |  | FALSE | Views.Trend.Fault.Heating Stage 1 |  | 1714 | 215 |  |  |  | 1714 | 215 | York RTU.Heating Control.Staged Heat Control.Number of Heating Stages Installed:Present Value > 0
[47 empty] | Group |  | FALSE | Views.Trend.Fault.Heating Stage 2 |  | 1714 | 216 |  |  |  | 1714 | 216 | York RTU.Heating Control.Staged Heat Control.Number of Heating Stages Installed:Present Value > 1
[47 empty] | Group |  | FALSE | Views.Trend.Fault.Heating Stage 3 |  | 1714 | 217 |  |  |  | 1714 | 217 | York RTU.Heating Control.Staged Heat Control.Number of Heating Stages Installed:Present Value > 2
[47 empty] | Group |  | FALSE | Views.Trend.Fault.Cooling Stage 1 |  | 1714 | 218 |  |  |  | 1714 | 218
[47 empty] | Group |  | FALSE | Views.Trend.Fault.Cooling Stage 2 |  | 1714 | 219 |  |  |  | 1714 | 219 | York RTU.Cooling Control.Number of Cooling Stages Installed:Present Value > 1
[47 empty] | Group |  | FALSE | Views.Trend.Fault.Cooling Stage 3 |  | 1714 | 220 |  |  |  | 1714 | 220 | York RTU.Cooling Control.Number of Cooling Stages Installed:Present Value > 2
[47 empty] | Group |  | FALSE | Views.Trend.Fault.Cooling Stage 4 |  | 1714 | 221 |  |  |  | 1714 | 221 | York RTU.Cooling Control.Number of Cooling Stages Installed:Present Value > 3
[47 empty] | Group |  | FALSE | Views.Trend.Diagnostics |  | 1714 | 198 |  |  |  | 1714 | 198 | York RTU.System Controllers.FDD Manager Controller:Present Value <> Not Present
[47 empty] | Group |  | FALSE | Views.Trend.Diagnostics.Cooling Stage 1 |  | 1714 | 218 |  |  |  | 1714 | 218
[47 empty] | Group |  | FALSE | Views.Trend.Diagnostics.Cooling Stage 2 |  | 1714 | 219 |  |  |  | 1714 | 219 | York RTU.Cooling Control.Number of Cooling Stages Installed:Present Value > 1
[47 empty] | Group |  | FALSE | Views.Trend.Diagnostics.Cooling Stage 3 |  | 1714 | 220 |  |  |  | 1714 | 220 | York RTU.Cooling Control.Number of Cooling Stages Installed:Present Value > 2
[47 empty] | Group |  | FALSE | Views.Trend.Diagnostics.Cooling Stage 4 |  | 1714 | 221 |  |  |  | 1714 | 221 | York RTU.Cooling Control.Number of Cooling Stages Installed:Present Value > 3
[47 empty] | View | FALSE |  | Set Schedule |  | 1712 | 25

## ViewDef
Type | Internal View | Minor Group | Folder Fullname (Long) | Name (Long) | Name SetId (Long) | Name EnumId (Long) | Custom Name | Folder Fullname (Short) | Name (Short) | Name SetId (Short) | Name EnumId (Short) | Presence Indicator | Remarks | Property Name | Prop. Name SetId | Prop. Name EnumId | Prop. Id | Requ. | Write-able | Priority Flag | Data Type Id | Data Type | Display Prec. (IP) | Unit (IP) | Unit Id (IP) | Min Value (IP) | Max Value (IP) | Min Prop. (IP) | Max Prop. (IP) | Display Prec. (SI) | Unit (SI) | Unit Id (SI) | Min Value (SI) | Max Value (SI) | Min Prop. (SI) | Max Prop. (SI) | String Max Length | MultiState Enums | EM Object Id
View | FALSE |  | Views.Status | Status | 1712 | 0 |  | Views.Status | Status | 1708 | 25
Group |  | TRUE | Views.Status.Thermostat | Thermostat | 1714 | 36 |  | Views.Status.Thermostat | Thermostat | 1709 | 415
Value |  |  | Views.Status.Thermostat | Y1 - Thermostat | 1675 | 150 |  | Views.Status.Thermostat | Y1-Tstat | 1709 | 11 |  |  | Y1 - Thermostat | 1675 | 150 | 7000 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 2
Value |  |  | Views.Status.Thermostat | Y2 - Thermostat | 1675 | 151 |  | Views.Status.Thermostat | Y2-Tstat | 1709 | 12 |  |  | Y2 - Thermostat | 1675 | 151 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 2
Value |  |  | Views.Status.Thermostat | Y3 - Thermostat | 1675 | 152 |  | Views.Status.Thermostat | Y3-Tstat | 1709 | 13 |  |  | Y3 - Thermostat | 1675 | 152 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 2
Value |  |  | Views.Status.Thermostat | Y4 - Thermostat | 1675 | 153 |  | Views.Status.Thermostat | Y4-Tstat | 1709 | 14 |  |  | Y4 - Thermostat | 1675 | 153 | 7003 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 2
Value |  |  | Views.Status.Thermostat | W1 - Thermostat | 1675 | 154 |  | Views.Status.Thermostat | W1-Tstat | 1709 | 15 |  |  | W1 - Thermostat | 1675 | 154 | 7004 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 2
Value |  |  | Views.Status.Thermostat | W2 - Thermostat | 1675 | 155 |  | Views.Status.Thermostat | W2-Tstat | 1709 | 16 |  |  | W2 - Thermostat | 1675 | 155 | 7005 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 2
Value |  |  | Views.Status.Thermostat | W3 - Thermostat | 1675 | 156 |  | Views.Status.Thermostat | W3-Tstat | 1709 | 17 |  |  | W3 - Thermostat | 1675 | 156 | 7006 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 2
Value |  |  | Views.Status.Thermostat | G - Thermostat | 1675 | 157 |  | Views.Status.Thermostat | G-Tstat | 1709 | 18 |  |  | G - Thermostat | 1675 | 157 | 7007 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 2
Value |  |  | Views.Status.Thermostat | Local Occupancy Input - Thermostat | 1675 | 158 |  | Views.Status.Thermostat | Occ-Tstat | 1709 | 19 |  |  | Local Occupancy Input - Thermostat | 1675 | 158 | 7008 | TRUE | FALSE | FALSE | 9 | MultiState |  | On/Off | 1686 | [5 empty] | On/Off | 1686 | [5 empty] | 0 = On 1 = Off | 2
Group |  | TRUE | Views.Status.Smoke Control | Smoke Control | 1714 | 30 |  | Views.Status.SmokeCtrl | SmokeCtrl | 1709 | 409
Value |  |  | Views.Status.Smoke Control | Operating Purge Command | 1675 | 258 |  | Views.Status.SmokeCtrl | OprPurgeCmd | 1709 | 332 |  |  | Operating Purge Command | 1675 | 258 | 7000 | TRUE | FALSE | FALSE | 9 | MultiState |  | False/True | 1701 | [5 empty] | False/True | 1701 | [5 empty] | 0 = False 1 = True | 27
Value |  |  | Views.Status.Smoke Control | Purge Command Source | 1675 | 259 |  | Views.Status.SmokeCtrl | PurgeCmdSrc | 1709 | 333 |  |  | Purge Command Source | 1675 | 259 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  | Effective Input Source 2 | 1732 | [5 empty] | Effective Input Source 2 | 1732 | [5 empty] | 0 = Unreliable 1 = Local Input 2 = Network Sensor 3 = High Priority ... | 27
Value |  |  | Views.Status.Smoke Control | Local Purge Command Input | 1675 | 260 |  | Views.Status.SmokeCtrl | Purge | 1709 | 334 |  |  | Local Purge Command Input | 1675 | 260 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  | False/True | 1701 | [5 empty] | False/True | 1701 | [5 empty] | 0 = False 1 = True | 27
Value |  |  | Views.Status.Smoke Control | Network Override Purge Command | 1675 | 261 |  | Views.Status.SmokeCtrl | NetPurge | 1709 | 335 |  |  | Network Override Purge Command | 1675 | 261 | 7003 | TRUE | TRUE | FALSE | 9 | MultiState |  | False/True | 1701 | [5 empty] | False/True | 1701 | [5 empty] | 0 = False 1 = True | 27
Value |  |  | Views.Status.Smoke Control | Shutdown Input/Smoke Detector | 1675 | 262 |  | Views.Status.SmokeCtrl | SD | 1709 | 336 |  |  | Shutdown Input/Smoke Detector | 1675 | 262 | 7004 | TRUE | FALSE | FALSE | 9 | MultiState |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 | [5 empty] | 0 = Normal 1 = Alarm | 27
Group |  | TRUE | Views.Status.Status | Status | 1714 | 35 |  | Views.Status.Status | Status | 1709 | 414
Value |  |  | Views.Status.Status | Unit Status | 1675 | 0 |  | Views.Status.Status | Unit-S | 1709 | 0 |  |  | Unit Status | 1675 | 0 | 7000 | TRUE | FALSE | FALSE | 9 | MultiState |  | SE RTU Unit Status | 1737 | [5 empty] | SE RTU Unit Status | 1737 | [5 empty] | 0 = Idle 1 = SD Alarm 2 = Purge Command 3 = Self Test ... | 1
Value |  |  | Views.Status.Status | Economizer Status | 1675 | 53 |  | Views.Status.Status | Econ-S | 1709 | 284 |  |  | Economizer Status | 1675 | 53 | 7003 | TRUE | FALSE | FALSE | 9 | MultiState |  | SE RTU Economizer Status | 1738 | [5 empty] | SE RTU Economizer Status | 1738 | [5 empty] | 0 = Disabled 1 = Damper Not Functional 2 = Purge 3 = Unavailable-Sensor Fault ... | 19
Value |  |  | Views.Status.Status | Exhaust Fan Status | 1675 | 237 |  | Views.Status.Status | ExF-S | 1709 | 311 |  |  | Exhaust Fan Status | 1675 | 237 | 7003 | TRUE | FALSE | FALSE | 9 | MultiState |  | SE RTU Exhaust Fan | 1745 | [5 empty] | SE RTU Exhaust Fan | 1745 | [5 empty] | 0 = Off-Idle 1 = On-Normal Command 2 = Off-Disabled 3 = Off-VFD Fault ... | 21
Value |  |  | Views.Status.Status | Fan Status | 1675 | 168 |  | Views.Status.Status | Fan-S | 1709 | 66 |  |  | Fan Status | 1675 | 168 | 7000 | TRUE | FALSE | FALSE | 9 | MultiState |  | SE RTU Fan Status | 1739 | [5 empty] | SE RTU Fan Status | 1739 | [5 empty] | 0 = Off-Idle 1 = On-Purge 2 = On-Gas Valve or Limit Fault 3 = On-Defrost ... | 3
Value |  |  | Views.Status.Status | Hot Gas Reheat Status | 1675 | 251 |  | Views.Status.Status | HGR-S | 1709 | 325 |  |  | Hot Gas Reheat Status | 1675 | 251 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  | SE RTU Hot Gas Reheat | 1744 | [5 empty] | SE RTU Hot Gas Reheat | 1744 | [5 empty] | 0 = Off-Idle 1 = On-Normal Command 2 = On-Alternate Operation Command 3 = Off-Disabled | 20
Value |  |  | Views.Status.Status | Cooling Status | 1675 | 69 |  | Views.Status.Status | Clg-S | 1709 | 93 |  |  | Cooling Status | 1675 | 69 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  | SE RTU Cooling Control Status | 1740 | [5 empty] | SE RTU Cooling Control Status | 1740 | [5 empty] | 0 = Off-Idle 1 = Thermostat Cooling 2 = Unoccupied Cooling 3 = Occupied Cooling ... | 4
Value |  |  | Views.Status.Status | Heating Status | 1675 | 106 |  | Views.Status.Status | Htg-S | 1709 | 225 |  |  | Heating Status | 1675 | 106 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  | SE RTU Heating Control Status | 1742 | [5 empty] | SE RTU Heating Control Status | 1742 | [5 empty] | 0 = Off-Idle 1 = On-Defrost 2 = SAT Tempering 3 = Morning Warmup ... | 13
Value |  |  | Views.Status.Status | Dirty Filter Switch | 1675 | 180 |  | Views.Status.Status | DFS | 1709 | 78 |  |  | Dirty Filter Switch | 1675 | 180 | 7012 | TRUE | FALSE | FALSE | 9 | MultiState |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 | [5 empty] | 0 = Normal 1 = Alarm | 3
Value |  |  | Views.Status.Status | UCB 24VAC Input | 1675 | 148 |  | Views.Status.Status | UCB24VForOutp | 1709 | 9 |  |  | UCB 24VAC Input | 1675 | 148 | 7009 | TRUE | FALSE | FALSE | 4 | Float | 10ths | V | 507:5 |  |  |  |  | 10ths | V | 507:5 | [6 empty] | 1
Group |  | TRUE | Views.Status.Control | Control | 1714 | 5 |  | Views.Status.SysCntlrs | SysCntlrs | 1709 | 466
Value |  |  | Views.Status.Control | Econ Controller | 1675 | 315 |  | Views.Status.SysCntlrs | EconCntlr | 1709 | 437 |  |  | Econ Controller | 1675 | 315 | 7004 | TRUE | FALSE | FALSE | 9 | MultiState |  | EIO Connection Status | 1662 | [5 empty] | EIO Connection Status | 1662 | [5 empty] | 0 = Not Present 1 = Offline 2 = Online | 29
Value |  |  | Views.Status.Control | 4 Stage Controller | 1675 | 316 |  | Views.Status.SysCntlrs | 4StgCntlr | 1709 | 438 |  |  | 4 Stage Controller | 1675 | 316 | 7005 | TRUE | FALSE | FALSE | 9 | MultiState |  | EIO Connection Status | 1662 | [5 empty] | EIO Connection Status | 1662 | [5 empty] | 0 = Not Present 1 = Offline 2 = Online | 29
Value |  |  | Views.Status.Control | FDD Manager Controller | 1675 | 317 |  | Views.Status.SysCntlrs | FDDMCntlr | 1709 | 439 |  |  | FDD Manager Controller | 1675 | 317 | 7006 | TRUE | FALSE | FALSE | 9 | MultiState |  | EIO Connection Status | 1662 | [5 empty] | EIO Connection Status | 1662 | [5 empty] | 0 = Not Present 1 = Offline 2 = Online | 29
Value |  |  | Views.Status.Control | FDD Subordinate Controller | 1675 | 318 |  | Views.Status.SysCntlrs | FDDSCntlr | 1709 | 440 |  |  | FDD Subordinate Controller | 1675 | 318 | 7007 | TRUE | FALSE | FALSE | 9 | MultiState |  | EIO Connection Status | 1662 | [5 empty] | EIO Connection Status | 1662 | [5 empty] | 0 = Not Present 1 = Offline 2 = Online | 29
View | FALSE |  | Views.Summary | Summary | 1712 | 1 |  | Views.Summary | Summary | 1708 | 27
Group |  | FALSE | Views.Summary.Sensors | Sensors | 1714 | 26 |  | Views.Summary.Sensors | Sensors | 1709 | 405
Group |  | TRUE | Views.Summary.Sensors.Operational Mode | Operational Mode | 1675 | 855 |  | Views.Summary.Sensors.OprMode | OprMode | 1709 | 539
Value |  |  | Views.Summary.Sensors.Operational Mode | Operational Outdoor Air Temperature | 1675 | 36 |  | Views.Summary.Sensors.OprMode | OprOAT | 1709 | 52 |  |  | Operational Outdoor Air Temperature | 1675 | 36 | 7000 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 26
Value |  |  | Views.Summary.Sensors.Operational Mode | Operational Space Temperature | 1675 | 15 |  | Views.Summary.Sensors.OprMode | OprST | 1709 | 28 |  |  | Operational Space Temperature | 1675 | 15 | 7006 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 25
Value |  |  | Views.Summary.Sensors.Operational Mode | Operational Space Temperature Setpoint Offset | 1675 | 30 |  | Views.Summary.Sensors.OprMode | OprSSO | 1709 | 46 |  |  | Operational Space Temperature Setpoint Offset | 1675 | 30 | 7024 | TRUE | FALSE | FALSE | 4 | Float | 10ths | delta deg F | 507:120 |  |  |  |  | 10ths | delta deg C | 507:359 | [6 empty] | 25
Value |  |  | Views.Summary.Sensors.Operational Mode | Operational Space Humidity | 1675 | 23 |  | Views.Summary.Sensors.OprMode | OprSH | 1709 | 39 |  |  | Operational Space Humidity | 1675 | 23 | 7017 | TRUE | FALSE | FALSE | 4 | Float | 10ths | %RH | 507:29 |  |  |  |  | 10ths | %RH | 507:29 | [6 empty] | 25
Value |  |  | Views.Summary.Sensors.Operational Mode | Operational Outdoor Air Humidity | 1675 | 40 |  | Views.Summary.Sensors.OprMode | OprOAH | 1709 | 56 |  |  | Operational Outdoor Air Humidity | 1675 | 40 | 7004 | TRUE | FALSE | FALSE | 4 | Float | 1s | %RH | 507:29 |  |  |  |  | 1s | %RH | 507:29 | [6 empty] | 26
Value |  |  | Views.Summary.Sensors.Operational Mode | Operational Indoor Air Quality | 1675 | 165 |  | Views.Summary.Sensors.OprMode | OprIAQ | 1709 | 34 |  |  | Operational Indoor Air Quality | 1675 | 165 | 7012 | TRUE | FALSE | FALSE | 4 | Float | 10s | ppm | 507:96 |  |  |  |  | 10s | ppm | 507:96 | [6 empty] | 25
Value |  |  | Views.Summary.Sensors.Operational Mode | Operational Outdoor Air Quality | 1675 | 45 |  | Views.Summary.Sensors.OprMode | OprOAQ | 1709 | 61 |  |  | Operational Outdoor Air Quality | 1675 | 45 | 7009 | TRUE | FALSE | FALSE | 4 | Float | 10s | ppm | 507:96 |  |  |  |  | 10s | ppm | 507:96 | [6 empty] | 26
Value |  |  | Views.Summary.Sensors.Operational Mode | Operating Purge Command | 1675 | 258 |  | Views.Summary.Sensors.OprMode | OprPurgeCmd | 1709 | 332 |  |  | Operating Purge Command | 1675 | 258 | 7000 | TRUE | FALSE | FALSE | 9 | MultiState |  | False/True | 1701 | [5 empty] | False/True | 1701 | [5 empty] | 0 = False 1 = True | 27
Group |  | TRUE | Views.Summary.Sensors.Sensors | Sensors | 1714 | 26 |  | Views.Summary.Sensors.Sensors | Sensors | 1709 | 405
Value |  |  | Views.Summary.Sensors.Sensors | Supply Air Temperature | 1675 | 182 |  | Views.Summary.Sensors.Sensors | SAT | 1709 | 80 |  |  | Supply Air Temperature | 1675 | 182 | 7014 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 3
Value |  |  | Views.Summary.Sensors.Sensors | Return Air Temperature | 1675 | 65 |  | Views.Summary.Sensors.Sensors | RAT | 1709 | 297 |  |  | Return Air Temperature | 1675 | 65 | 7038 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 25
Value |  |  | Views.Summary.Sensors.Sensors | Outdoor Air Temperature Input | 1675 | 38 |  | Views.Summary.Sensors.Sensors | OAT | 1709 | 54 |  |  | Outdoor Air Temperature Input | 1675 | 38 | 7002 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 26
Value |  |  | Views.Summary.Sensors.Sensors | Outdoor Air Temperature Source | 1675 | 37 |  | Views.Summary.Sensors.Sensors | OATSrc | 1709 | 53 |  |  | Outdoor Air Temperature Source | 1675 | 37 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  | Effective Input Source 2 | 1732 | [5 empty] | Effective Input Source 2 | 1732 | [5 empty] | 0 = Unreliable 1 = Local Input 2 = Network Sensor 3 = High Priority ... | 26
Value |  |  | Views.Summary.Sensors.Sensors | Space Temperature Input | 1675 | 164 |  | Views.Summary.Sensors.Sensors | ST | 1709 | 32 |  |  | Space Temperature Input | 1675 | 164 | 7010 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 25
Value |  |  | Views.Summary.Sensors.Sensors | Space Temperature Source | 1675 | 16 |  | Views.Summary.Sensors.Sensors | STSrc | 1709 | 29 |  |  | Space Temperature Source | 1675 | 16 | 7007 | TRUE | FALSE | FALSE | 9 | MultiState |  | Effective Input Source | 1715 | [5 empty] | Effective Input Source | 1715 | [5 empty] | 0 = Unreliable 1 = Return Air Temp 2 = Local Input 3 = Network Sensor ... | 25
Value |  |  | Views.Summary.Sensors.Sensors | Space Temperature Alarm Setpoint Offset | 1675 | 162 |  | Views.Summary.Sensors.Sensors | STAlarmOffset | 1709 | 30 |  |  | Space Temperature Alarm Setpoint Offset | 1675 | 162 | 7008 | TRUE | TRUE | FALSE | 4 | Float | 1s | delta deg F | 507:120 | 0 | 25 |  |  | 1s | delta deg C | 507:359 | 0 | 14 |  |  |  |  | 25
Value |  |  | Views.Summary.Sensors.Sensors | Space Temperature Alarm Time Delay | 1675 | 163 |  | Views.Summary.Sensors.Sensors | STAlarmDelay | 1709 | 31 |  |  | Space Temperature Alarm Time Delay | 1675 | 163 | 7009 | TRUE | TRUE | FALSE | 17 | SignedInteger | 1s | minutes | 507:72 | 0 | 120 |  |  | 1s | minutes | 507:72 | 0 | 120 |  |  |  |  | 25
Value |  |  | Views.Summary.Sensors.Sensors | Space Temp Setpoint Offset Input | 1675 | 32 |  | Views.Summary.Sensors.Sensors | SSO | 1709 | 48 |  |  | Space Temp Setpoint Offset Input | 1675 | 32 | 7026 | TRUE | FALSE | FALSE | 4 | Float | 10ths | delta deg F | 507:120 |  |  |  |  | 10ths | delta deg C | 507:359 | [6 empty] | 25
Value |  |  | Views.Summary.Sensors.Sensors | Space Temperature Setpoint Offset Source | 1675 | 31 |  | Views.Summary.Sensors.Sensors | SSOSrc | 1709 | 47 |  |  | Space Temperature Setpoint Offset Source | 1675 | 31 | 7025 | TRUE | FALSE | FALSE | 9 | MultiState |  | Effective Input Source 2 | 1732 | [5 empty] | Effective Input Source 2 | 1732 | [5 empty] | 0 = Unreliable 1 = Local Input 2 = Network Sensor 3 = High Priority ... | 25
Value |  |  | Views.Summary.Sensors.Sensors | Space Temperature Setpoint Offset Range | 1675 | 34 |  | Views.Summary.Sensors.Sensors | SSORange | 1709 | 50 |  |  | Space Temperature Setpoint Offset Range | 1675 | 34 | 7028 | TRUE | TRUE | FALSE | 4 | Float | 10ths | delta deg F | 507:120 | 0 | 5 |  |  | 10ths | delta deg C | 507:359 | 0 | 3 |  |  |  |  | 25
Value |  |  | Views.Summary.Sensors.Sensors | Space Humidity RAH Input | 1675 | 25 |  | Views.Summary.Sensors.Sensors | RAH | 1709 | 41 |  |  | Space Humidity RAH Input | 1675 | 25 | 7019 | TRUE | FALSE | FALSE | 4 | Float | 10ths | %RH | 507:29 |  |  |  |  | 10ths | %RH | 507:29 | [6 empty] | 25
Value |  |  | Views.Summary.Sensors.Sensors | Space Humidity Source | 1675 | 24 |  | Views.Summary.Sensors.Sensors | SHSrc | 1709 | 40 |  |  | Space Humidity Source | 1675 | 24 | 7018 | TRUE | FALSE | FALSE | 9 | MultiState |  | Effective Input Source 2 | 1732 | [5 empty] | Effective Input Source 2 | 1732 | [5 empty] | 0 = Unreliable 1 = Local Input 2 = Network Sensor 3 = High Priority ... | 25
Value |  |  | Views.Summary.Sensors.Sensors | Outdoor Air Humidity Input | 1675 | 43 |  | Views.Summary.Sensors.Sensors | OAH | 1709 | 59 |  |  | Outdoor Air Humidity Input | 1675 | 43 | 7007 | TRUE | FALSE | FALSE | 4 | Float | 10ths | %RH | 507:29 |  |  |  |  | 10ths | %RH | 507:29 | [6 empty] | 26
Value |  |  | Views.Summary.Sensors.Sensors | Outdoor Air Humidity Source | 1675 | 42 |  | Views.Summary.Sensors.Sensors | OAHSrc | 1709 | 58 |  |  | Outdoor Air Humidity Source | 1675 | 42 | 7006 | TRUE | FALSE | FALSE | 9 | MultiState |  | Effective Input Source 2 | 1732 | [5 empty] | Effective Input Source 2 | 1732 | [5 empty] | 0 = Unreliable 1 = Local Input 2 = Network Sensor 3 = High Priority ... | 26
Value |  |  | Views.Summary.Sensors.Sensors | Indoor Air Quality | 1675 | 19 |  | Views.Summary.Sensors.Sensors | IAQ | 1709 | 36 |  |  | Indoor Air Quality | 1675 | 19 | 7014 | TRUE | FALSE | FALSE | 4 | Float | 10s | ppm | 507:96 |  |  |  |  | 10s | ppm | 507:96 | [6 empty] | 25
Value |  |  | Views.Summary.Sensors.Sensors | Indoor Air Quality Source | 1675 | 20 |  | Views.Summary.Sensors.Sensors | IAQSrc | 1709 | 35 |  |  | Indoor Air Quality Source | 1675 | 20 | 7013 | TRUE | FALSE | FALSE | 9 | MultiState |  | Effective Input Source 2 | 1732 | [5 empty] | Effective Input Source 2 | 1732 | [5 empty] | 0 = Unreliable 1 = Local Input 2 = Network Sensor 3 = High Priority ... | 25
Value |  |  | Views.Summary.Sensors.Sensors | Outdoor Air Quality Input | 1675 | 47 |  | Views.Summary.Sensors.Sensors | OAQ | 1709 | 63 |  |  | Outdoor Air Quality Input | 1675 | 47 | 7011 | TRUE | FALSE | FALSE | 4 | Float | 10s | ppm | 507:96 |  |  |  |  | 10s | ppm | 507:96 | [6 empty] | 26
Value |  |  | Views.Summary.Sensors.Sensors | Outdoor Air Quality Source | 1675 | 46 |  | Views.Summary.Sensors.Sensors | OAQSrc | 1709 | 62 |  |  | Outdoor Air Quality Source | 1675 | 46 | 7010 | TRUE | FALSE | FALSE | 9 | MultiState |  | Effective Input Source 2 | 1732 | [5 empty] | Effective Input Source 2 | 1732 | [5 empty] | 0 = Unreliable 1 = Local Input 2 = Network Sensor 3 = High Priority ... | 26
Value |  |  | Views.Summary.Sensors.Sensors | Purge Command Source | 1675 | 259 |  | Views.Summary.Sensors.Sensors | PurgeCmdSrc | 1709 | 333 |  |  | Purge Command Source | 1675 | 259 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  | Effective Input Source 2 | 1732 | [5 empty] | Effective Input Source 2 | 1732 | [5 empty] | 0 = Unreliable 1 = Local Input 2 = Network Sensor 3 = High Priority ... | 27
Value |  |  | Views.Summary.Sensors.Sensors | Supply Air Humidity | 1675 | 224 |  | Views.Summary.Sensors.Sensors | SAH | 1709 | 295 |  |  | Supply Air Humidity | 1675 | 224 | 7014 | TRUE | FALSE | FALSE | 4 | Float | 1s | %RH | 507:29 |  |  |  |  | 1s | %RH | 507:29 | [6 empty] | 19
Value |  |  | Views.Summary.Sensors.Sensors | Mixed Air Temperature | 1675 | 62 |  | Views.Summary.Sensors.Sensors | MAT | 1709 | 293 |  |  | Mixed Air Temperature | 1675 | 62 | 7012 | TRUE | FALSE | FALSE | 4 | Float | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 | [6 empty] | 19
Value |  |  | Views.Summary.Sensors.Sensors | Building Static Pressure | 1675 | 241 |  | Views.Summary.Sensors.Sensors | BldgPres | 1709 | 315 |  |  | Building Static Pressure | 1675 | 241 | 7007 | TRUE | FALSE | FALSE | 4 | Float | 1000ths | in wc | 507:58 |  |  |  |  | 1000ths | kPa | 507:54 | [6 empty] | 21
Value |  |  | Views.Summary.Sensors.Sensors | Duct Static Pressure | 1675 | 183 |  | Views.Summary.Sensors.Sensors | DctPrs | 1709 | 81 |  |  | Duct Static Pressure | 1675 | 183 | 7015 | TRUE | FALSE | FALSE | 4 | Float | 100ths | in wc | 507:58 |  |  |  |  | 100ths | kPa | 507:54 | [6 empty] | 3
Value |  |  | Views.Summary.Sensors.Sensors | Netsensor Calibration | 1714 | 266 |  | Views.Summary.Sensors.Sensors | NS-Calibration | 1709 | 766 |  |  | Netsensor Calibration | 1714 | 266 | 7077 | TRUE | TRUE | FALSE | 4 | Float | 10ths | delta deg F | 507:120 | -5 | 5 |  |  | 10ths | delta deg C | 507:359 | -3 | 3 |  |  |  |  | 25
Group |  | FALSE | Views.Summary.Unit | Unit | 1714 | 153 |  | Views.Summary.Unit | Unit | 1709 | 472
Value |  |  | Views.Summary.Unit | Unit Name | 1675 | 1 |  | Views.Summary.Unit | Name | 1709 | 1 |  |  | Unit Name | 1675 | 1 | 7001 | TRUE | TRUE | FALSE | 7 | String | [14 empty] | 30 |  | 1
Value |  |  | Views.Summary.Unit | Unit Model Number | 1675 | 3 |  | Views.Summary.Unit | Model# | 1709 | 2 |  |  | Unit Model Number | 1675 | 3 | 7002 | TRUE | TRUE | FALSE | 7 | String | [14 empty] | 40 |  | 1
Value |  |  | Views.Summary.Unit | Unit Serial Number | 1675 | 4 |  | Views.Summary.Unit | Serial# | 1709 | 3 |  |  | Unit Serial Number | 1675 | 4 | 7003 | TRUE | TRUE | FALSE | 7 | String | [14 empty] | 40 |  | 1
Value |  |  | Views.Summary.Unit | Model Name | 1675 | 448 |  | Views.Summary.Unit | ModelName | 1709 | 583 |  |  | Model Name | 1675 | 448 | 7014 | TRUE | FALSE | FALSE | 7 | String | [14 empty] | 30 |  | 1
Value |  |  | Views.Summary.Unit | Unit Status | 1675 | 0 |  | Views.Summary.Unit | Unit-S | 1709 | 0 |  |  | Unit Status | 1675 | 0 | 7000 | TRUE | FALSE | FALSE | 9 | MultiState |  | SE RTU Unit Status | 1737 | [5 empty] | SE RTU Unit Status | 1737 | [5 empty] | 0 = Idle 1 = SD Alarm 2 = Purge Command 3 = Self Test ... | 1
Value |  |  | Views.Summary.Unit | Unit Enable | 1675 | 462 |  | Views.Summary.Unit | UnitEn | 1709 | 641 |  |  | Unit Enable | 1675 | 462 | 7019 | TRUE | TRUE | FALSE | 9 | MultiState |  | Shutdown/Enable | 349 | [5 empty] | Shutdown/Enable | 349 | [5 empty] | 0 = Shutdown 1 = Enable | 1
Value |  |  | Views.Summary.Unit | Hardware Reset | 1675 | 499 |  | Views.Summary.Unit | HdwrReset | 1709 | 631 |  |  | Hardware Reset | 1675 | 499 | 7021 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 1
Value |  |  | Views.Summary.Unit | Reset Lockouts | 1675 | 337 |  | Views.Summary.Unit | ResetLO | 1709 | 464 |  |  | Reset Lockouts | 1675 | 337 | 7011 | TRUE | TRUE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 1
View | FALSE |  | Views.Commissioning | Commissioning | 1712 | 2 |  | Views.Commission | Commission | 1708 | 28
Group |  | FALSE | Views.Commissioning.Quick Start | Quick Start | 1714 | 223 |  | Views.Commission.Quick Start | Quick Start | 1709 | 720
Value |  |  | Views.Commissioning.Quick Start | Number of Cooling Stages Installed | 1675 | 67 |  | Views.Commission.Quick Start | #ClgStgs | 1709 | 92 |  |  | Number of Cooling Stages Installed | 1675 | 67 | 7001 | TRUE | TRUE | FALSE | 16 | Byte | 1s |  | 507:95 | 1 | 4 |  |  | 1s |  | 507:95 | 1 | 4 |  |  |  |  | 4
Value |  |  | Views.Commissioning.Quick Start | Number of Heating Stages Installed | 1675 | 215 |  | Views.Commission.Quick Start | #HtgStgs | 1709 | 250 |  |  | Number of Heating Stages Installed | 1675 | 215 | 7000 | TRUE | TRUE | FALSE | 16 | Byte | 1s |  | 507:95 | 0 | 3 |  |  | 1s |  | 507:95 | 0 | 3 |  |  |  |  | 14
Value |  |  | Views.Commissioning.Quick Start | Number of Heat Pump Stages Installed | 1675 | 380 |  | Views.Commission.Quick Start | #HtPumpStgs | 1709 | 491 |  |  | Number of Heat Pump Stages Installed | 1675 | 380 | 7000 | TRUE | TRUE | FALSE | 4 | Float | 1s |  | 507:95 | 0 | 2 |  |  | 1s |  | 507:95 | 0 | 2 |  |  |  |  | 38
Value |  |  | Views.Commissioning.Quick Start | Number of Refrig Systems Installed | 1675 | 495 |  | Views.Commission.Quick Start | #RefrigSys | 1709 | 627 |  |  | Number of Refrig Systems Installed | 1675 | 495 | 7044 | TRUE | TRUE | FALSE | 4 | Float | 1s |  | 507:95 | 0 | 4 |  |  | 1s |  | 507:95 | 0 | 4 |  |  |  |  | 4
Value |  |  | Views.Commissioning.Quick Start | Fan Control Type | 1675 | 173 |  | Views.Commission.Quick Start | FanCtl-Type | 1709 | 71 |  |  | Fan Control Type | 1675 | 173 | 7005 | TRUE | TRUE | FALSE | 9 | MultiState |  | SE RTU Fan Control Type | 1619 | [5 empty] | SE RTU Fan Control Type | 1619 | [5 empty] | 0 = Single Speed 1 = Not Used 2 = Fixed Variable 3 = Variable Speed | 3
Value |  |  | Views.Commissioning.Quick Start | Thermostat Only Control Enabled | 1675 | 160 |  | Views.Commission.Quick Start | Tstat-Only | 1709 | 21 |  |  | Thermostat Only Control Enabled | 1675 | 160 | 7010 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 2
Value |  |  | Views.Commissioning.Quick Start | Continuous Fan Operation in Occupied Mode | 1675 | 186 |  | Views.Commission.Quick Start | FanOnOcc | 1709 | 84 |  |  | Continuous Fan Operation in Occupied Mode | 1675 | 186 | 7018 | TRUE | TRUE | FALSE | 9 | MultiState |  | Yes/No | 1698 | [5 empty] | Yes/No | 1698 | [5 empty] | 0 = Yes 1 = No | 3
Value |  |  | Views.Commissioning.Quick Start | Economizer Minimum Position Setpoint | 1675 | 292 |  | Views.Commission.Quick Start | Econ-MinPos | 1709 | 381 |  |  | Economizer Minimum Position Setpoint | 1675 | 292 | 7017 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 19
Value |  |  | Views.Commissioning.Quick Start | Supply Air Temperature | 1675 | 182 |  | Views.Commission.Quick Start | SAT | 1709 | 80 |  |  | Supply Air Temperature | 1675 | 182 | 7014 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 3
Value |  |  | Views.Commissioning.Quick Start | Return Air Temperature | 1675 | 65 |  | Views.Commission.Quick Start | RAT | 1709 | 297 |  |  | Return Air Temperature | 1675 | 65 | 7038 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 25
Value |  |  | Views.Commissioning.Quick Start | Outdoor Air Temperature Input | 1675 | 38 |  | Views.Commission.Quick Start | OAT | 1709 | 54 |  |  | Outdoor Air Temperature Input | 1675 | 38 | 7002 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 26
Value |  |  | Views.Commissioning.Quick Start | Cooling Status | 1675 | 69 |  | Views.Commission.Quick Start | Clg-S | 1709 | 93 |  |  | Cooling Status | 1675 | 69 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  | SE RTU Cooling Control Status | 1740 | [5 empty] | SE RTU Cooling Control Status | 1740 | [5 empty] | 0 = Off-Idle 1 = Thermostat Cooling 2 = Unoccupied Cooling 3 = Occupied Cooling ... | 4
Value |  |  | Views.Commissioning.Quick Start | Heating Status | 1675 | 106 |  | Views.Commission.Quick Start | Htg-S | 1709 | 225 |  |  | Heating Status | 1675 | 106 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  | SE RTU Heating Control Status | 1742 | [5 empty] | SE RTU Heating Control Status | 1742 | [5 empty] | 0 = Off-Idle 1 = On-Defrost 2 = SAT Tempering 3 = Morning Warmup ... | 13
Value |  |  | Views.Commissioning.Quick Start | Cooling Mode Enabled For Operation | 1675 | 66 |  | Views.Commission.Quick Start | Clg-En | 1709 | 91 |  |  | Cooling Mode Enabled For Operation | 1675 | 66 | 7000 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 4
Value |  |  | Views.Commissioning.Quick Start | Heating Mode Enabled For Operation | 1675 | 105 |  | Views.Commission.Quick Start | Htg-En | 1709 | 224 |  |  | Heating Mode Enabled For Operation | 1675 | 105 | 7000 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 13
Value |  |  | Views.Commissioning.Quick Start | Unique Equipment Identifier | 1675 | 1567 |  | Views.Commission.Quick Start | Unique Equipment Identifier | 1675 | 1567 |  |  | Unique Equipment Identifier | 1675 | 1567 | 7043 | TRUE | TRUE | FALSE | 9 | MultiState |  | SE RTU Equipment Configuration | 3356 | [5 empty] | SE RTU Equipment Configuration | 3356 | [5 empty] | 0 = Standard 1 = Tandem Cir1 With 2 Stage Cir2 2 = 2 Stage Cir1 With 2 Stage Cir2 3 = 2 Stage Cir1 With Single Cir2 ... | 1
Group |  | FALSE | Views.Commissioning.Standard | Standard | 1709 | 610 |  | Views.Commission.Standard | Standard | 1709 | 610
Value |  |  | Views.Commissioning.Standard | Occupancy Mode | 1675 | 161 |  | Views.Commission.Standard | OccMode | 1709 | 24 |  |  | Occupancy Mode | 1675 | 161 | 7002 | TRUE | TRUE | FALSE | 9 | MultiState |  | SE Occupancy Mode | 1728 | [5 empty] | SE Occupancy Mode | 1728 | [5 empty] | 0 = Schedule 1 = External | 25
Value |  |  | Views.Commissioning.Standard | Thermostat Only Control Enabled | 1675 | 160 |  | Views.Commission.Standard | Tstat-Only | 1709 | 21 |  |  | Thermostat Only Control Enabled | 1675 | 160 | 7010 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 2
Value |  |  | Views.Commissioning.Standard | Cooling Mode Enabled For Operation | 1675 | 66 |  | Views.Commission.Standard | Clg-En | 1709 | 91 |  |  | Cooling Mode Enabled For Operation | 1675 | 66 | 7000 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 4
Value |  |  | Views.Commissioning.Standard | Number of Cooling Stages Installed | 1675 | 67 |  | Views.Commission.Standard | #ClgStgs | 1709 | 92 |  |  | Number of Cooling Stages Installed | 1675 | 67 | 7001 | TRUE | TRUE | FALSE | 16 | Byte | 1s |  | 507:95 | 1 | 4 |  |  | 1s |  | 507:95 | 1 | 4 |  |  |  |  | 4
Value |  |  | Views.Commissioning.Standard | Heating Mode Enabled For Operation | 1675 | 105 |  | Views.Commission.Standard | Htg-En | 1709 | 224 |  |  | Heating Mode Enabled For Operation | 1675 | 105 | 7000 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 13
Value |  |  | Views.Commissioning.Standard | Number of Heating Stages Installed | 1675 | 215 |  | Views.Commission.Standard | #HtgStgs | 1709 | 250 |  |  | Number of Heating Stages Installed | 1675 | 215 | 7000 | TRUE | TRUE | FALSE | 16 | Byte | 1s |  | 507:95 | 0 | 3 |  |  | 1s |  | 507:95 | 0 | 3 |  |  |  |  | 14
Value |  |  | Views.Commissioning.Standard | Economizer Enabled For Operation | 1675 | 50 |  | Views.Commission.Standard | Econ-En | 1709 | 281 |  |  | Economizer Enabled For Operation | 1675 | 50 | 7000 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 19
Value |  |  | Views.Commissioning.Standard | Economizer Minimum Position Setpoint | 1675 | 292 |  | Views.Commission.Standard | Econ-MinPos | 1709 | 381 |  |  | Economizer Minimum Position Setpoint | 1675 | 292 | 7017 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 19
Value |  |  | Views.Commissioning.Standard | Economizer Damper Minimum Position Low Speed Fan | 1675 | 327 |  | Views.Commission.Standard | LowSpeedFan-MinPos | 1709 | 447 |  |  | Economizer Damper Minimum Position Low Speed Fan | 1675 | 327 | 7025 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 19
Value |  |  | Views.Commissioning.Standard | Continuous Fan Operation in Occupied Mode | 1675 | 186 |  | Views.Commission.Standard | FanOnOcc | 1709 | 84 |  |  | Continuous Fan Operation in Occupied Mode | 1675 | 186 | 7018 | TRUE | TRUE | FALSE | 9 | MultiState |  | Yes/No | 1698 | [5 empty] | Yes/No | 1698 | [5 empty] | 0 = Yes 1 = No | 3
Value |  |  | Views.Commissioning.Standard | SAT Limit for Cooling Enable | 1675 | 143 |  | Views.Commission.Standard | SATCoolLimit-En | 1709 | 106 |  |  | SAT Limit for Cooling Enable | 1675 | 143 | 7015 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 4
Value |  |  | Views.Commissioning.Standard | SAT Limit for Cooling Setpoint | 1675 | 75 |  | Views.Commission.Standard | SATCoolLimit-Sp | 1709 | 107 |  |  | SAT Limit for Cooling Setpoint | 1675 | 75 | 7016 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 40 | 65 |  |  | 1s | deg C | 507:62 | 4 | 18 |  |  |  |  | 4
Value |  |  | Views.Commissioning.Standard | OAT Cooling Cutout Enabled | 1675 | 127 |  | Views.Commission.Standard | ClgOATCutout-En | 1709 | 97 |  |  | OAT Cooling Cutout Enabled | 1675 | 127 | 7006 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 4
Value |  |  | Views.Commissioning.Standard | OAT Cooling Cutout | 1675 | 74 |  | Views.Commission.Standard | ClgOATCutout | 1709 | 98 |  |  | OAT Cooling Cutout | 1675 | 74 | 7007 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 0 | 100 |  |  | 1s | deg C | 507:62 | -18 | 38 |  |  |  |  | 4
Value |  |  | Views.Commissioning.Standard | Circuit 1 OAT Cooling Cutout | 2644 | 442 |  | Views.Commission.Standard | Circ1ClgOATCutout | 2645 | 425 |  |  | Circuit 1 OAT Cooling Cutout | 2644 | 442 | 7068 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 |  | 100 | 7070 |  | 1s | deg C | 507:62 |  | 38 | 7070 |  |  |  | 4
Value |  |  | Views.Commissioning.Standard | Circuit 2 OAT Cooling Cutout | 2644 | 443 |  | Views.Commission.Standard | Circ2ClgOATCutout | 2645 | 426 |  |  | Circuit 2 OAT Cooling Cutout | 2644 | 443 | 7069 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 |  | 100 | 7071 |  | 1s | deg C | 507:62 |  | 38 | 7071 |  |  |  | 4
Value |  |  | Views.Commissioning.Standard | Unique Equipment Identifier | 1675 | 1567 |  | Views.Commission.Standard | Unique Equipment Identifier | 1675 | 1567 |  |  | Unique Equipment Identifier | 1675 | 1567 | 7043 | TRUE | TRUE | FALSE | 9 | MultiState |  | SE RTU Equipment Configuration | 3356 | [5 empty] | SE RTU Equipment Configuration | 3356 | [5 empty] | 0 = Standard 1 = Tandem Cir1 With 2 Stage Cir2 2 = 2 Stage Cir1 With 2 Stage Cir2 3 = 2 Stage Cir1 With Single Cir2 ... | 1
Group |  | FALSE | Views.Commissioning.Options | Options | 1712 | 44 |  | Views.Commission.Options | Options | 1712 | 44
Value |  |  | Views.Commissioning.Options | Fan Control Type | 1675 | 173 |  | Views.Commission.Options | FanCtl-Type | 1709 | 71 |  |  | Fan Control Type | 1675 | 173 | 7005 | TRUE | TRUE | FALSE | 9 | MultiState |  | SE RTU Fan Control Type | 1619 | [5 empty] | SE RTU Fan Control Type | 1619 | [5 empty] | 0 = Single Speed 1 = Not Used 2 = Fixed Variable 3 = Variable Speed | 3
Value |  |  | Views.Commissioning.Options | Exhaust Type | 1675 | 147 |  | Views.Commission.Options | ExFType | 1709 | 8 |  |  | Exhaust Type | 1675 | 147 | 7008 | TRUE | TRUE | FALSE | 9 | MultiState |  | SE RTU Exhaust Setup | 1639 | [5 empty] | SE RTU Exhaust Setup | 1639 | [5 empty] | 0 = None 1 = Non-Modulating 2 = Modulating Damper 3 = Variable Frequency Fan | 1
Value |  |  | Views.Commissioning.Options | Number of Refrig Systems Installed | 1675 | 495 |  | Views.Commission.Options | #RefrigSys | 1709 | 627 |  |  | Number of Refrig Systems Installed | 1675 | 495 | 7044 | TRUE | TRUE | FALSE | 4 | Float | 1s |  | 507:95 | 0 | 4 |  |  | 1s |  | 507:95 | 0 | 4 |  |  |  |  | 4
Value |  |  | Views.Commissioning.Options | Circuit 1 Modulating Condenser Fan Installed | 2644 | 323 |  | Views.Commission.Options | ModCondFanCir1En | 2645 | 342 |  |  | Circuit 1 Modulating Condenser Fan Installed | 2644 | 323 | 7063 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 4
Value |  |  | Views.Commissioning.Options | Circuit 2 Modulating Condenser Fan Installed | 2644 | 324 |  | Views.Commission.Options | ModCondFanCir2En | 2645 | 343 |  |  | Circuit 2 Modulating Condenser Fan Installed | 2644 | 324 | 7064 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 4
Value |  |  | Views.Commissioning.Options | Low Ambient Enabled | 1675 | 649 |  | Views.Commission.Options | LowAmb-En | 1709 | 662 |  |  | Low Ambient Enabled | 1675 | 649 | 7051 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 4
Value |  |  | Views.Commissioning.Options | Lead/Lag Equalize Cooling Stage Runtime Enabled | 1675 | 72 |  | Views.Commission.Options | LeadLag-En | 1709 | 95 |  |  | Lead/Lag Equalize Cooling Stage Runtime Enabled | 1675 | 72 | 7004 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 4
Value |  |  | Views.Commissioning.Options | Hot Gas Bypass Present | 1675 | 89 |  | Views.Commission.Options | HGP-Inst | 1709 | 139 |  |  | Hot Gas Bypass Present | 1675 | 89 | 7004 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 5
Value |  |  | Views.Commissioning.Options | Heating Mode Enabled For Operation | 1675 | 105 |  | Views.Commission.Options | Htg-En | 1709 | 224 |  |  | Heating Mode Enabled For Operation | 1675 | 105 | 7000 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 13
Value |  |  | Views.Commissioning.Options | Heating Control Type | 1675 | 107 |  | Views.Commission.Options | Htg-Type | 1709 | 6 |  |  | Heating Control Type | 1675 | 107 | 7006 | TRUE | TRUE | FALSE | 9 | MultiState |  | Heat Cool Type | 1608 | [5 empty] | Heat Cool Type | 1608 | [5 empty] | 0 = Staged 1 = Proportional | 1
Value |  |  | Views.Commissioning.Options | SAT Air Temp Limit for Heating Enabled | 1675 | 108 |  | Views.Commission.Options | SATHtgLimit-En | 1709 | 226 |  |  | SAT Air Temp Limit for Heating Enabled | 1675 | 108 | 7002 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 13
Value |  |  | Views.Commissioning.Options | SAT Air Temp Limit For Heating Setpoint | 1675 | 109 |  | Views.Commission.Options | SATHtgLimit-Sp | 1709 | 227 |  |  | SAT Air Temp Limit For Heating Setpoint | 1675 | 109 | 7003 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 100 | 180 |  |  | 1s | deg C | 507:62 | 38 | 82 |  |  |  |  | 13
Value |  |  | Views.Commissioning.Options | Outdoor Air Temp Heating Cutout Setpoint | 1675 | 110 |  | Views.Commission.Options | HtgOATCutout-Sp | 1709 | 228 |  |  | Outdoor Air Temp Heating Cutout Setpoint | 1675 | 110 | 7004 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 0 | 100 |  |  | 1s | deg C | 507:62 | -18 | 38 |  |  |  |  | 13
Value |  |  | Views.Commissioning.Options | Air Proving Switch Setup | 1675 | 174 |  | Views.Commission.Options | APSSetup | 1709 | 72 |  |  | Air Proving Switch Setup | 1675 | 174 | 7006 | TRUE | TRUE | FALSE | 9 | MultiState |  | Fan Setup | 1622 | [5 empty] | Fan Setup | 1622 | [5 empty] | 0 = Constant Volume 1 = Variable Volume 2 = None | 3
Value |  |  | Views.Commissioning.Options | Dirty Filter Switch Installed | 1675 | 364 |  | Views.Commission.Options | DFSInst | 1709 | 475 |  |  | Dirty Filter Switch Installed | 1675 | 364 | 7035 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 3
Value |  |  | Views.Commissioning.Options | Demand Ventilation Mode of Operation | 1675 | 225 |  | Views.Commission.Options | DVent-Mode | 1709 | 298 |  |  | Demand Ventilation Mode of Operation | 1675 | 225 | 7000 | TRUE | TRUE | FALSE | 9 | MultiState |  | SE RTU DCV Mode | 1729 | [5 empty] | SE RTU DCV Mode | 1729 | [5 empty] | 0 = Disabled 1 = Controlled by IAQ 2 = Diff between IAQ and OAQ | 23
Value |  |  | Views.Commissioning.Options | Hot Gas Reheat Enabled For Operation | 1675 | 249 |  | Views.Commission.Options | HGR-En | 1709 | 323 |  |  | Hot Gas Reheat Enabled For Operation | 1675 | 249 | 7000 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 20
Value |  |  | Views.Commissioning.Options | Morning Warmup Enabled | 1675 | 209 |  | Views.Commission.Options | MornW-En | 1709 | 244 |  |  | Morning Warmup Enabled | 1675 | 209 | 7020 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 13
Value |  |  | Views.Commissioning.Options | Number of Heat Pump Stages Installed | 1675 | 380 |  | Views.Commission.Options | #HtPumpStgs | 1709 | 491 |  |  | Number of Heat Pump Stages Installed | 1675 | 380 | 7000 | TRUE | TRUE | FALSE | 4 | Float | 1s |  | 507:95 | 0 | 2 |  |  | 1s |  | 507:95 | 0 | 2 |  |  |  |  | 38
Value |  |  | Views.Commissioning.Options | Low Ambient Fan Pre-run Time For Cooling | 1675 | 73 |  | Views.Commission.Options | LowAmbFanPrerunCool | 1709 | 96 |  |  | Low Ambient Fan Pre-run Time For Cooling | 1675 | 73 | 7005 | TRUE | TRUE | FALSE | 17 | SignedInteger | 1s | seconds | 507:73 | 0 | 255 |  |  | 1s | seconds | 507:73 | 0 | 255 |  |  |  |  | 4
Value |  |  | Views.Commissioning.Options | PID Tuning Reset | 1675 | 631 |  | Views.Commission.Options | PIDTunRst | 1709 | 651 |  |  | PID Tuning Reset | 1675 | 631 | 7063 | TRUE | TRUE | FALSE | 9 | MultiState |  | False/True | 1701 | [5 empty] | False/True | 1701 | [5 empty] | 0 = False 1 = True | 25
Value |  |  | Views.Commissioning.Options | Low Ambient Start | 1675 | 1457 |  | Views.Commission.Options | LowAmbStart | 1709 | 697 |  |  | Low Ambient Start | 1675 | 1457 | 7056 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 4
Value |  |  | Views.Commissioning.Options | SZ VAV Enabled | 1675 | 491 |  | Views.Commission.Options | SZVAVEn | 1709 | 623 |  |  | SZ VAV Enabled | 1675 | 491 | 7020 | TRUE | TRUE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 1
Value |  |  | Views.Commissioning.Options | Pressurize Instead Of Purge | 1714 | 222 |  | Views.Commission.Options | PressurizeNotPurge | 1709 | 709 |  |  | Pressurize Instead Of Purge | 1714 | 222 | 7005 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 27
Value |  |  | Views.Commissioning.Options | Cooling Allowed During Heat Limit | 1714 | 230 |  | Views.Commission.Options | CoolDuringHeatLimit | 1709 | 727 |  |  | Cooling Allowed During Heat Limit | 1714 | 230 | 7060 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 4
Value |  |  | Views.Commissioning.Options | FDD Alarm Enable | 1714 | 236 |  | Views.Commission.Options | FDDAlarmEn | 1709 | 733 |  |  | FDD Alarm Enable | 1714 | 236 | 7062 | TRUE | TRUE | FALSE | 9 | MultiState |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 | [5 empty] | 0 = Disable 1 = Enable | 4
Value |  |  | Views.Commissioning.Options | Econ Sensor Fault Indications | 1675 | 1605 |  | Views.Commission.Options | EconSensorFaults | 1709 | 736 |  |  | Econ Sensor Fault Indications | 1675 | 1605 | 7033 | TRUE | TRUE | FALSE | 9 | MultiState |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 | [5 empty] | 0 = Disable 1 = Enable | 19
Value |  |  | Views.Commissioning.Options | Oil Switch Installed | 2644 | 418 |  | Views.Commission.Options | Oil Switch Installed | 2644 | 418 |  |  | Oil Switch Installed | 2644 | 418 | 7077 | TRUE | TRUE | FALSE | 1 | Boolean | [16 empty] | 4
Group |  | FALSE | Views.Commissioning.Network Setup | Network Setup | 1712 | 15 |  | Views.Commission.Network Setup | Network Setup | 1712 | 15
Value |  |  | Views.Commissioning.Network Setup | FC Comm Mode | 1675 | 496 |  | Views.Commission.Network Setup | FcBusMode | 1709 | 628 |  |  | FC Comm Mode | 1675 | 496 | 7007 | TRUE | FALSE | FALSE | 9 | MultiState |  | FC Bus Mode | 1222 | [5 empty] | FC Bus Mode | 1222 | [5 empty] | 0 = Wired Field Bus 1 = Wireless Field Bus 2 = N2 Subordinate Field Bus 3 = Modbus Field Bus ... | 31
Value |  |  | Views.Commissioning.Network Setup | Address | 1675 | 282 |  | Views.Commission.Network Setup | Address | 1709 | 352 |  |  | Address | 1675 | 282 | 7001 | TRUE | TRUE | FALSE | 17 | SignedInteger | 1s |  | 507:95 | 4 | 127 |  |  | 1s |  | 507:95 | 4 | 127 |  |  |  |  | 31
Value |  |  | Views.Commissioning.Network Setup | Device OID | 1675 | 283 |  | Views.Commission.Network Setup | DeviceId | 1709 | 353 |  |  | Device OID | 1675 | 283 | 7002 | TRUE | TRUE | FALSE | 2 | UnsignedLong | 1s |  | 507:95 | 0 | 4194302 |  |  | 1s |  | 507:95 | 0 | 4194302 |  |  |  |  | 31
Value |  |  | Views.Commissioning.Network Setup | Baud Rate | 1675 | 285 |  | Views.Commission.Network Setup | BaudRate | 1709 | 355 |  |  | Baud Rate | 1675 | 285 | 7004 | TRUE | TRUE | FALSE | 9 | MultiState |  | MSTPDL Baud Rate | 300 | [5 empty] | MSTPDL Baud Rate | 300 | [5 empty] | 0 = Auto 1 = 1200 2 = 9600 3 = 19200 ... | 31
Value |  |  | Views.Commissioning.Network Setup | Device Name | 1675 | 326 |  | Views.Commission.Network Setup | DevName | 1709 | 446 |  |  | Device Name | 1675 | 326 | 7009 | TRUE | TRUE | FALSE | 7 | String | [14 empty] | 30 |  | 29
Value |  |  | Views.Commissioning.Network Setup | BACnet Encoding Type | 1675 | 847 |  | Views.Commission.Network Setup | EncodeType | 1709 | 668 |  |  | BACnet Encoding Type | 1675 | 847 | 7008 | TRUE | TRUE | FALSE | 9 | MultiState |  | BACnet Encoding | 575 | [5 empty] | BACnet Encoding | 575 | [5 empty] | 0 = ISO 10646 (UCS-2) 1 = ANSI X3.4 (US-ASCII) 2 = Microsoft DBCS code page 932 (Japanese Shift JIS) 3 = ISO 10646 (UTF-8) | 31
Group |  | FALSE | Views.Commissioning.Commissioning Mode | Commissioning Mode | 1675 | 1244 |  | Views.Commission.Commissioning Mode | Commissioning Mode | 1675 | 1244
Value |  |  | Views.Commissioning.Commissioning Mode | Commissioning Mode | 1675 | 1244 |  | Views.Commission.Commissioning Mode | Commissioning Mode | 1675 | 1244 |  |  | Commissioning Mode | 1675 | 1244 | 7000 | TRUE | TRUE | FALSE | 9 | MultiState |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 | [5 empty] | 0 = Disable 1 = Enable | 41
Value |  |  | Views.Commissioning.Commissioning Mode | Commissioning Time Remaining | 2644 | 447 |  | Views.Commission.Commissioning Mode | CommishTimeRemaining | 2645 | 428 |  |  | Commissioning Time Remaining | 2644 | 447 | 7001 | TRUE | FALSE | FALSE | 4 | Float | 10ths | minutes | 507:72 | 0 | 100 |  |  | 10ths | minutes | 507:72 | 0 | 100 |  |  |  |  | 41
Value |  |  | Views.Commissioning.Commissioning Mode | Extend Commissioning Time | 2644 | 448 |  | Views.Commission.Commissioning Mode | ExtendCommishTime | 2645 | 429 |  |  | Extend Commissioning Time | 2644 | 448 | 7002 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 41
Value |  |  | Views.Commissioning.Commissioning Mode | Unit Enable | 1675 | 462 |  | Views.Commission.Commissioning Mode | UnitEn | 1709 | 641 |  |  | Unit Enable | 1675 | 462 | 7003 | TRUE | TRUE | FALSE | 9 | MultiState |  | Shutdown/Enable | 349 | [5 empty] | Shutdown/Enable | 349 | [5 empty] | 0 = Shutdown 1 = Enable | 41
Value |  |  | Views.Commissioning.Commissioning Mode | Supply Fan Command | 2644 | 208 |  | Views.Commission.Commissioning Mode | Fan | 1709 | 79 |  |  | Supply Fan Command | 2644 | 208 | 7004 | TRUE | TRUE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 41
Value |  |  | Views.Commissioning.Commissioning Mode | Fan % Command | 1675 | 169 |  | Views.Commission.Commissioning Mode | FanVFD | 1709 | 67 |  |  | Fan % Command | 1675 | 169 | 7005 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 41
Value |  |  | Views.Commissioning.Commissioning Mode | Compressor Stage Command 1 | 1714 | 145 |  | Views.Commission.Commissioning Mode | C1 | 1709 | 127 |  |  | Compressor Stage Command 1 | 1714 | 145 | 7006 | TRUE | TRUE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 41
Value |  |  | Views.Commissioning.Commissioning Mode | Modulating Compressor Output | 2644 | 292 |  | Views.Commission.Commissioning Mode | ModCompOut | 2645 | 311 |  |  | Modulating Compressor Output | 2644 | 292 | 7023 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 41
Value |  |  | Views.Commissioning.Commissioning Mode | Compressor Stage Command 2 | 1714 | 146 |  | Views.Commission.Commissioning Mode | C2 | 1709 | 128 |  |  | Compressor Stage Command 2 | 1714 | 146 | 7007 | TRUE | TRUE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 41
Value |  |  | Views.Commissioning.Commissioning Mode | Compressor Stage Command 3 | 1714 | 147 |  | Views.Commission.Commissioning Mode | C3 | 1709 | 129 |  |  | Compressor Stage Command 3 | 1714 | 147 | 7008 | TRUE | TRUE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 41
Value |  |  | Views.Commissioning.Commissioning Mode | Compressor Stage Command 4 | 1714 | 148 |  | Views.Commission.Commissioning Mode | C4 | 1709 | 130 |  |  | Compressor Stage Command 4 | 1714 | 148 | 7009 | TRUE | TRUE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 41
Value |  |  | Views.Commissioning.Commissioning Mode | Condenser Fan 1 | 1675 | 128 |  | Views.Commission.Commissioning Mode | CN-Fan | 1709 | 109 |  |  | Condenser Fan 1 | 1675 | 128 | 7010 | TRUE | TRUE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 41
Value |  |  | Views.Commissioning.Commissioning Mode | Modulating Condenser Fan 1 Output | 2644 | 293 |  | Views.Commission.Commissioning Mode | ModCondFan1Out | 2645 | 312 |  |  | Modulating Condenser Fan 1 Output | 2644 | 293 | 7024 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 41
Value |  |  | Views.Commissioning.Commissioning Mode | Condenser Fan 2 | 1675 | 129 |  | Views.Commission.Commissioning Mode | CF2 | 1709 | 110 |  |  | Condenser Fan 2 | 1675 | 129 | 7011 | TRUE | TRUE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 41
Value |  |  | Views.Commissioning.Commissioning Mode | Modulating Condenser Fan 2 Output | 2644 | 294 |  | Views.Commission.Commissioning Mode | ModCondFan2Out | 2645 | 313 |  |  | Modulating Condenser Fan 2 Output | 2644 | 294 | 7025 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 41
Value |  |  | Views.Commissioning.Commissioning Mode | Heating Stage Command 1 | 1714 | 149 |  | Views.Commission.Commissioning Mode | H1 | 1709 | 251 |  |  | Heating Stage Command 1 | 1714 | 149 | 7012 | TRUE | TRUE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 41
Value |  |  | Views.Commissioning.Commissioning Mode | Heating Stage Command 2 | 1714 | 150 |  | Views.Commission.Commissioning Mode | H2 | 1709 | 252 |  |  | Heating Stage Command 2 | 1714 | 150 | 7013 | TRUE | TRUE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 41
Value |  |  | Views.Commissioning.Commissioning Mode | Heating Stage Command 3 | 1714 | 151 |  | Views.Commission.Commissioning Mode | H3 | 1709 | 253 |  |  | Heating Stage Command 3 | 1714 | 151 | 7014 | TRUE | TRUE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 41
Value |  |  | Views.Commissioning.Commissioning Mode | Hot Gas Reheat | 1714 | 13 |  | Views.Commission.Commissioning Mode | HGR | 1709 | 324 |  |  | Hot Gas Reheat | 1714 | 13 | 7015 | TRUE | TRUE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 41
Value |  |  | Views.Commissioning.Commissioning Mode | Hot Gas Reheat | 1714 | 13 |  | Views.Commission.Commissioning Mode | HGR | 1709 | 324 |  |  | Hot Gas Reheat | 1714 | 13 | 7021 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 41
Value |  |  | Views.Commissioning.Commissioning Mode | Hot Gas Reheat Bleed Valve Command | 2644 | 238 |  | Views.Commission.Commissioning Mode | Hot Gas Reheat Bleed Valve Command | 2644 | 238 |  |  | Hot Gas Reheat Bleed Valve Command | 2644 | 238 | 7022 | TRUE | TRUE | FALSE | 9 | MultiState |  | Close/Open | 939 | [5 empty] | Close/Open | 939 | [5 empty] | 0 = Close 1 = Open | 41
Value |  |  | Views.Commissioning.Commissioning Mode | Economizer Damper % Command | 1675 | 51 |  | Views.Commission.Commissioning Mode | Econ | 1709 | 282 |  |  | Economizer Damper % Command | 1675 | 51 | 7016 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 41
Value |  |  | Views.Commissioning.Commissioning Mode | Exhaust Fan VFD % Command | 1675 | 236 |  | Views.Commission.Commissioning Mode | ExFanVFD | 1709 | 310 |  |  | Exhaust Fan VFD % Command | 1675 | 236 | 7018 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 41
Value |  |  | Views.Commissioning.Commissioning Mode | Exhaust Fan Command | 1675 | 235 |  | Views.Commission.Commissioning Mode | ExFan | 1709 | 309 |  |  | Exhaust Fan Command | 1675 | 235 | 7017 | TRUE | TRUE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 41
Value |  |  | Views.Commissioning.Commissioning Mode | Exhaust Damper % Command | 1675 | 242 |  | Views.Commission.Commissioning Mode | EAD-O | 1709 | 316 |  |  | Exhaust Damper % Command | 1675 | 242 | 7020 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 41
Value |  |  | Views.Commissioning.Commissioning Mode | Cancel ASCD Timers | 1675 | 336 |  | Views.Commission.Commissioning Mode | Cancel ASCD Timers | 1675 | 336 |  |  | Cancel ASCD Timers | 1675 | 336 | 7019 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 41
View | FALSE |  | Views.Controller | Controller | 1712 | 3 |  | Views.Controller | Controller | 1708 | 29
Group |  | FALSE | Views.Controller.Network | Network | 1714 | 19 |  | Views.Controller.Network | Network | 1709 | 398
Value |  |  | Views.Controller.Network | Device Name | 1675 | 326 |  | Views.Controller.Network | DevName | 1709 | 446 |  |  | Device Name | 1675 | 326 | 7009 | TRUE | TRUE | FALSE | 7 | String | [14 empty] | 30 |  | 29
Value |  |  | Views.Controller.Network | Address | 1675 | 282 |  | Views.Controller.Network | Address | 1709 | 352 |  |  | Address | 1675 | 282 | 7001 | TRUE | TRUE | FALSE | 17 | SignedInteger | 1s |  | 507:95 | 4 | 127 |  |  | 1s |  | 507:95 | 4 | 127 |  |  |  |  | 31
Value |  |  | Views.Controller.Network | Time Zone | 1675 | 278 |  | Views.Controller.Network | TimeZone | 1709 | 349 |  |  | Time Zone | 1675 | 278 | 7007 | TRUE | TRUE | FALSE | 9 | MultiState |  | SE RTU Time Zone | 1731 | [5 empty] | SE RTU Time Zone | 1731 | [5 empty] | 51 = Eastern 53 = Central 57 = Mountain 58 = Pacific ... | 30
Value |  |  | Views.Controller.Network | Description | 1675 | 2 |  | Views.Controller.Network | Descrip | 1709 | 473 |  |  | Description | 1675 | 2 | 7010 | TRUE | TRUE | FALSE | 7 | String | [14 empty] | 40 |  | 29
Value |  |  | Views.Controller.Network | Communication Status | 1675 | 281 |  | Views.Controller.Network | Comm-S | 1709 | 341 |  |  | Communication Status | 1675 | 281 | 7000 | TRUE | FALSE | FALSE | 9 | MultiState |  | MSTPDL Port Status | 302 | [5 empty] | MSTPDL Port Status | 302 | [5 empty] | 0 = Not Configured 1 = Active 2 = Waiting For Poll For Manager 3 = Not Received Token For Long ... | 31
Value |  |  | Views.Controller.Network | FC Comm Mode | 1675 | 496 |  | Views.Controller.Network | FcBusMode | 1709 | 628 |  |  | FC Comm Mode | 1675 | 496 | 7007 | TRUE | FALSE | FALSE | 9 | MultiState |  | FC Bus Mode | 1222 | [5 empty] | FC Bus Mode | 1222 | [5 empty] | 0 = Wired Field Bus 1 = Wireless Field Bus 2 = N2 Subordinate Field Bus 3 = Modbus Field Bus ... | 31
Value |  |  | Views.Controller.Network | Operating Baud Rate | 1675 | 284 |  | Views.Controller.Network | OprBaudRate | 1709 | 354 |  |  | Operating Baud Rate | 1675 | 284 | 7003 | TRUE | FALSE | FALSE | 9 | MultiState |  | MSTPDL Baud Rate | 300 | [5 empty] | MSTPDL Baud Rate | 300 | [5 empty] | 0 = Auto 1 = 1200 2 = 9600 3 = 19200 ... | 31
Value |  |  | Views.Controller.Network | Baud Rate | 1675 | 285 |  | Views.Controller.Network | BaudRate | 1709 | 355 |  |  | Baud Rate | 1675 | 285 | 7004 | TRUE | TRUE | FALSE | 9 | MultiState |  | MSTPDL Baud Rate | 300 | [5 empty] | MSTPDL Baud Rate | 300 | [5 empty] | 0 = Auto 1 = 1200 2 = 9600 3 = 19200 ... | 31
Value |  |  | Views.Controller.Network | Device OID | 1675 | 283 |  | Views.Controller.Network | DeviceId | 1709 | 353 |  |  | Device OID | 1675 | 283 | 7002 | TRUE | TRUE | FALSE | 2 | UnsignedLong | 1s |  | 507:95 | 0 | 4194302 |  |  | 1s |  | 507:95 | 0 | 4194302 |  |  |  |  | 31
Value |  |  | Views.Controller.Network | Language | 1675 | 267 |  | Views.Controller.Network | Language | 1709 | 337 |  |  | Language | 1675 | 267 | 7000 | TRUE | TRUE | FALSE | 9 | MultiState |  | SE RTU Languages | 1730 | [5 empty] | SE RTU Languages | 1730 | [5 empty] | 7 = English 10 = French 28 = Spanish | 29
Value |  |  | Views.Controller.Network | Units | 1675 | 268 |  | Views.Controller.Network | Units | 1709 | 338 |  |  | Units | 1675 | 268 | 7001 | TRUE | TRUE | FALSE | 9 | MultiState |  | Unit Set | 869 | [5 empty] | Unit Set | 869 | [5 empty] | 0 = IP 1 = SI | 29
Value |  |  | Views.Controller.Network | Number of Network Sensors Online | 1675 | 35 |  | Views.Controller.Network | #NetSensors | 1709 | 51 |  |  | Number of Network Sensors Online | 1675 | 35 | 7029 | TRUE | FALSE | FALSE | 17 | SignedInteger | 1s |  | 507:95 |  |  |  |  | 1s |  | 507:95 | [6 empty] | 25
Value |  |  | Views.Controller.Network | Relearn System | 1675 | 269 |  | Views.Controller.Network | Relearn | 1709 | 339 |  |  | Relearn System | 1675 | 269 | 7002 | TRUE | TRUE | FALSE | 9 | MultiState |  | Relearn | 1793 | [5 empty] | Relearn | 1793 | [5 empty] | 0 = False 1 = True | 29
Value |  |  | Views.Controller.Network | BACnet Encoding Type | 1675 | 847 |  | Views.Controller.Network | EncodeType | 1709 | 668 |  |  | BACnet Encoding Type | 1675 | 847 | 7008 | TRUE | TRUE | FALSE | 9 | MultiState |  | BACnet Encoding | 575 | [5 empty] | BACnet Encoding | 575 | [5 empty] | 0 = ISO 10646 (UCS-2) 1 = ANSI X3.4 (US-ASCII) 2 = Microsoft DBCS code page 932 (Japanese Shift JIS) 3 = ISO 10646 (UTF-8) | 31
Value |  |  | Views.Controller.Network | Radio Code Version | 1714 | 202 |  | Views.Controller.Network | Radio Code Version | 1714 | 202 |  |  | Radio Code Version | 1714 | 202 | 7009 | TRUE | FALSE | FALSE | 7 | String | [14 empty] | 30 |  | 31
Value |  |  | Views.Controller.Network | Active Channel | 1714 | 203 |  | Views.Controller.Network | Active Channel | 1714 | 203 |  |  | Active Channel | 1714 | 203 | 7010 | TRUE | FALSE | FALSE | 4 | Float | 1s |  | 507:95 |  |  |  |  | 1s |  | 507:95 | [6 empty] | 31
Value |  |  | Views.Controller.Network | Signal Strength | 1714 | 204 |  | Views.Controller.Network | Signal Strength | 1714 | 204 |  |  | Signal Strength | 1714 | 204 | 7011 | TRUE | FALSE | FALSE | 9 | MultiState |  | Wireless Signal Strength | 1223 | [5 empty] | Wireless Signal Strength | 1223 | [5 empty] | 0 = None 1 = Weak 2 = Average 3 = Strong | 31
Value |  |  | Views.Controller.Network | Connection Status | 1714 | 205 |  | Views.Controller.Network | Connection Status | 1714 | 205 |  |  | Connection Status | 1714 | 205 | 7012 | TRUE | FALSE | FALSE | 9 | MultiState |  | Radio Status | 1236 | [5 empty] | Radio Status | 1236 | [5 empty] | 0 = Offline 1 = Not Associated 2 = Online 3 = Radio Processor Fault | 31
Value |  |  | Views.Controller.Network | Network State | 1714 | 206 |  | Views.Controller.Network | Network State | 1714 | 206 |  |  | Network State | 1714 | 206 | 7013 | TRUE | FALSE | FALSE | 9 | MultiState |  | Wireless Status | 2513 | [5 empty] | Wireless Status | 2513 | [5 empty] | 0 = Normal 1 = Lost Coordinator 2 = Network Reforming 3 = Single Neighbor ... | 31
Value |  |  | Views.Controller.Network | Short Address | 1714 | 208 |  | Views.Controller.Network | Short Address | 1714 | 208 |  |  | Short Address | 1714 | 208 | 7015 | TRUE | FALSE | FALSE | 2 | UnsignedLong | 1s |  | 507:95 |  |  |  |  | 1s |  | 507:95 | [6 empty] | 31
Value |  |  | Views.Controller.Network | Baud Rate | 1675 | 285 |  | Views.Controller.Network | BaudRate | 1709 | 355 |  |  | Baud Rate | 1675 | 285 | 7019 | TRUE | TRUE | FALSE | 9 | MultiState |  | Baud Rate | 121 | [5 empty] | Baud Rate | 121 | [5 empty] | 0 = 9600 1 = 19200 2 = 38400 3 = 57600 4 = 115200 | 31
Value |  |  | Views.Controller.Network | Parity | 1675 | 1594 |  | Views.Controller.Network | Parity | 1709 | 703 |  |  | Parity | 1675 | 1594 | 7020 | TRUE | TRUE | FALSE | 9 | MultiState |  | Pager Parity | 430 | [5 empty] | Pager Parity | 430 | [5 empty] | 0 = None 1 = Odd 2 = Even 3 = Mark 4 = Space | 31
Value |  |  | Views.Controller.Network | Stop Bits | 1675 | 1595 |  | Views.Controller.Network | StopBits | 1709 | 704 |  |  | Stop Bits | 1675 | 1595 | 7021 | TRUE | TRUE | FALSE | 9 | MultiState |  | Stopbits | 124 | [5 empty] | Stopbits | 124 | [5 empty] | 0 = 1 1 = 1.5 2 = 2 | 31
Group |  | FALSE | Views.Controller.Firmware | Firmware | 1714 | 11 |  | Views.Controller.Firm | Firm | 1709 | 391
Group |  | TRUE | Views.Controller.Firmware.UCB | UCB | 1714 | 154 |  | Views.Controller.Firm.UCB | UCB | 1709 | 467
Value |  |  | Views.Controller.Firmware.UCB | Firmware Status | 1675 | 146 |  | Views.Controller.Firm.UCB | Firm-S | 1709 | 5 |  |  | Firmware Status | 1675 | 146 | 7005 | TRUE | FALSE | FALSE | 9 | MultiState |  | PMO Firmware Versions Status | 1727 | [5 empty] | PMO Firmware Versions Status | 1727 | [5 empty] | 0 = Firmware Versions OK 1 = Firmware Versions Do Not Match the Package | 1
Value |  |  | Views.Controller.Firmware.UCB | Firmware Version | 1675 | 5 |  | Views.Controller.Firm.UCB | FirmVer | 1709 | 4 |  |  | Firmware Version | 1675 | 5 | 7004 | TRUE | FALSE | FALSE | 7 | String | [14 empty] | 30 |  | 1
Value |  |  | Views.Controller.Firmware.UCB | Firmware Main Version | 1675 | 287 |  | Views.Controller.Firm.UCB | UCBMainVer | 1709 | 357 |  |  | Firmware Main Version | 1675 | 287 | 7000 | TRUE | FALSE | FALSE | 7 | String | [14 empty] | 30 |  | 32
Value |  |  | Views.Controller.Firmware.UCB | Application Version | 1675 | 288 |  | Views.Controller.Firm.UCB | UCBAppVer | 1709 | 358 |  |  | Application Version | 1675 | 288 | 7001 | TRUE | FALSE | FALSE | 7 | String | [14 empty] | 30 |  | 32
Value |  |  | Views.Controller.Firmware.UCB | Hardware Version | 1675 | 290 |  | Views.Controller.Firm.UCB | UCBHardVer | 1709 | 360 |  |  | Hardware Version | 1675 | 290 | 7003 | TRUE | FALSE | FALSE | 7 | String | [14 empty] | 30 |  | 32
Value |  |  | Views.Controller.Firmware.UCB | Serial Flash Size | 1675 | 1680 |  | Views.Controller.Firm.UCB | SerialFlashSize | 1709 | 738 |  |  | Serial Flash Size | 1675 | 1680 | 7044 | TRUE | FALSE | FALSE | 2 | UnsignedLong | 1s |  | 507:95 |  |  |  |  | 1s |  | 507:95 | [6 empty] | 1
Group |  | TRUE | Views.Controller.Firmware.Economizer | Economizer | 1714 | 8 |  | Views.Controller.Firm.Econ | Econ | 1709 | 282 | York RTU.System Controllers.Econ Controller:Present Value <> Not Present
Value |  |  | Views.Controller.Firmware.Economizer | Firmware Main Version | 1675 | 287 |  | Views.Controller.Firm.Econ | EconMainVer | 1709 | 361 |  |  | Firmware Main Version | 1675 | 287 | 7000 | TRUE | FALSE | FALSE | 7 | String | [14 empty] | 30 |  | 33
Value |  |  | Views.Controller.Firmware.Economizer | Application Version | 1675 | 288 |  | Views.Controller.Firm.Econ | EconAppVer | 1709 | 362 |  |  | Application Version | 1675 | 288 | 7001 | TRUE | FALSE | FALSE | 7 | String | [14 empty] | 30 |  | 33
Value |  |  | Views.Controller.Firmware.Economizer | Hardware Version | 1675 | 290 |  | Views.Controller.Firm.Econ | EconHardVer | 1709 | 364 |  |  | Hardware Version | 1675 | 290 | 7003 | TRUE | FALSE | FALSE | 7 | String | [14 empty] | 30 |  | 33
Group |  | TRUE | Views.Controller.Firmware.4 Stage | 4 Stage | 1714 | 155 |  | Views.Controller.Firm.4 Stage | 4 Stage | 1714 | 155 | York RTU.System Controllers.4 Stage Controller:Present Value <> Not Present
Value |  |  | Views.Controller.Firmware.4 Stage | Firmware Main Version | 1675 | 287 |  | Views.Controller.Firm.4 Stage | 4StgMainVer | 1709 | 365 |  |  | Firmware Main Version | 1675 | 287 | 7000 | TRUE | FALSE | FALSE | 7 | String | [14 empty] | 30 |  | 34
Value |  |  | Views.Controller.Firmware.4 Stage | Application Version | 1675 | 288 |  | Views.Controller.Firm.4 Stage | 4StgAppVer | 1709 | 366 |  |  | Application Version | 1675 | 288 | 7001 | TRUE | FALSE | FALSE | 7 | String | [14 empty] | 30 |  | 34
Value |  |  | Views.Controller.Firmware.4 Stage | Hardware Version | 1675 | 290 |  | Views.Controller.Firm.4 Stage | 4StgHardVer | 1709 | 368 |  |  | Hardware Version | 1675 | 290 | 7003 | TRUE | FALSE | FALSE | 7 | String | [14 empty] | 30 |  | 34
Group |  | TRUE | Views.Controller.Firmware.FDD Manager | FDD Manager | 1714 | 156 |  | Views.Controller.Firm.FDD Manager | FDD Manager | 1714 | 156 | York RTU.System Controllers.FDD Manager Controller:Present Value <> Not Present
Value |  |  | Views.Controller.Firmware.FDD Manager | Firmware Main Version | 1675 | 287 |  | Views.Controller.Firm.FDD Manager | FDDMMainVer | 1709 | 369 |  |  | Firmware Main Version | 1675 | 287 | 7000 | TRUE | FALSE | FALSE | 7 | String | [14 empty] | 30 |  | 35
Value |  |  | Views.Controller.Firmware.FDD Manager | Application Version | 1675 | 288 |  | Views.Controller.Firm.FDD Manager | FDDMAppVer | 1709 | 370 |  |  | Application Version | 1675 | 288 | 7001 | TRUE | FALSE | FALSE | 7 | String | [14 empty] | 30 |  | 35
Value |  |  | Views.Controller.Firmware.FDD Manager | Hardware Version | 1675 | 290 |  | Views.Controller.Firm.FDD Manager | FDDMHardVer | 1709 | 372 |  |  | Hardware Version | 1675 | 290 | 7003 | TRUE | FALSE | FALSE | 7 | String | [14 empty] | 30 |  | 35
Group |  | TRUE | Views.Controller.Firmware.FDD Subordinate | FDD Subordinate | 1714 | 157 |  | Views.Controller.Firm.FDD Subordinate | FDD Subordinate | 1714 | 157 | York RTU.System Controllers.FDD Subordinate Controller:Present Value <> Not Present
Value |  |  | Views.Controller.Firmware.FDD Subordinate | Firmware Main Version | 1675 | 287 |  | Views.Controller.Firm.FDD Subordinate | FDDSMainVer | 1709 | 373 |  |  | Firmware Main Version | 1675 | 287 | 7000 | TRUE | FALSE | FALSE | 7 | String | [14 empty] | 30 |  | 36
Value |  |  | Views.Controller.Firmware.FDD Subordinate | Application Version | 1675 | 288 |  | Views.Controller.Firm.FDD Subordinate | FDDSAppVer | 1709 | 374 |  |  | Application Version | 1675 | 288 | 7001 | TRUE | FALSE | FALSE | 7 | String | [14 empty] | 30 |  | 36
Value |  |  | Views.Controller.Firmware.FDD Subordinate | Hardware Version | 1675 | 290 |  | Views.Controller.Firm.FDD Subordinate | FDDSHardVer | 1709 | 376 |  |  | Hardware Version | 1675 | 290 | 7003 | TRUE | FALSE | FALSE | 7 | String | [14 empty] | 30 |  | 36
Group |  | FALSE | Views.Controller.Bluetooth | Bluetooth | 1714 | 271 |  | Views.Controller.Bluetooth | Bluetooth | 1709 | 771 | York RTU.Bluetooth.Status:Present Value = Normal
Value |  |  | Views.Controller.Bluetooth | Bluetooth Enabled | 1675 | 1691 |  | Views.Controller.Bluetooth | BT-Ena | 1709 | 784 |  |  | Bluetooth Enabled | 1675 | 1691 | 7006 | TRUE | TRUE | FALSE | 9 | MultiState |  | False/True | 1701 | [5 empty] | False/True | 1701 | [5 empty] | 0 = False 1 = True | 22
Value |  |  | Views.Controller.Bluetooth | BLE Connection Status | 1675 | 1683 |  | Views.Controller.Bluetooth | BT-Status | 1709 | 772 |  |  | BLE Connection Status | 1675 | 1683 | 7000 | TRUE | FALSE | FALSE | 9 | MultiState |  | BLE Connection Status | 40548 | [5 empty] | BLE Connection Status | 40548 | [5 empty] | 0 = Not Connected 1 = Waiting for Connection 2 = Connected 3 = Disabled 4 = Error | 22
Value |  |  | Views.Controller.Bluetooth | Initiate Connection | 1675 | 1684 |  | Views.Controller.Bluetooth | BT-Command | 1709 | 773 |  |  | Initiate Connection | 1675 | 1684 | 7001 | TRUE | TRUE | FALSE | 9 | MultiState |  | BLE Initiate Connection | 40549 | [5 empty] | BLE Initiate Connection | 40549 | [5 empty] | 0 = Start 1 = Stop 2 = Started 3 = Stopped | 22
Value |  |  | Views.Controller.Bluetooth | PIN | 1675 | 1685 |  | Views.Controller.Bluetooth | PIN | 1709 | 774 |  |  | PIN | 1675 | 1685 | 7002 | TRUE | FALSE | FALSE | 7 | String | [14 empty] | -1 |  | 22
Value |  |  | Views.Controller.Bluetooth | BLE Device Name | 1675 | 1686 |  | Views.Controller.Bluetooth | BT-Name | 1709 | 775 |  |  | BLE Device Name | 1675 | 1686 | 7003 | TRUE | FALSE | FALSE | 7 | String | [14 empty] | -1 |  | 22
Value |  |  | Views.Controller.Bluetooth | Clear Bluetooth Connections | 1675 | 1692 |  | Views.Controller.Bluetooth | BT-ClrInfo | 1709 | 785 |  |  | Clear Bluetooth Connections | 1675 | 1692 | 7007 | TRUE | TRUE | FALSE | 9 | MultiState |  | False/True | 1701 | [5 empty] | False/True | 1701 | [5 empty] | 0 = False 1 = True | 22
Value |  |  | Views.Controller.Bluetooth | Bluetooth Firmware Version | 1675 | 1687 |  | Views.Controller.Bluetooth | BT-Version | 1709 | 776 |  |  | Bluetooth Firmware Version | 1675 | 1687 | 7004 | TRUE | FALSE | FALSE | 7 | String | [14 empty] | -1 |  | 22
Group |  | FALSE | Views.Controller.Network Inputs | Network Inputs | 1714 | 20 |  | Views.Controller.NetworkInputs | NetworkInputs | 1709 | 399
Value |  |  | Views.Controller.Network Inputs | Network Override Space Temperature | 1675 | 18 |  | Views.Controller.NetworkInputs | NetST | 1709 | 33 |  |  | Network Override Space Temperature | 1675 | 18 | 7011 | TRUE | TRUE | FALSE | 4 | Float | 10ths | deg F | 507:64 | 0 | 100 |  |  | 10ths | deg C | 507:62 | 4 | 38 |  |  |  |  | 25
Value |  |  | Views.Controller.Network Inputs | Network Override Space Setpoint Offset | 1675 | 33 |  | Views.Controller.NetworkInputs | NetSSO | 1709 | 49 |  |  | Network Override Space Setpoint Offset | 1675 | 33 | 7027 | TRUE | TRUE | FALSE | 4 | Float | 10ths | delta deg F | 507:120 | -5 | 5 |  |  | 10ths | delta deg C | 507:359 | -3 | 3 |  |  |  |  | 25
Value |  |  | Views.Controller.Network Inputs | Network Override Zone Humidity | 1675 | 26 |  | Views.Controller.NetworkInputs | NetSH | 1709 | 42 |  |  | Network Override Zone Humidity | 1675 | 26 | 7020 | TRUE | TRUE | FALSE | 4 | Float | 10ths | %RH | 507:29 | 0 | 100 |  |  | 10ths | %RH | 507:29 | 0 | 100 |  |  |  |  | 25
Value |  |  | Views.Controller.Network Inputs | Network Occupancy Request | 1675 | 13 |  | Views.Controller.NetworkInputs | NetOcc | 1709 | 26 |  |  | Network Occupancy Request | 1675 | 13 | 7004 | TRUE | TRUE | FALSE | 9 | MultiState |  | Occ Sensor | 344 | [5 empty] | Occ Sensor | 344 | [5 empty] | 0 = Occupied 1 = UnOccupied 2 = Not Set | 25
Value |  |  | Views.Controller.Network Inputs | Network Temporary Occupancy Request | 1675 | 12 |  | Views.Controller.NetworkInputs | NetTempOcc | 1709 | 25 |  |  | Network Temporary Occupancy Request | 1675 | 12 | 7003 | TRUE | TRUE | FALSE | 9 | MultiState |  | False/True | 1701 | [5 empty] | False/True | 1701 | [5 empty] | 0 = False 1 = True | 25
Value |  |  | Views.Controller.Network Inputs | Network Override Indoor Air Quality | 1675 | 22 |  | Views.Controller.NetworkInputs | NetIAQ | 1709 | 38 |  |  | Network Override Indoor Air Quality | 1675 | 22 | 7016 | TRUE | TRUE | FALSE | 4 | Float | 10s | ppm | 507:96 | 0 | 5000 |  |  | 10s | ppm | 507:96 | 0 | 5000 |  |  |  |  | 25
Value |  |  | Views.Controller.Network Inputs | Network Override Fan Request | 1675 | 29 |  | Views.Controller.NetworkInputs | NetFanReq | 1709 | 45 |  |  | Network Override Fan Request | 1675 | 29 | 7023 | TRUE | TRUE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 25
Value |  |  | Views.Controller.Network Inputs | Network Override Outdoor Air Temperature | 1675 | 39 |  | Views.Controller.NetworkInputs | NetOAT | 1709 | 55 |  |  | Network Override Outdoor Air Temperature | 1675 | 39 | 7003 | TRUE | TRUE | FALSE | 4 | Float | 10ths | deg F | 507:64 | -50 | 125 |  |  | 10ths | deg C | 507:62 | -18 | 52 |  |  |  |  | 26
Value |  |  | Views.Controller.Network Inputs | Network Override Outdoor Air Humidity | 1675 | 44 |  | Views.Controller.NetworkInputs | NetOAH | 1709 | 60 |  |  | Network Override Outdoor Air Humidity | 1675 | 44 | 7008 | TRUE | TRUE | FALSE | 4 | Float | 10ths | %RH | 507:29 | 0 | 100 |  |  | 10ths | %RH | 507:29 | 0 | 100 |  |  |  |  | 26
Value |  |  | Views.Controller.Network Inputs | Network Override Outdoor Air Quality | 1675 | 49 |  | Views.Controller.NetworkInputs | NetOAQ | 1709 | 65 |  |  | Network Override Outdoor Air Quality | 1675 | 49 | 7013 | TRUE | TRUE | FALSE | 4 | Float | 10s | ppm | 507:96 | 0 | 5000 |  |  | 10s | ppm | 507:96 | 0 | 5000 |  |  |  |  | 26
Value |  |  | Views.Controller.Network Inputs | Network Override Purge Command | 1675 | 261 |  | Views.Controller.NetworkInputs | NetPurge | 1709 | 335 |  |  | Network Override Purge Command | 1675 | 261 | 7003 | TRUE | TRUE | FALSE | 9 | MultiState |  | False/True | 1701 | [5 empty] | False/True | 1701 | [5 empty] | 0 = False 1 = True | 27
Value |  |  | Views.Controller.Network Inputs | Direct Loadshed | 1675 | 497 |  | Views.Controller.NetworkInputs | DirLoadshd | 1709 | 629 |  |  | Direct Loadshed | 1675 | 497 | 7061 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 25
Value |  |  | Views.Controller.Network Inputs | Redline | 1675 | 500 |  | Views.Controller.NetworkInputs | Redline | 1709 | 632 |  |  | Redline | 1675 | 500 | 7062 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 25
Group |  | FALSE | Views.Controller.FDD | FDD | 1714 | 179 |  | Views.Controller.FDD | FDD | 1709 | 611
Value |  |  | Views.Controller.FDD | Unit Type | 1675 | 130 |  | Views.Controller.FDD | UnitType | 1709 | 111 |  |  | Unit Type | 1675 | 130 | 7020 | TRUE | TRUE | FALSE | 9 | MultiState |  | SE RTU Equipment Type | 1685 | [5 empty] | SE RTU Equipment Type | 1685 | [5 empty] | 0 = Not Used 1 = Package Cool 2 = Package HP 3 = Split Cool ... | 4
Value |  |  | Views.Controller.FDD | EER | 1675 | 131 |  | Views.Controller.FDD | EER | 1709 | 112 |  |  | EER | 1675 | 131 | 7021 | TRUE | TRUE | FALSE | 4 | Float | 1s |  | 507:95 | 0 | 20 |  |  | 1s |  | 507:95 | 0 | 20 |  |  |  |  | 4
Value |  |  | Views.Controller.FDD | Subcooling Goal | 1675 | 132 |  | Views.Controller.FDD | SubcoolGoal | 1709 | 113 |  |  | Subcooling Goal | 1675 | 132 | 7022 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | -10 | 20 |  |  | 1s | deg C | 507:62 | -23 | -6 |  |  |  |  | 4
Value |  |  | Views.Controller.FDD | Refrigerant Type | 1675 | 133 |  | Views.Controller.FDD | RefrigType | 1709 | 114 |  |  | Refrigerant Type | 1675 | 133 | 7023 | TRUE | TRUE | FALSE | 9 | MultiState |  | SE RTU Refrigerant Type | 1682 | [5 empty] | SE RTU Refrigerant Type | 1682 | [5 empty] | 0 = R22 1 = R12 2 = R500 3 = R134A ... | 4
Value |  |  | Views.Controller.FDD | High Side Port Location | 1675 | 134 |  | Views.Controller.FDD | HiSidePortLoc | 1709 | 115 |  |  | High Side Port Location | 1675 | 134 | 7024 | TRUE | TRUE | FALSE | 9 | MultiState |  | SE RTU High Side Port | 1681 | [5 empty] | SE RTU High Side Port | 1681 | [5 empty] | 0 = Liquid 1 = Discharge | 4
Value |  |  | Views.Controller.FDD | Evaporator Coil Type | 1675 | 101 |  | Views.Controller.FDD | EvapCoil-Type | 1709 | 116 |  |  | Evaporator Coil Type | 1675 | 101 | 7025 | TRUE | TRUE | FALSE | 9 | MultiState |  | Cooling Coil Type | 1722 | [5 empty] | Cooling Coil Type | 1722 | [5 empty] | 0 = MicroChannel 1 = Tube and Fin | 4
Value |  |  | Views.Controller.FDD | Condenser Coil Type | 1675 | 103 |  | Views.Controller.FDD | CondCoil-Type | 1709 | 117 |  |  | Condenser Coil Type | 1675 | 103 | 7026 | TRUE | TRUE | FALSE | 9 | MultiState |  | Cooling Coil Type | 1722 | [5 empty] | Cooling Coil Type | 1722 | [5 empty] | 0 = MicroChannel 1 = Tube and Fin | 4
Value |  |  | Views.Controller.FDD | Indoor Metering Device Type | 1675 | 135 |  | Views.Controller.FDD | InMeterDev-Type | 1709 | 118 |  |  | Indoor Metering Device Type | 1675 | 135 | 7027 | TRUE | TRUE | FALSE | 9 | MultiState |  | SE RTU Expansion Device | 1684 | [5 empty] | SE RTU Expansion Device | 1684 | [5 empty] | 0 = TxV 1 = FO 2 = TxV Or FO 3 = n | 4
Value |  |  | Views.Controller.FDD | Outdoor Metering Device Type | 1675 | 136 |  | Views.Controller.FDD | OutMeterDev-Type | 1709 | 445 |  |  | Outdoor Metering Device Type | 1675 | 136 | 7028 | TRUE | TRUE | FALSE | 9 | MultiState |  | SE RTU Expansion Device | 1684 | [5 empty] | SE RTU Expansion Device | 1684 | [5 empty] | 0 = TxV 1 = FO 2 = TxV Or FO 3 = n | 4
Value |  |  | Views.Controller.FDD | Unit Capacity | 1675 | 371 |  | Views.Controller.FDD | UnitCap | 1709 | 482 |  |  | Unit Capacity | 1675 | 371 | 7038 | TRUE | TRUE | FALSE | 4 | Float | 10ths | tons refr | 507:52 | 0 | 130 |  |  | 10ths | kW | 507:48 | 0 | 460 |  |  |  |  | 4
Value |  |  | Views.Controller.FDD | Fan Power | 1675 | 372 |  | Views.Controller.FDD | FanPower | 1709 | 483 |  |  | Fan Power | 1675 | 372 | 7039 | TRUE | TRUE | FALSE | 4 | Float | 10ths | kW | 507:48 | 0 | 19 |  |  | 10ths | kW | 507:48 | 0 | 19 |  |  |  |  | 4
Value |  |  | Views.Controller.FDD | Super Heat Goal | 1675 | 373 |  | Views.Controller.FDD | SuperHeatGoal | 1709 | 484 |  |  | Super Heat Goal | 1675 | 373 | 7040 | TRUE | TRUE | FALSE | 4 | Float | 10ths | deg F | 507:64 | 10 | 30 |  |  | 10ths | deg C | 507:62 | -12.2 | -1.1 |  |  |  |  | 4
Value |  |  | Views.Controller.FDD | Altitude | 1675 | 374 |  | Views.Controller.FDD | Altitude | 1709 | 485 |  |  | Altitude | 1675 | 374 | 7041 | TRUE | TRUE | FALSE | 4 | Float | 10ths | ft | 507:33 | -1500 | 30000 |  |  | 10ths | m | 507:31 | -457.2 | 9144 |  |  |  |  | 4
Group |  | FALSE | Views.Controller.Time | Time | 1675 | 271 |  | Views.Controller.Time | Time | 1709 | 342
Value |  |  | Views.Controller.Time | Time | 1675 | 271 |  | Views.Controller.Time | Time | 1709 | 342 |  |  | Time | 1675 | 271 | 7000 | TRUE | FALSE | FALSE | 11 | Time | [16 empty] | 30
Value |  |  | Views.Controller.Time | Date | 1675 | 272 |  | Views.Controller.Time | Date | 1709 | 343 |  |  | Date | 1675 | 272 | 7001 | TRUE | FALSE | FALSE | 10 | Date | [16 empty] | 30
Value |  |  | Views.Controller.Time | Time Zone | 1675 | 278 |  | Views.Controller.Time | TimeZone | 1709 | 349 |  |  | Time Zone | 1675 | 278 | 7007 | TRUE | TRUE | FALSE | 9 | MultiState |  | SE RTU Time Zone | 1731 | [5 empty] | SE RTU Time Zone | 1731 | [5 empty] | 51 = Eastern 53 = Central 57 = Mountain 58 = Pacific ... | 30
Group |  | FALSE | Views.Controller.Description | Description | 1675 | 2 |  | Views.Controller.Descrip | Descrip | 1709 | 473
Value |  |  | Views.Controller.Description | Rooftop Controller Type | 1675 | 466 |  | Views.Controller.Descrip | CntrlType | 1709 | 639 |  |  | Rooftop Controller Type | 1675 | 466 | 7017 | TRUE | TRUE | FALSE | 9 | MultiState |  | LCCS Controller Type | 1244 | [5 empty] | LCCS Controller Type | 1244 | [5 empty] | 0 = Changeover Bypass 1 = VAV 2 = Constant Volume 3 = TEC | 1
Value |  |  | Views.Controller.Description | Rooftop Equipment Type | 1675 | 467 |  | Views.Controller.Descrip | EquipType | 1709 | 640 |  |  | Rooftop Equipment Type | 1675 | 467 | 7018 | TRUE | TRUE | FALSE | 9 | MultiState |  | LCCS Equipment Type | 1368 | [5 empty] | LCCS Equipment Type | 1368 | [5 empty] | 0 = Unknown 1 = RTU 2 = Split 3 = HeatPump | 1
Group |  | FALSE | Views.Controller.Controller Info | Controller Info | 1712 | 26 |  | Views.Controller.Controller Info | Controller Info | 1712 | 26
Value |  |  | Views.Controller.Controller Info | Brightness Setting | 1675 | 641 |  | Views.Controller.Controller Info | Brightness Setting | 1675 | 641 |  |  | Brightness Setting | 1675 | 641 | 7011 | TRUE | TRUE | FALSE | 18 | UnsignedInteger | 1s |  | 507:95 | 3 | 10 |  |  | 1s |  | 507:95 | 3 | 10 |  |  |  |  | 29
Value |  |  | Views.Controller.Controller Info | Firmware Version | 1675 | 5 |  | Views.Controller.Controller Info | Firmware Version | 1675 | 5 |  |  | Firmware Version | 1675 | 5 | 7004 | TRUE | FALSE | FALSE | 7 | String | [14 empty] | 30 |  | 1
Value |  |  | Views.Controller.Controller Info | Firmware Status | 1675 | 146 |  | Views.Controller.Controller Info | Firmware Status | 1675 | 146 |  |  | Firmware Status | 1675 | 146 | 7005 | TRUE | FALSE | FALSE | 9 | MultiState |  | PMO Firmware Versions Status | 1727 | [5 empty] | PMO Firmware Versions Status | 1727 | [5 empty] | 0 = Firmware Versions OK 1 = Firmware Versions Do Not Match the Package | 1
Value |  |  | Views.Controller.Controller Info | Language | 1675 | 267 |  | Views.Controller.Controller Info | Language | 1675 | 267 |  |  | Language | 1675 | 267 | 7000 | TRUE | TRUE | FALSE | 9 | MultiState |  | SE RTU Languages | 1730 | [5 empty] | SE RTU Languages | 1730 | [5 empty] | 7 = English 10 = French 28 = Spanish | 29
Value |  |  | Views.Controller.Controller Info | Units | 1675 | 268 |  | Views.Controller.Controller Info | Units | 1675 | 268 |  |  | Units | 1675 | 268 | 7001 | TRUE | TRUE | FALSE | 9 | MultiState |  | Unit Set | 869 | [5 empty] | Unit Set | 869 | [5 empty] | 0 = IP 1 = SI | 29
View | FALSE |  | Views.Details | Details | 1712 | 4 |  | Views.Details | Details | 1708 | 31
Group |  | FALSE | Views.Details.Occupancy Status | Occupancy Status | 1675 | 757 |  | Views.Details.OCC | OCC | 1709 | 380
Value |  |  | Views.Details.Occupancy Status | Occupancy Mode | 1675 | 161 |  | Views.Details.OCC | OccMode | 1709 | 24 |  |  | Occupancy Mode | 1675 | 161 | 7002 | TRUE | TRUE | FALSE | 9 | MultiState |  | SE Occupancy Mode | 1728 | [5 empty] | SE Occupancy Mode | 1728 | [5 empty] | 0 = Schedule 1 = External | 25
Value |  |  | Views.Details.Occupancy Status | Occupancy Input | 1675 | 291 |  | Views.Details.OCC | OCC | 1709 | 380 |  |  | Occupancy Input | 1675 | 291 | 7030 | TRUE | FALSE | FALSE | 9 | MultiState |  | SE RTU Unocc/Occ | 1658 | [5 empty] | SE RTU Unocc/Occ | 1658 | [5 empty] | 0 = Occupied 1 = Unoccupied | 25
Value |  |  | Views.Details.Occupancy Status | Operational Occupancy | 1675 | 10 |  | Views.Details.OCC | OprOcc | 1709 | 23 |  |  | Operational Occupancy | 1675 | 10 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  | Occ Effective | 345 | [5 empty] | Occ Effective | 345 | [5 empty] | 0 = Occupied 1 = UnOccupied 2 = Bypass 3 = Standby | 25
Value |  |  | Views.Details.Occupancy Status | Occupancy Input Source | 1675 | 9 |  | Views.Details.OCC | OccSrc | 1709 | 22 |  |  | Occupancy Input Source | 1675 | 9 | 7000 | TRUE | FALSE | FALSE | 9 | MultiState |  | Effective Occupancy Source | 1668 | [5 empty] | Effective Occupancy Source | 1668 | [5 empty] | 0 = Local Input 1 = Local Network Sensor 2 = BAS Network Request 3 = Local Schedule 4 = Temporary Occupancy | 25
Value |  |  | Views.Details.Occupancy Status | Temporary Occupancy Input | 1675 | 329 |  | Views.Details.OCC | TempOCC | 1709 | 448 |  |  | Temporary Occupancy Input | 1675 | 329 | 7040 | TRUE | TRUE | FALSE | 9 | MultiState |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 | [5 empty] | 0 = Disable 1 = Enable | 25
Value |  |  | Views.Details.Occupancy Status | Temporary Occupancy Timeout | 1675 | 14 |  | Views.Details.OCC | TempOccTimeout | 1709 | 27 |  |  | Temporary Occupancy Timeout | 1675 | 14 | 7005 | TRUE | TRUE | FALSE | 17 | SignedInteger | 1s | minutes | 507:72 | 30 | 600 |  |  | 1s | minutes | 507:72 | 30 | 600 |  |  |  |  | 25
Value |  |  | Views.Details.Occupancy Status | Off During Unoccupied | 1675 | 501 |  | Views.Details.OCC | OffDurUnocc | 1709 | 633 |  |  | Off During Unoccupied | 1675 | 501 | 7059 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 25
Value |  |  | Views.Details.Occupancy Status | Optimal Start Enabled | 1675 | 377 |  | Views.Details.OCC | OptStrt-En | 1709 | 488 |  |  | Optimal Start Enabled | 1675 | 377 | 7036 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 13
Value |  |  | Views.Details.Occupancy Status | Early Start Period | 1675 | 379 |  | Views.Details.OCC | EarlyStrtPeriod | 1709 | 490 |  |  | Early Start Period | 1675 | 379 | 7038 | TRUE | TRUE | FALSE | 4 | Float | 1s | minutes | 507:72 | 0 | 120 |  |  | 1s | minutes | 507:72 | 0 | 120 |  |  |  |  | 13
Value |  |  | Views.Details.Occupancy Status | Pre Occupancy Purge Enable | 1675 | 1455 |  | Views.Details.OCC | PreOccPurgeEna | 1709 | 696 |  |  | Pre Occupancy Purge Enable | 1675 | 1455 | 7065 | TRUE | TRUE | FALSE | 9 | MultiState |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 | [5 empty] | 0 = Disable 1 = Enable | 25
Value |  |  | Views.Details.Occupancy Status | Pre Occupancy Purge Time | 1675 | 1458 |  | Views.Details.OCC | PreOccPurgeTime | 1709 | 698 |  |  | Pre Occupancy Purge Time | 1675 | 1458 | 7066 | TRUE | TRUE | FALSE | 4 | Float | 1s | minutes | 507:72 | 1 | 120 |  |  | 1s | minutes | 507:72 | 1 | 120 |  |  |  |  | 25
Value |  |  | Views.Details.Occupancy Status | Pre Occupancy Purge Upper SAT Setpoint | 1675 | 1459 |  | Views.Details.OCC | PreOccUpSAT_SP | 1709 | 699 |  |  | Pre Occupancy Purge Upper SAT Setpoint | 1675 | 1459 | 7067 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 80 | 100 |  |  | 1s | deg C | 507:62 | 26 | 38 |  |  |  |  | 25
Value |  |  | Views.Details.Occupancy Status | Pre Occupancy Purge Lower SAT Setpoint | 1675 | 1460 |  | Views.Details.OCC | PreOccLowSAT_SP | 1709 | 700 |  |  | Pre Occupancy Purge Lower SAT Setpoint | 1675 | 1460 | 7068 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 35 | 55 |  |  | 1s | deg C | 507:62 | 1 | 13 |  |  |  |  | 25
Group |  | FALSE | Views.Details.Cooling | Cooling | 1714 | 6 |  | Views.Details.Clg | Clg | 1709 | 388
Group |  | FALSE | Views.Details.Cooling.Setup | Setup | 1714 | 29 |  | Views.Details.Clg.Setup | Setup | 1709 | 408
Value |  |  | Views.Details.Cooling.Setup | CV Occupied Cooling Setpoint | 1675 | 141 |  | Views.Details.Clg.Setup | ClgOcc-Sp | 1709 | 123 |  |  | CV Occupied Cooling Setpoint | 1675 | 141 | 7033 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 45 | 98 |  |  | 1s | deg C | 507:62 | 7 | 36 |  |  |  |  | 4
Value |  |  | Views.Details.Cooling.Setup | CV Unoccupied Cooling Setpoint | 1675 | 142 |  | Views.Details.Clg.Setup | ClgUnocc-Sp | 1709 | 124 |  |  | CV Unoccupied Cooling Setpoint | 1675 | 142 | 7034 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 46 | 99 |  |  | 1s | deg C | 507:62 | 8 | 37 |  |  |  |  | 4
Value |  |  | Views.Details.Cooling.Setup | SZ VAV Occupied Cooling Setpoint | 1675 | 644 |  | Views.Details.Clg.Setup | SZVAVClgOcc-Sp | 1709 | 656 |  |  | SZ VAV Occupied Cooling Setpoint | 1675 | 644 | 7048 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 45 | 98 |  |  | 1s | deg C | 507:62 | 7 | 36 |  |  |  |  | 4
Value |  |  | Views.Details.Cooling.Setup | SZ VAV Unoccupied Cooling Setpoint | 1675 | 646 |  | Views.Details.Clg.Setup | SZVAVClgUnocc-Sp | 1709 | 657 |  |  | SZ VAV Unoccupied Cooling Setpoint | 1675 | 646 | 7049 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 45 | 98 |  |  | 1s | deg C | 507:62 | 7 | 36 |  |  |  |  | 4
Value |  |  | Views.Details.Cooling.Setup | Common Setpoint | 2596 | 0 |  | Views.Details.Clg.Setup | Common-SP | 1709 | 702 |  |  | Common Setpoint | 2596 | 0 | 7074 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 45 | 98 |  |  | 1s | deg C | 507:62 | 8 | 36 |  |  |  |  | 25
Value |  |  | Views.Details.Cooling.Setup | Auto Changeover | 1675 | 1469 |  | Views.Details.Clg.Setup | Auto Changeover | 1675 | 1469 |  |  | Auto Changeover | 1675 | 1469 | 7076 | TRUE | TRUE | FALSE | 4 | Float | 10ths | delta deg F | 507:120 | 2 | 5 |  |  | 10ths | delta deg C | 507:359 | 1.1 | 2.8 |  |  |  |  | 25
Value |  |  | Views.Details.Cooling.Setup | Heat Cool Setpoint Mode | 1714 | 212 |  | Views.Details.Clg.Setup | Heat Cool Setpoint Mode | 1714 | 212 |  |  | Heat Cool Setpoint Mode | 1714 | 212 | 7075 | TRUE | TRUE | FALSE | 9 | MultiState |  | Heat Cool Setpoint Mode | 2596 | [5 empty] | Heat Cool Setpoint Mode | 2596 | [5 empty] | 0 = Common Setpoint 1 = Individual Setpoints | 25
Value |  |  | Views.Details.Cooling.Setup | Compressor Stage 1 Enabled | 1714 | 40 |  | Views.Details.Clg.Setup | C1-En | 1709 | 135 |  |  | Compressor Stage Enabled | 1675 | 86 | 7003 | TRUE | TRUE | FALSE | 9 | MultiState |  | Yes/No | 1698 | [5 empty] | Yes/No | 1698 | [5 empty] | 0 = Yes 1 = No | 5
Value |  |  | Views.Details.Cooling.Setup | Compressor Stage 2 Enabled | 1714 | 56 |  | Views.Details.Clg.Setup | C2-En | 1709 | 136 |  |  | Compressor Stage Enabled | 1675 | 86 | 7003 | TRUE | TRUE | FALSE | 9 | MultiState |  | Yes/No | 1698 | [5 empty] | Yes/No | 1698 | [5 empty] | 0 = Yes 1 = No | 7
Value |  |  | Views.Details.Cooling.Setup | Compressor Stage 3 Enabled | 1714 | 72 |  | Views.Details.Clg.Setup | C3-En | 1709 | 137 |  |  | Compressor Stage Enabled | 1675 | 86 | 7003 | TRUE | TRUE | FALSE | 9 | MultiState |  | Yes/No | 1698 | [5 empty] | Yes/No | 1698 | [5 empty] | 0 = Yes 1 = No | 9
Value |  |  | Views.Details.Cooling.Setup | Compressor Stage 4 Enabled | 1714 | 88 |  | Views.Details.Clg.Setup | C4-En | 1709 | 138 |  |  | Compressor Stage Enabled | 1675 | 86 | 7003 | TRUE | TRUE | FALSE | 9 | MultiState |  | Yes/No | 1698 | [5 empty] | Yes/No | 1698 | [5 empty] | 0 = Yes 1 = No | 11
Value |  |  | Views.Details.Cooling.Setup | Minimum Runtime for a Cooling Stage | 1675 | 71 |  | Views.Details.Clg.Setup | MinRtCoolStg | 1709 | 94 |  |  | Minimum Runtime for a Cooling Stage | 1675 | 71 | 7003 | TRUE | TRUE | FALSE | 16 | Byte | 1s | minutes | 507:72 | 3 | 10 |  |  | 1s | minutes | 507:72 | 3 | 10 |  |  |  |  | 4
Value |  |  | Views.Details.Cooling.Setup | Cooling Adaptive Tuning Enable | 1675 | 486 |  | Views.Details.Clg.Setup | ClgAdapTunEn | 1709 | 617 |  |  | Cooling Adaptive Tuning Enable | 1675 | 486 | 7043 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 4
Value |  |  | Views.Details.Cooling.Setup | Low Ambient Enabled | 1675 | 649 |  | Views.Details.Clg.Setup | LowAmb-En | 1709 | 662 |  |  | Low Ambient Enabled | 1675 | 649 | 7051 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 4
Value |  |  | Views.Details.Cooling.Setup | Low Ambient Cooling Stages 10 on 5 off Setpoint | 1675 | 78 |  | Views.Details.Clg.Setup | LowAmb10On5OffSp | 1709 | 101 |  |  | Low Ambient Cooling Stages 10 on 5 off Setpoint | 1675 | 78 | 7010 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 0 | 60 |  |  | 1s | deg C | 507:62 | -18 | 15 |  |  |  |  | 4
Value |  |  | Views.Details.Cooling.Setup | Lead/Lag Equalize Cooling Stage Runtime Enabled | 1675 | 72 |  | Views.Details.Clg.Setup | LeadLag-En | 1709 | 95 |  |  | Lead/Lag Equalize Cooling Stage Runtime Enabled | 1675 | 72 | 7004 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 4
Value |  |  | Views.Details.Cooling.Setup | OAT Cooling Cutout Enabled | 1675 | 127 |  | Views.Details.Clg.Setup | ClgOATCutout-En | 1709 | 97 |  |  | OAT Cooling Cutout Enabled | 1675 | 127 | 7006 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 4
Value |  |  | Views.Details.Cooling.Setup | OAT Cooling Cutout | 1675 | 74 |  | Views.Details.Clg.Setup | ClgOATCutout | 1709 | 98 |  |  | OAT Cooling Cutout | 1675 | 74 | 7007 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 0 | 100 |  |  | 1s | deg C | 507:62 | -18 | 38 |  |  |  |  | 4
Value |  |  | Views.Details.Cooling.Setup | SAT Limit for Cooling Enable | 1675 | 143 |  | Views.Details.Clg.Setup | SATCoolLimit-En | 1709 | 106 |  |  | SAT Limit for Cooling Enable | 1675 | 143 | 7015 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 4
Value |  |  | Views.Details.Cooling.Setup | SAT Limit for Cooling Setpoint | 1675 | 75 |  | Views.Details.Clg.Setup | SATCoolLimit-Sp | 1709 | 107 |  |  | SAT Limit for Cooling Setpoint | 1675 | 75 | 7016 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 40 | 65 |  |  | 1s | deg C | 507:62 | 4 | 18 |  |  |  |  | 4
Value |  |  | Views.Details.Cooling.Setup | Hot Gas Bypass Present | 1675 | 89 |  | Views.Details.Clg.Setup | HGP-Inst | 1709 | 139 |  |  | Hot Gas Bypass Present | 1675 | 89 | 7004 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 5
Value |  |  | Views.Details.Cooling.Setup | Freeze Condition Setpoint | 1675 | 99 |  | Views.Details.Clg.Setup | Freeze-Sp | 1709 | 108 |  |  | Freeze Condition Setpoint | 1675 | 99 | 7017 | TRUE | TRUE | FALSE | 4 | Float | 10ths | deg F | 507:64 | 20 | 32 |  |  | 10ths | deg C | 507:62 | -7 | 0 |  |  |  |  | 4
Value |  |  | Views.Details.Cooling.Setup | Pump Out Enable | 1675 | 619 |  | Views.Details.Clg.Setup | PmpOut-En | 1709 | 644 |  |  | Pump Out Enable | 1675 | 619 | 7046 | TRUE | TRUE | FALSE | 9 | MultiState |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 | [5 empty] | 0 = Disable 1 = Enable | 4
Value |  |  | Views.Details.Cooling.Setup | Low Ambient Fan Pre-run Time For Cooling | 1675 | 73 |  | Views.Details.Clg.Setup | LowAmbFanPrerunCool | 1709 | 96 |  |  | Low Ambient Fan Pre-run Time For Cooling | 1675 | 73 | 7005 | TRUE | TRUE | FALSE | 17 | SignedInteger | 1s | seconds | 507:73 | 0 | 255 |  |  | 1s | seconds | 507:73 | 0 | 255 |  |  |  |  | 4
Value |  |  | Views.Details.Cooling.Setup | Cooling Manual Tuning | 1675 | 478 |  | Views.Details.Clg.Setup | ClgManualTune | 1709 | 690 |  |  | Operational Error Sigma | 1675 | 1076 | 7054 | TRUE | TRUE | FALSE | 4 | Float | 10ths | delta deg F | 507:120 | 1 | 2.5 |  |  | 10ths | delta deg C | 507:359 | 0.6 | 1.5 |  |  |  |  | 4
Value |  |  | Views.Details.Cooling.Setup | Low Ambient Start | 1675 | 1457 |  | Views.Details.Clg.Setup | LowAmbStart | 1709 | 697 |  |  | Low Ambient Start | 1675 | 1457 | 7056 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 4
Value |  |  | Views.Details.Cooling.Setup | 4 Pipe Split Enable | 1675 | 1454 |  | Views.Details.Clg.Setup | 4pipeEna | 1709 | 695 |  |  | 4 Pipe Split Enable | 1675 | 1454 | 7055 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 4
Value |  |  | Views.Details.Cooling.Setup | Cooling Rapid Start Enable | 1714 | 267 |  | Views.Details.Clg.Setup | ClgRapidStartEn | 1709 | 767 |  |  | Cooling Rapid Start Enable | 1714 | 267 | 7101 | TRUE | TRUE | FALSE | 9 | MultiState |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 | [5 empty] | 0 = Disable 1 = Enable | 4
Value |  |  | Views.Details.Cooling.Setup | Cooling Rapid Start Time | 1714 | 269 |  | Views.Details.Clg.Setup | ClgRapidStartTime | 1709 | 769 |  |  | Cooling Rapid Start Time | 1714 | 269 | 7102 | TRUE | TRUE | FALSE | 4 | Float | 1s | minutes | 507:72 | 2 | 30 |  |  | 1s | minutes | 507:72 | 2 | 30 |  |  |  |  | 4
Group |  | FALSE | Views.Details.Cooling.Service | Service | 1714 | 27 |  | Views.Details.Clg.Service | Service | 1709 | 406
Group |  | TRUE | Views.Details.Cooling.Service.Unit | Unit | 1714 | 153 |  | Views.Details.Clg.Service.Unit | Unit | 1709 | 472
Value |  |  | Views.Details.Cooling.Service.Unit | Staged Cooling Command | 1675 | 628 |  | Views.Details.Clg.Service.Unit | StgClgCmd | 1709 | 648 |  |  | Staged Cooling Command | 1675 | 628 | 7047 | TRUE | FALSE | FALSE | 4 | Float | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 | [6 empty] | 4
Value |  |  | Views.Details.Cooling.Service.Unit | CV Operating Cooling Setpoint | 1675 | 144 |  | Views.Details.Clg.Service.Unit | OprCVClg-Sp | 1709 | 125 |  |  | CV Operating Cooling Setpoint | 1675 | 144 | 7035 | TRUE | FALSE | FALSE | 4 | Float | 100ths | deg F | 507:64 |  |  |  |  | 100ths | deg C | 507:62 | [6 empty] | 4
Value |  |  | Views.Details.Cooling.Service.Unit | VAV Operating Cooling Setpoint | 1675 | 1679 |  | Views.Details.Clg.Service.Unit | OprVAVClg-Sp | 1709 | 122 |  |  | VAV Operating Cooling Setpoint | 1675 | 1679 | 7032 | TRUE | FALSE | FALSE | 4 | Float | 100ths | deg F | 507:64 |  |  |  |  | 100ths | deg C | 507:62 | [6 empty] | 4
Value |  |  | Views.Details.Cooling.Service.Unit | Cooling Status | 1675 | 69 |  | Views.Details.Clg.Service.Unit | Clg-S | 1709 | 93 |  |  | Cooling Status | 1675 | 69 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  | SE RTU Cooling Control Status | 1740 | [5 empty] | SE RTU Cooling Control Status | 1740 | [5 empty] | 0 = Off-Idle 1 = Thermostat Cooling 2 = Unoccupied Cooling 3 = Occupied Cooling ... | 4
Value |  |  | Views.Details.Cooling.Service.Unit | Operational Outdoor Air Temperature | 1675 | 36 |  | Views.Details.Clg.Service.Unit | OprOAT | 1709 | 52 |  |  | Operational Outdoor Air Temperature | 1675 | 36 | 7000 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 26
Value |  |  | Views.Details.Cooling.Service.Unit | Operational Space Temperature | 1675 | 15 |  | Views.Details.Clg.Service.Unit | OprST | 1709 | 28 |  |  | Operational Space Temperature | 1675 | 15 | 7006 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 25
Value |  |  | Views.Details.Cooling.Service.Unit | Return Air Temperature | 1675 | 65 |  | Views.Details.Clg.Service.Unit | RAT | 1709 | 297 |  |  | Return Air Temperature | 1675 | 65 | 7038 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 25
Value |  |  | Views.Details.Cooling.Service.Unit | Econ Free Cooling Available | 1675 | 52 |  | Views.Details.Clg.Service.Unit | Econ-Free | 1709 | 283 |  |  | Econ Free Cooling Available | 1675 | 52 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 19
Value |  |  | Views.Details.Cooling.Service.Unit | Supply Air Temperature | 1675 | 182 |  | Views.Details.Clg.Service.Unit | SAT | 1709 | 80 |  |  | Supply Air Temperature | 1675 | 182 | 7014 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 3
Value |  |  | Views.Details.Cooling.Service.Unit | Y1 - Thermostat | 1675 | 150 |  | Views.Details.Clg.Service.Unit | Y1-Tstat | 1709 | 11 |  |  | Y1 - Thermostat | 1675 | 150 | 7000 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 2
Value |  |  | Views.Details.Cooling.Service.Unit | Y2 - Thermostat | 1675 | 151 |  | Views.Details.Clg.Service.Unit | Y2-Tstat | 1709 | 12 |  |  | Y2 - Thermostat | 1675 | 151 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 2
Value |  |  | Views.Details.Cooling.Service.Unit | Y3 - Thermostat | 1675 | 152 |  | Views.Details.Clg.Service.Unit | Y3-Tstat | 1709 | 13 |  |  | Y3 - Thermostat | 1675 | 152 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 2
Value |  |  | Views.Details.Cooling.Service.Unit | Y4 - Thermostat | 1675 | 153 |  | Views.Details.Clg.Service.Unit | Y4-Tstat | 1709 | 14 |  |  | Y4 - Thermostat | 1675 | 153 | 7003 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 2
Value |  |  | Views.Details.Cooling.Service.Unit | Condenser Fan 1 | 1675 | 128 |  | Views.Details.Clg.Service.Unit | CN-Fan | 1709 | 109 |  |  | Condenser Fan 1 | 1675 | 128 | 7018 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 4
Value |  |  | Views.Details.Cooling.Service.Unit | Modulating Condenser Fan 1 Output | 2644 | 293 |  | Views.Details.Clg.Service.Unit | ModCondFan1Out | 2645 | 312 |  |  | Modulating Condenser Fan 1 Output | 2644 | 293 | 7065 | TRUE | FALSE | FALSE | 4 | Float | 10ths | % | 507:98 | 0 | 100 |  |  | 10ths | % | 507:98 | 0 | 100 |  |  |  |  | 4
Value |  |  | Views.Details.Cooling.Service.Unit | Condenser Fan 2 | 1675 | 129 |  | Views.Details.Clg.Service.Unit | CF2 | 1709 | 110 |  |  | Condenser Fan 2 | 1675 | 129 | 7019 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 4
Value |  |  | Views.Details.Cooling.Service.Unit | Modulating Condenser Fan 2 Output | 2644 | 294 |  | Views.Details.Clg.Service.Unit | ModCondFan2Out | 2645 | 313 |  |  | Modulating Condenser Fan 2 Output | 2644 | 294 | 7066 | TRUE | FALSE | FALSE | 4 | Float | 10ths | % | 507:98 | 0 | 100 |  |  | 10ths | % | 507:98 | 0 | 100 |  |  |  |  | 4
Group |  | TRUE | Views.Details.Cooling.Service.Stage 1 | Stage 1 | 1714 | 31 |  | Views.Details.Clg.Service.Stage 1 | Stage 1 | 1709 | 410
Value |  |  | Views.Details.Cooling.Service.Stage 1 | Compressor Stage 1 Status | 1714 | 39 |  | Views.Details.Clg.Service.Stage 1 | C1-S | 1709 | 131 |  |  | Compressor Stage Status | 1675 | 85 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  | SE RTU DX Cooling Circuit 1 Status | 1741 | [5 empty] | SE RTU DX Cooling Circuit 1 Status | 1741 | [5 empty] | 0 = Off-Idle 1 = On-Minimum On Time 2 = On-Normal Command 3 = Off-Cooling Is Disabled ... | 5
Value |  |  | Views.Details.Cooling.Service.Stage 1 | Compressor Stage Command 1 | 1714 | 145 |  | Views.Details.Clg.Service.Stage 1 | C1 | 1709 | 127 |  |  | Compressor Stage Command | 1675 | 84 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 5
Value |  |  | Views.Details.Cooling.Service.Stage 1 | Modulating Compressor Output | 2644 | 292 |  | Views.Details.Clg.Service.Stage 1 | ModCompOut | 2645 | 311 |  |  | Modulating Compressor Output | 2644 | 292 | 7067 | TRUE | FALSE | FALSE | 4 | Float | 10ths | % | 507:98 | 0 | 100 |  |  | 10ths | % | 507:98 | 0 | 100 |  |  |  |  | 4
Value |  |  | Views.Details.Cooling.Service.Stage 1 | Min On Time Remaining 1 | 1714 | 41 |  | Views.Details.Clg.Service.Stage 1 | C1OnTmr | 1709 | 148 |  |  | Min On Time Remaining | 1675 | 92 | 7007 | TRUE | FALSE | FALSE | 17 | SignedInteger | 1s | seconds | 507:73 |  |  |  |  | 1s | seconds | 507:73 | [6 empty] | 5
Value |  |  | Views.Details.Cooling.Service.Stage 1 | Anti-Short Cycle Delay Time Remaining 1 | 1714 | 42 |  | Views.Details.Clg.Service.Stage 1 | C1ASCDTmr | 1709 | 152 |  |  | Anti-Short Cycle Delay Time Remaining | 1675 | 145 | 7008 | TRUE | FALSE | FALSE | 17 | SignedInteger | 1s | seconds | 507:73 |  |  |  |  | 1s | seconds | 507:73 | [6 empty] | 5
Value |  |  | Views.Details.Cooling.Service.Stage 1 | Compressor Stage Accumulated Runtime 1 | 1714 | 43 |  | Views.Details.Clg.Service.Stage 1 | C1RunTim | 1709 | 140 |  |  | Compressor Stage Accumulated Runtime | 1675 | 90 | 7005 | TRUE | TRUE | FALSE | 4 | Float | 1s | hours | 507:71 | 0 | 10000 |  |  | 1s | hours | 507:71 | 0 | 10000 |  |  |  |  | 5
Value |  |  | Views.Details.Cooling.Service.Stage 1 | Efficiency Index 1 | 1714 | 52 |  | Views.Details.Clg.Service.Stage 1 | C1-EI | 1709 | 216 |  |  | Efficiency Index | 1675 | 201 | 7008 | TRUE | FALSE | FALSE | 4 | Float | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 | [6 empty] | 6
Value |  |  | Views.Details.Cooling.Service.Stage 1 | Capacity Index 1 | 1714 | 53 |  | Views.Details.Clg.Service.Stage 1 | C1-CI | 1709 | 220 |  |  | Capacity Index | 1675 | 202 | 7009 | TRUE | FALSE | FALSE | 4 | Float | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 | [6 empty] | 6
Value |  |  | Views.Details.Cooling.Service.Stage 1 | Condensing Temperature over Ambient 1 | 1714 | 54 |  | Views.Details.Clg.Service.Stage 1 | C1-CondTempOvrAmb | 1709 | 212 |  |  | Condensing Temperature over Ambient | 1675 | 200 | 7007 | TRUE | FALSE | FALSE | 4 | Float | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 | [6 empty] | 6
Value |  |  | Views.Details.Cooling.Service.Stage 1 | Evaporating Temperature Value Circuit 1 | 1714 | 164 |  | Views.Details.Clg.Service.Stage 1 | C1-EvapTempValue | 1709 | 534 |  |  | Evaporating Temp Value | 1675 | 424 | 7014 | TRUE | FALSE | FALSE | 4 | Float | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 | [6 empty] | 6
Value |  |  | Views.Details.Cooling.Service.Stage 1 | Cooling Circuit Test Status | 1675 | 193 |  | Views.Details.Clg.Service.Stage 1 | ClgCktTestS-1 | 1709 | 478 |  |  | Cooling Circuit Test Status | 1675 | 193 | 7000 | TRUE | FALSE | FALSE | 9 | MultiState |  | SE FDD Codes | 1694 | [5 empty] | SE FDD Codes | 1694 | [5 empty] | 0 = Unknown Status 1 = Basic Data Not Available Manual Entry 2 = Basic Data Not Available 3 = Return Wet Bulb Temp Not Available ... | 6
Value |  |  | Views.Details.Cooling.Service.Stage 1 | Superheat | 1675 | 198 |  | Views.Details.Clg.Service.Stage 1 | C1-SuperHeat | 1709 | 204 |  |  | Superheat | 1675 | 198 | 7005 | TRUE | FALSE | FALSE | 4 | Float | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 | [6 empty] | 6
Value |  |  | Views.Details.Cooling.Service.Stage 1 | Subcooling | 1675 | 199 |  | Views.Details.Clg.Service.Stage 1 | C1-SubCool | 1709 | 208 |  |  | Subcooling | 1675 | 199 | 7006 | TRUE | FALSE | FALSE | 4 | Float | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 | [6 empty] | 6
Value |  |  | Views.Details.Cooling.Service.Stage 1 | Oil Level Switch | 2644 | 507 |  | Views.Details.Clg.Service.Stage 1 | OIL-A | 2645 | 467 |  |  | Oil Level Switch | 2644 | 507 | 7076 | TRUE | FALSE | FALSE | 9 | MultiState |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 | [5 empty] | 0 = Normal 1 = Alarm | 4
Group |  | TRUE | Views.Details.Cooling.Service.Stage 2 | Stage 2 | 1714 | 32 |  | Views.Details.Clg.Service.Stage 2 | Stage 2 | 1709 | 411 | York RTU.Cooling Control.Cooling Stages Available:Present Value > 1
Value |  |  | Views.Details.Cooling.Service.Stage 2 | Compressor Stage 2 Status | 1714 | 55 |  | Views.Details.Clg.Service.Stage 2 | C2-S | 1709 | 132 |  |  | Compressor Stage Status | 1675 | 85 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  | SE RTU DX Cooling Circuit 1 Status | 1741 | [5 empty] | SE RTU DX Cooling Circuit 1 Status | 1741 | [5 empty] | 0 = Off-Idle 1 = On-Minimum On Time 2 = On-Normal Command 3 = Off-Cooling Is Disabled ... | 7
Value |  |  | Views.Details.Cooling.Service.Stage 2 | Compressor Stage Command 2 | 1714 | 146 |  | Views.Details.Clg.Service.Stage 2 | C2 | 1709 | 128 |  |  | Compressor Stage Command | 1675 | 84 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 7
Value |  |  | Views.Details.Cooling.Service.Stage 2 | Min On Time Remaining 2 | 1714 | 57 |  | Views.Details.Clg.Service.Stage 2 | C2OnTmr | 1709 | 149 |  |  | Min On Time Remaining | 1675 | 92 | 7007 | TRUE | FALSE | FALSE | 17 | SignedInteger | 1s | seconds | 507:73 |  |  |  |  | 1s | seconds | 507:73 | [6 empty] | 7
Value |  |  | Views.Details.Cooling.Service.Stage 2 | Anti-Short Cycle Delay Time Remaining 2 | 1714 | 58 |  | Views.Details.Clg.Service.Stage 2 | C2ASCDTmr | 1709 | 153 |  |  | Anti-Short Cycle Delay Time Remaining | 1675 | 145 | 7008 | TRUE | FALSE | FALSE | 17 | SignedInteger | 1s | seconds | 507:73 |  |  |  |  | 1s | seconds | 507:73 | [6 empty] | 7
Value |  |  | Views.Details.Cooling.Service.Stage 2 | Compressor Stage Accumulated Runtime 2 | 1714 | 59 |  | Views.Details.Clg.Service.Stage 2 | C2RunTim | 1709 | 141 |  |  | Compressor Stage Accumulated Runtime | 1675 | 90 | 7005 | TRUE | TRUE | FALSE | 4 | Float | 1s | hours | 507:71 | 0 | 10000 |  |  | 1s | hours | 507:71 | 0 | 10000 |  |  |  |  | 7
Value |  |  | Views.Details.Cooling.Service.Stage 2 | Efficiency Index 2 | 1714 | 68 |  | Views.Details.Clg.Service.Stage 2 | C2-EI | 1709 | 217 |  |  | Efficiency Index | 1675 | 201 | 7008 | TRUE | FALSE | FALSE | 4 | Float | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 | [6 empty] | 8
Value |  |  | Views.Details.Cooling.Service.Stage 2 | Capacity Index 2 | 1714 | 69 |  | Views.Details.Clg.Service.Stage 2 | C2-CI | 1709 | 221 |  |  | Capacity Index | 1675 | 202 | 7009 | TRUE | FALSE | FALSE | 4 | Float | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 | [6 empty] | 8
Value |  |  | Views.Details.Cooling.Service.Stage 2 | Condensing Temperature over Ambient 2 | 1714 | 70 |  | Views.Details.Clg.Service.Stage 2 | C2-CondTempOvrAmb | 1709 | 213 |  |  | Condensing Temperature over Ambient | 1675 | 200 | 7007 | TRUE | FALSE | FALSE | 4 | Float | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 | [6 empty] | 8
Value |  |  | Views.Details.Cooling.Service.Stage 2 | Evaporating Temperature Value Circuit 2 | 1714 | 165 |  | Views.Details.Clg.Service.Stage 2 | C2-EvapTempValue | 1709 | 535 |  |  | Evaporating Temp Value | 1675 | 424 | 7014 | TRUE | FALSE | FALSE | 4 | Float | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 | [6 empty] | 8
Value |  |  | Views.Details.Cooling.Service.Stage 2 | Cooling Circuit Test Status | 1675 | 193 |  | Views.Details.Clg.Service.Stage 2 | ClgCktTestS-2 | 1709 | 479 |  |  | Cooling Circuit Test Status | 1675 | 193 | 7000 | TRUE | FALSE | FALSE | 9 | MultiState |  | SE FDD Codes | 1694 | [5 empty] | SE FDD Codes | 1694 | [5 empty] | 0 = Unknown Status 1 = Basic Data Not Available Manual Entry 2 = Basic Data Not Available 3 = Return Wet Bulb Temp Not Available ... | 8
Value |  |  | Views.Details.Cooling.Service.Stage 2 | Superheat | 1675 | 198 |  | Views.Details.Clg.Service.Stage 2 | C2-SuperHeat | 1709 | 205 |  |  | Superheat | 1675 | 198 | 7005 | TRUE | FALSE | FALSE | 4 | Float | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 | [6 empty] | 8
Value |  |  | Views.Details.Cooling.Service.Stage 2 | Subcooling | 1675 | 199 |  | Views.Details.Clg.Service.Stage 2 | C2-SubCool | 1709 | 209 |  |  | Subcooling | 1675 | 199 | 7006 | TRUE | FALSE | FALSE | 4 | Float | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 | [6 empty] | 8
Group |  | TRUE | Views.Details.Cooling.Service.Stage 3 | Stage 3 | 1714 | 33 |  | Views.Details.Clg.Service.Stage 3 | Stage 3 | 1709 | 412 | York RTU.Cooling Control.Cooling Stages Available:Present Value > 2
Value |  |  | Views.Details.Cooling.Service.Stage 3 | Compressor Stage 3 Status | 1714 | 71 |  | Views.Details.Clg.Service.Stage 3 | C3-S | 1709 | 133 |  |  | Compressor Stage Status | 1675 | 85 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  | SE RTU DX Cooling Circuit 1 Status | 1741 | [5 empty] | SE RTU DX Cooling Circuit 1 Status | 1741 | [5 empty] | 0 = Off-Idle 1 = On-Minimum On Time 2 = On-Normal Command 3 = Off-Cooling Is Disabled ... | 9
Value |  |  | Views.Details.Cooling.Service.Stage 3 | Compressor Stage Command 3 | 1714 | 147 |  | Views.Details.Clg.Service.Stage 3 | C3 | 1709 | 129 |  |  | Compressor Stage Command | 1675 | 84 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 9
Value |  |  | Views.Details.Cooling.Service.Stage 3 | Min On Time Remaining 3 | 1714 | 73 |  | Views.Details.Clg.Service.Stage 3 | C3OnTmr | 1709 | 150 |  |  | Min On Time Remaining | 1675 | 92 | 7007 | TRUE | FALSE | FALSE | 17 | SignedInteger | 1s | seconds | 507:73 |  |  |  |  | 1s | seconds | 507:73 | [6 empty] | 9
Value |  |  | Views.Details.Cooling.Service.Stage 3 | Anti-Short Cycle Delay Time Remaining 3 | 1714 | 74 |  | Views.Details.Clg.Service.Stage 3 | C3ASCDTmr | 1709 | 154 |  |  | Anti-Short Cycle Delay Time Remaining | 1675 | 145 | 7008 | TRUE | FALSE | FALSE | 17 | SignedInteger | 1s | seconds | 507:73 |  |  |  |  | 1s | seconds | 507:73 | [6 empty] | 9
Value |  |  | Views.Details.Cooling.Service.Stage 3 | Compressor Stage Accumulated Runtime 3 | 1714 | 75 |  | Views.Details.Clg.Service.Stage 3 | C3RunTim | 1709 | 142 |  |  | Compressor Stage Accumulated Runtime | 1675 | 90 | 7005 | TRUE | TRUE | FALSE | 4 | Float | 1s | hours | 507:71 | 0 | 10000 |  |  | 1s | hours | 507:71 | 0 | 10000 |  |  |  |  | 9
Value |  |  | Views.Details.Cooling.Service.Stage 3 | Efficiency Index 3 | 1714 | 84 |  | Views.Details.Clg.Service.Stage 3 | C3-EI | 1709 | 218 |  |  | Efficiency Index | 1675 | 201 | 7008 | TRUE | FALSE | FALSE | 4 | Float | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 | [6 empty] | 10
Value |  |  | Views.Details.Cooling.Service.Stage 3 | Capacity Index 3 | 1714 | 85 |  | Views.Details.Clg.Service.Stage 3 | C3-CI | 1709 | 222 |  |  | Capacity Index | 1675 | 202 | 7009 | TRUE | FALSE | FALSE | 4 | Float | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 | [6 empty] | 10
Value |  |  | Views.Details.Cooling.Service.Stage 3 | Condensing Temperature over Ambient 3 | 1714 | 86 |  | Views.Details.Clg.Service.Stage 3 | C3-CondTempOvrAmb | 1709 | 214 |  |  | Condensing Temperature over Ambient | 1675 | 200 | 7007 | TRUE | FALSE | FALSE | 4 | Float | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 | [6 empty] | 10
Value |  |  | Views.Details.Cooling.Service.Stage 3 | Evaporating Temperature Value Circuit 3 | 1714 | 166 |  | Views.Details.Clg.Service.Stage 3 | C3-EvapTempValue | 1709 | 536 |  |  | Evaporating Temp Value | 1675 | 424 | 7014 | TRUE | FALSE | FALSE | 4 | Float | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 | [6 empty] | 10
Value |  |  | Views.Details.Cooling.Service.Stage 3 | Cooling Circuit Test Status | 1675 | 193 |  | Views.Details.Clg.Service.Stage 3 | ClgCktTestS-3 | 1709 | 480 |  |  | Cooling Circuit Test Status | 1675 | 193 | 7000 | TRUE | FALSE | FALSE | 9 | MultiState |  | SE FDD Codes | 1694 | [5 empty] | SE FDD Codes | 1694 | [5 empty] | 0 = Unknown Status 1 = Basic Data Not Available Manual Entry 2 = Basic Data Not Available 3 = Return Wet Bulb Temp Not Available ... | 10
Value |  |  | Views.Details.Cooling.Service.Stage 3 | Superheat | 1675 | 198 |  | Views.Details.Clg.Service.Stage 3 | C3-SuperHeat | 1709 | 206 |  |  | Superheat | 1675 | 198 | 7005 | TRUE | FALSE | FALSE | 4 | Float | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 | [6 empty] | 10
Value |  |  | Views.Details.Cooling.Service.Stage 3 | Subcooling | 1675 | 199 |  | Views.Details.Clg.Service.Stage 3 | C3-SubCool | 1709 | 210 |  |  | Subcooling | 1675 | 199 | 7006 | TRUE | FALSE | FALSE | 4 | Float | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 | [6 empty] | 10
Group |  | TRUE | Views.Details.Cooling.Service.Stage 4 | Stage 4 | 1714 | 34 |  | Views.Details.Clg.Service.Stage 4 | Stage 4 | 1709 | 413 | York RTU.Cooling Control.Cooling Stages Available:Present Value > 3
Value |  |  | Views.Details.Cooling.Service.Stage 4 | Compressor Stage 4 Status | 1714 | 87 |  | Views.Details.Clg.Service.Stage 4 | C4-S | 1709 | 134 |  |  | Compressor Stage Status | 1675 | 85 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  | SE RTU DX Cooling Circuit 1 Status | 1741 | [5 empty] | SE RTU DX Cooling Circuit 1 Status | 1741 | [5 empty] | 0 = Off-Idle 1 = On-Minimum On Time 2 = On-Normal Command 3 = Off-Cooling Is Disabled ... | 11
Value |  |  | Views.Details.Cooling.Service.Stage 4 | Compressor Stage Command 4 | 1714 | 148 |  | Views.Details.Clg.Service.Stage 4 | C4 | 1709 | 130 |  |  | Compressor Stage Command | 1675 | 84 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 11
Value |  |  | Views.Details.Cooling.Service.Stage 4 | Min On Time Remaining 4 | 1714 | 89 |  | Views.Details.Clg.Service.Stage 4 | C4OnTmr | 1709 | 151 |  |  | Min On Time Remaining | 1675 | 92 | 7007 | TRUE | FALSE | FALSE | 17 | SignedInteger | 1s | seconds | 507:73 |  |  |  |  | 1s | seconds | 507:73 | [6 empty] | 11
Value |  |  | Views.Details.Cooling.Service.Stage 4 | Anti-Short Cycle Delay Time Remaining 4 | 1714 | 90 |  | Views.Details.Clg.Service.Stage 4 | C4ASCDTmr | 1709 | 155 |  |  | Anti-Short Cycle Delay Time Remaining | 1675 | 145 | 7008 | TRUE | FALSE | FALSE | 17 | SignedInteger | 1s | seconds | 507:73 |  |  |  |  | 1s | seconds | 507:73 | [6 empty] | 11
Value |  |  | Views.Details.Cooling.Service.Stage 4 | Compressor Stage Accumulated Runtime 4 | 1714 | 91 |  | Views.Details.Clg.Service.Stage 4 | C4RunTim | 1709 | 143 |  |  | Compressor Stage Accumulated Runtime | 1675 | 90 | 7005 | TRUE | TRUE | FALSE | 4 | Float | 1s | hours | 507:71 | 0 | 10000 |  |  | 1s | hours | 507:71 | 0 | 10000 |  |  |  |  | 11
Value |  |  | Views.Details.Cooling.Service.Stage 4 | Efficiency Index 4 | 1714 | 100 |  | Views.Details.Clg.Service.Stage 4 | C4-EI | 1709 | 219 |  |  | Efficiency Index | 1675 | 201 | 7008 | TRUE | FALSE | FALSE | 4 | Float | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 | [6 empty] | 12
Value |  |  | Views.Details.Cooling.Service.Stage 4 | Capacity Index 4 | 1714 | 101 |  | Views.Details.Clg.Service.Stage 4 | C4-CI | 1709 | 223 |  |  | Capacity Index | 1675 | 202 | 7009 | TRUE | FALSE | FALSE | 4 | Float | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 | [6 empty] | 12
Value |  |  | Views.Details.Cooling.Service.Stage 4 | Condensing Temperature over Ambient 4 | 1714 | 102 |  | Views.Details.Clg.Service.Stage 4 | C4-CondTempOvrAmb | 1709 | 215 |  |  | Condensing Temperature over Ambient | 1675 | 200 | 7007 | TRUE | FALSE | FALSE | 4 | Float | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 | [6 empty] | 12
Value |  |  | Views.Details.Cooling.Service.Stage 4 | Evaporating Temperature Value Circuit 4 | 1714 | 167 |  | Views.Details.Clg.Service.Stage 4 | C4-EvapTempValue | 1709 | 537 |  |  | Evaporating Temp Value | 1675 | 424 | 7014 | TRUE | FALSE | FALSE | 4 | Float | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 | [6 empty] | 12
Value |  |  | Views.Details.Cooling.Service.Stage 4 | Cooling Circuit Test Status | 1675 | 193 |  | Views.Details.Clg.Service.Stage 4 | ClgCktTestS-4 | 1709 | 481 |  |  | Cooling Circuit Test Status | 1675 | 193 | 7000 | TRUE | FALSE | FALSE | 9 | MultiState |  | SE FDD Codes | 1694 | [5 empty] | SE FDD Codes | 1694 | [5 empty] | 0 = Unknown Status 1 = Basic Data Not Available Manual Entry 2 = Basic Data Not Available 3 = Return Wet Bulb Temp Not Available ... | 12
Value |  |  | Views.Details.Cooling.Service.Stage 4 | Superheat | 1675 | 198 |  | Views.Details.Clg.Service.Stage 4 | C4-SuperHeat | 1709 | 207 |  |  | Superheat | 1675 | 198 | 7005 | TRUE | FALSE | FALSE | 4 | Float | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 | [6 empty] | 12
Value |  |  | Views.Details.Cooling.Service.Stage 4 | Subcooling | 1675 | 199 |  | Views.Details.Clg.Service.Stage 4 | C4-SubCool | 1709 | 211 |  |  | Subcooling | 1675 | 199 | 7006 | TRUE | FALSE | FALSE | 4 | Float | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 | [6 empty] | 12
Group |  | FALSE | Views.Details.Cooling.Sensors | Sensors | 1714 | 26 |  | Views.Details.Clg.Sensors | Sensors | 1709 | 405
Value |  |  | Views.Details.Cooling.Sensors | Evaporator Coil Temp 1 | 1714 | 44 |  | Views.Details.Clg.Sensors | EC1 | 1709 | 180 |  |  | Evaporator Coil Temp | 1675 | 100 | 7015 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 5
Value |  |  | Views.Details.Cooling.Sensors | Condenser Coil Temp 1 | 1714 | 45 |  | Views.Details.Clg.Sensors | CC1 | 1709 | 184 |  |  | Condenser Coil Temp | 1675 | 102 | 7016 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 5
Value |  |  | Views.Details.Cooling.Sensors | Discharge Line Pressure 1 | 2644 | 378 |  | Views.Details.Clg.Sensors | DLP1 | 2645 | 386 |  |  | Discharge Line Pressure | 2644 | 482 | 7024 | TRUE | FALSE | FALSE | 4 | Float | 10ths | psi | 507:56 | 0 | 750 |  |  | 1s | kPa | 507:54 | 0 | 5172 |  |  |  |  | 6
Value |  |  | Views.Details.Cooling.Sensors | Suction Pressure 1 | 1714 | 46 |  | Views.Details.Clg.Sensors | SLP-1 | 1709 | 188 |  |  | Suction Pressure | 1675 | 194 | 7001 | TRUE | FALSE | FALSE | 4 | Float | 10ths | psi | 507:56 |  |  |  |  | 1s | kPa | 507:54 | [6 empty] | 6
Value |  |  | Views.Details.Cooling.Sensors | Liquid Pressure 1 | 1714 | 47 |  | Views.Details.Clg.Sensors | LLP-1 | 1709 | 192 |  |  | Liquid Pressure | 1675 | 195 | 7002 | TRUE | FALSE | FALSE | 4 | Float | 10ths | psi | 507:56 |  |  |  |  | 1s | kPa | 507:54 | [6 empty] | 6
Value |  |  | Views.Details.Cooling.Sensors | Discharge Line Temperature 1 | 2644 | 380 |  | Views.Details.Clg.Sensors | DLT1 | 2645 | 388 |  |  | Discharge Line Temperature | 2644 | 483 | 7025 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 | -50 | 250 |  |  | 10ths | deg C | 507:62 | -45.6 | 121.1 |  |  |  |  | 6
Value |  |  | Views.Details.Cooling.Sensors | Suction Temperature 1 | 1714 | 48 |  | Views.Details.Clg.Sensors | SLT-1 | 1709 | 196 |  |  | Suction Temperature | 1675 | 196 | 7003 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 6
Value |  |  | Views.Details.Cooling.Sensors | Liquid Temperature 1 | 1714 | 49 |  | Views.Details.Clg.Sensors | LLT-1 | 1709 | 200 |  |  | Liquid Temperature | 1675 | 197 | 7004 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 6
Value |  |  | Views.Details.Cooling.Sensors | Evaporator Coil Temp 2 | 1714 | 60 |  | Views.Details.Clg.Sensors | EC2 | 1709 | 181 |  |  | Evaporator Coil Temp | 1675 | 100 | 7015 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 7
Value |  |  | Views.Details.Cooling.Sensors | Condenser Coil Temp 2 | 1714 | 61 |  | Views.Details.Clg.Sensors | CC2 | 1709 | 185 |  |  | Condenser Coil Temp | 1675 | 102 | 7016 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 7
Value |  |  | Views.Details.Cooling.Sensors | Discharge Line Pressure 2 | 2644 | 379 |  | Views.Details.Clg.Sensors | DLP2 | 2645 | 387 |  |  | Discharge Line Pressure | 2644 | 482 | 7024 | TRUE | FALSE | FALSE | 4 | Float | 10ths | psi | 507:56 | 0 | 750 |  |  | 1s | kPa | 507:54 | 0 | 5172 |  |  |  |  | 8
Value |  |  | Views.Details.Cooling.Sensors | Suction Pressure 2 | 1714 | 62 |  | Views.Details.Clg.Sensors | SLP-2 | 1709 | 189 |  |  | Suction Pressure | 1675 | 194 | 7001 | TRUE | FALSE | FALSE | 4 | Float | 10ths | psi | 507:56 |  |  |  |  | 1s | kPa | 507:54 | [6 empty] | 8
Value |  |  | Views.Details.Cooling.Sensors | Liquid Pressure 2 | 1714 | 63 |  | Views.Details.Clg.Sensors | LLP-2 | 1709 | 193 |  |  | Liquid Pressure | 1675 | 195 | 7002 | TRUE | FALSE | FALSE | 4 | Float | 10ths | psi | 507:56 |  |  |  |  | 1s | kPa | 507:54 | [6 empty] | 8
Value |  |  | Views.Details.Cooling.Sensors | Discharge Line Temperature 2 | 2644 | 381 |  | Views.Details.Clg.Sensors | DLT2 | 2645 | 389 |  |  | Discharge Line Temperature | 2644 | 483 | 7025 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 | -50 | 250 |  |  | 10ths | deg C | 507:62 | -45.6 | 121.1 |  |  |  |  | 8
Value |  |  | Views.Details.Cooling.Sensors | Suction Temperature 2 | 1714 | 64 |  | Views.Details.Clg.Sensors | SLT-2 | 1709 | 197 |  |  | Suction Temperature | 1675 | 196 | 7003 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 8
Value |  |  | Views.Details.Cooling.Sensors | Liquid Temperature 2 | 1714 | 65 |  | Views.Details.Clg.Sensors | LLT-2 | 1709 | 201 |  |  | Liquid Temperature | 1675 | 197 | 7004 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 8
Value |  |  | Views.Details.Cooling.Sensors | Evaporator Coil Temp 3 | 1714 | 76 |  | Views.Details.Clg.Sensors | EC3 | 1709 | 182 |  |  | Evaporator Coil Temp | 1675 | 100 | 7015 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 9
Value |  |  | Views.Details.Cooling.Sensors | Condenser Coil Temp 3 | 1714 | 77 |  | Views.Details.Clg.Sensors | CC3 | 1709 | 186 |  |  | Condenser Coil Temp | 1675 | 102 | 7016 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 9
Value |  |  | Views.Details.Cooling.Sensors | Suction Pressure 3 | 1714 | 78 |  | Views.Details.Clg.Sensors | SLP-3 | 1709 | 190 |  |  | Suction Pressure | 1675 | 194 | 7001 | TRUE | FALSE | FALSE | 4 | Float | 10ths | psi | 507:56 |  |  |  |  | 1s | kPa | 507:54 | [6 empty] | 10
Value |  |  | Views.Details.Cooling.Sensors | Liquid Pressure 3 | 1714 | 79 |  | Views.Details.Clg.Sensors | LLP-3 | 1709 | 194 |  |  | Liquid Pressure | 1675 | 195 | 7002 | TRUE | FALSE | FALSE | 4 | Float | 10ths | psi | 507:56 |  |  |  |  | 1s | kPa | 507:54 | [6 empty] | 10
Value |  |  | Views.Details.Cooling.Sensors | Suction Temperature 3 | 1714 | 80 |  | Views.Details.Clg.Sensors | SLT-3 | 1709 | 198 |  |  | Suction Temperature | 1675 | 196 | 7003 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 10
Value |  |  | Views.Details.Cooling.Sensors | Liquid Temperature 3 | 1714 | 81 |  | Views.Details.Clg.Sensors | LLT-3 | 1709 | 202 |  |  | Liquid Temperature | 1675 | 197 | 7004 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 10
Value |  |  | Views.Details.Cooling.Sensors | Evaporator Coil Temp 4 | 1714 | 92 |  | Views.Details.Clg.Sensors | EC4 | 1709 | 183 |  |  | Evaporator Coil Temp | 1675 | 100 | 7015 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 11
Value |  |  | Views.Details.Cooling.Sensors | Condenser Coil Temp 4 | 1714 | 93 |  | Views.Details.Clg.Sensors | CC4 | 1709 | 187 |  |  | Condenser Coil Temp | 1675 | 102 | 7016 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 11
Value |  |  | Views.Details.Cooling.Sensors | Suction Pressure 4 | 1714 | 94 |  | Views.Details.Clg.Sensors | SLP-4 | 1709 | 191 |  |  | Suction Pressure | 1675 | 194 | 7001 | TRUE | FALSE | FALSE | 4 | Float | 10ths | psi | 507:56 |  |  |  |  | 1s | kPa | 507:54 | [6 empty] | 12
Value |  |  | Views.Details.Cooling.Sensors | Liquid Pressure 4 | 1714 | 95 |  | Views.Details.Clg.Sensors | LLP-4 | 1709 | 195 |  |  | Liquid Pressure | 1675 | 195 | 7002 | TRUE | FALSE | FALSE | 4 | Float | 10ths | psi | 507:56 |  |  |  |  | 1s | kPa | 507:54 | [6 empty] | 12
Value |  |  | Views.Details.Cooling.Sensors | Suction Temperature 4 | 1714 | 96 |  | Views.Details.Clg.Sensors | SLT-4 | 1709 | 199 |  |  | Suction Temperature | 1675 | 196 | 7003 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 12
Value |  |  | Views.Details.Cooling.Sensors | Liquid Temperature 4 | 1714 | 97 |  | Views.Details.Clg.Sensors | LLT-4 | 1709 | 203 |  |  | Liquid Temperature | 1675 | 197 | 7004 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 12
Group |  | FALSE | Views.Details.Cooling.Safeties | Safeties | 1714 | 25 |  | Views.Details.Clg.Safeties | Safeties | 1709 | 404
Value |  |  | Views.Details.Cooling.Safeties | High Pressure Limit 1 | 1714 | 121 |  | Views.Details.Clg.Safeties | HPS1 | 1709 | 156 |  |  | High Pressure Limit | 1675 | 93 | 7009 | TRUE | FALSE | FALSE | 9 | MultiState |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 | [5 empty] | 0 = Normal 1 = Alarm | 5
Value |  |  | Views.Details.Cooling.Safeties | High Pressure Lockout 1 | 1714 | 129 |  | Views.Details.Clg.Safeties | HPS1-LO | 1709 | 160 |  |  | High Pressure Lockout | 1675 | 94 | 7010 | TRUE | FALSE | FALSE | 9 | MultiState |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 | [5 empty] | 0 = Normal 1 = Lockout | 5
Value |  |  | Views.Details.Cooling.Safeties | Low Pressure Limit 1 | 1714 | 122 |  | Views.Details.Clg.Safeties | LPS1 | 1709 | 164 |  |  | Low Pressure Limit | 1675 | 95 | 7011 | TRUE | FALSE | FALSE | 9 | MultiState |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 | [5 empty] | 0 = Normal 1 = Alarm | 5
Value |  |  | Views.Details.Cooling.Safeties | Low Pressure Lockout 1 | 1714 | 130 |  | Views.Details.Clg.Safeties | LPS1-LO | 1709 | 168 |  |  | Low Pressure Lockout | 1675 | 96 | 7012 | TRUE | FALSE | FALSE | 9 | MultiState |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 | [5 empty] | 0 = Normal 1 = Lockout | 5
Value |  |  | Views.Details.Cooling.Safeties | Freeze Condition 1 | 1714 | 131 |  | Views.Details.Clg.Safeties | FS1 | 1709 | 172 |  |  | Freeze Condition | 1675 | 97 | 7013 | TRUE | FALSE | FALSE | 9 | MultiState |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 | [5 empty] | 0 = Normal 1 = Alarm | 5
Value |  |  | Views.Details.Cooling.Safeties | Freeze Condition Lockout 1 | 1714 | 132 |  | Views.Details.Clg.Safeties | FS1-LO | 1709 | 176 |  |  | Freeze Condition Lockout | 1675 | 98 | 7014 | TRUE | FALSE | FALSE | 9 | MultiState |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 | [5 empty] | 0 = Normal 1 = Lockout | 5
Value |  |  | Views.Details.Cooling.Safeties | High Pressure Limit 2 | 1714 | 123 |  | Views.Details.Clg.Safeties | HPS2 | 1709 | 157 |  |  | High Pressure Limit | 1675 | 93 | 7009 | TRUE | FALSE | FALSE | 9 | MultiState |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 | [5 empty] | 0 = Normal 1 = Alarm | 7
Value |  |  | Views.Details.Cooling.Safeties | High Pressure Lockout 2 | 1714 | 133 |  | Views.Details.Clg.Safeties | HPS2-LO | 1709 | 161 |  |  | High Pressure Lockout | 1675 | 94 | 7010 | TRUE | FALSE | FALSE | 9 | MultiState |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 | [5 empty] | 0 = Normal 1 = Lockout | 7
Value |  |  | Views.Details.Cooling.Safeties | Low Pressure Limit 2 | 1714 | 124 |  | Views.Details.Clg.Safeties | LPS2 | 1709 | 165 |  |  | Low Pressure Limit | 1675 | 95 | 7011 | TRUE | FALSE | FALSE | 9 | MultiState |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 | [5 empty] | 0 = Normal 1 = Alarm | 7
Value |  |  | Views.Details.Cooling.Safeties | Low Pressure Lockout 2 | 1714 | 134 |  | Views.Details.Clg.Safeties | LPS2-LO | 1709 | 169 |  |  | Low Pressure Lockout | 1675 | 96 | 7012 | TRUE | FALSE | FALSE | 9 | MultiState |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 | [5 empty] | 0 = Normal 1 = Lockout | 7
Value |  |  | Views.Details.Cooling.Safeties | Freeze Condition 2 | 1714 | 135 |  | Views.Details.Clg.Safeties | FS2 | 1709 | 173 |  |  | Freeze Condition | 1675 | 97 | 7013 | TRUE | FALSE | FALSE | 9 | MultiState |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 | [5 empty] | 0 = Normal 1 = Alarm | 7
Value |  |  | Views.Details.Cooling.Safeties | Freeze Condition Lockout 2 | 1714 | 136 |  | Views.Details.Clg.Safeties | FS2-LO | 1709 | 177 |  |  | Freeze Condition Lockout | 1675 | 98 | 7014 | TRUE | FALSE | FALSE | 9 | MultiState |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 | [5 empty] | 0 = Normal 1 = Lockout | 7
Value |  |  | Views.Details.Cooling.Safeties | High Pressure Limit 3 | 1714 | 125 |  | Views.Details.Clg.Safeties | HPS3 | 1709 | 158 |  |  | High Pressure Limit | 1675 | 93 | 7009 | TRUE | FALSE | FALSE | 9 | MultiState |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 | [5 empty] | 0 = Normal 1 = Alarm | 9
Value |  |  | Views.Details.Cooling.Safeties | High Pressure Lockout 3 | 1714 | 137 |  | Views.Details.Clg.Safeties | HPS3-LO | 1709 | 162 |  |  | High Pressure Lockout | 1675 | 94 | 7010 | TRUE | FALSE | FALSE | 9 | MultiState |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 | [5 empty] | 0 = Normal 1 = Lockout | 9
Value |  |  | Views.Details.Cooling.Safeties | Low Pressure Limit 3 | 1714 | 126 |  | Views.Details.Clg.Safeties | LPS3 | 1709 | 166 |  |  | Low Pressure Limit | 1675 | 95 | 7011 | TRUE | FALSE | FALSE | 9 | MultiState |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 | [5 empty] | 0 = Normal 1 = Alarm | 9
Value |  |  | Views.Details.Cooling.Safeties | Low Pressure Lockout 3 | 1714 | 138 |  | Views.Details.Clg.Safeties | LPS3-LO | 1709 | 170 |  |  | Low Pressure Lockout | 1675 | 96 | 7012 | TRUE | FALSE | FALSE | 9 | MultiState |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 | [5 empty] | 0 = Normal 1 = Lockout | 9
Value |  |  | Views.Details.Cooling.Safeties | Freeze Condition 3 | 1714 | 139 |  | Views.Details.Clg.Safeties | FS3 | 1709 | 174 |  |  | Freeze Condition | 1675 | 97 | 7013 | TRUE | FALSE | FALSE | 9 | MultiState |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 | [5 empty] | 0 = Normal 1 = Alarm | 9
Value |  |  | Views.Details.Cooling.Safeties | Freeze Condition Lockout 3 | 1714 | 140 |  | Views.Details.Clg.Safeties | FS3-LO | 1709 | 178 |  |  | Freeze Condition Lockout | 1675 | 98 | 7014 | TRUE | FALSE | FALSE | 9 | MultiState |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 | [5 empty] | 0 = Normal 1 = Lockout | 9
Value |  |  | Views.Details.Cooling.Safeties | High Pressure Limit 4 | 1714 | 127 |  | Views.Details.Clg.Safeties | HPS4 | 1709 | 159 |  |  | High Pressure Limit | 1675 | 93 | 7009 | TRUE | FALSE | FALSE | 9 | MultiState |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 | [5 empty] | 0 = Normal 1 = Alarm | 11
Value |  |  | Views.Details.Cooling.Safeties | High Pressure Lockout 4 | 1714 | 141 |  | Views.Details.Clg.Safeties | HPS4-LO | 1709 | 163 |  |  | High Pressure Lockout | 1675 | 94 | 7010 | TRUE | FALSE | FALSE | 9 | MultiState |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 | [5 empty] | 0 = Normal 1 = Lockout | 11
Value |  |  | Views.Details.Cooling.Safeties | Low Pressure Limit 4 | 1714 | 128 |  | Views.Details.Clg.Safeties | LPS4 | 1709 | 167 |  |  | Low Pressure Limit | 1675 | 95 | 7011 | TRUE | FALSE | FALSE | 9 | MultiState |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 | [5 empty] | 0 = Normal 1 = Alarm | 11
Value |  |  | Views.Details.Cooling.Safeties | Low Pressure Lockout 4 | 1714 | 142 |  | Views.Details.Clg.Safeties | LPS4-LO | 1709 | 171 |  |  | Low Pressure Lockout | 1675 | 96 | 7012 | TRUE | FALSE | FALSE | 9 | MultiState |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 | [5 empty] | 0 = Normal 1 = Lockout | 11
Value |  |  | Views.Details.Cooling.Safeties | Freeze Condition 4 | 1714 | 143 |  | Views.Details.Clg.Safeties | FS4 | 1709 | 175 |  |  | Freeze Condition | 1675 | 97 | 7013 | TRUE | FALSE | FALSE | 9 | MultiState |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 | [5 empty] | 0 = Normal 1 = Alarm | 11
Value |  |  | Views.Details.Cooling.Safeties | Freeze Condition Lockout 4 | 1714 | 144 |  | Views.Details.Clg.Safeties | FS4-LO | 1709 | 179 |  |  | Freeze Condition Lockout | 1675 | 98 | 7014 | TRUE | FALSE | FALSE | 9 | MultiState |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 | [5 empty] | 0 = Normal 1 = Lockout | 11
Value |  |  | Views.Details.Cooling.Safeties | A2L Leak Detector Alarm | 1714 | 276 |  | Views.Details.Clg.Safeties | A2LLeakAlarm | 1709 | 787 |  |  | A2L Leak Detector Alarm | 1714 | 276 | 7103 | TRUE | FALSE | FALSE | 9 | MultiState |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 | [5 empty] | 0 = Normal 1 = Alarm | 4
Value |  |  | Views.Details.Cooling.Safeties | A2L Leak Detector Alarm-Lockout | 1714 | 280 |  | Views.Details.Clg.Safeties | A2LLeakAlarm-LO | 1709 | 791 |  |  | A2L Leak Detector Alarm-Lockout | 1714 | 280 | 7106 | TRUE | FALSE | FALSE | 9 | MultiState |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 | [5 empty] | 0 = Normal 1 = Lockout | 4
Value |  |  | Views.Details.Cooling.Safeties | Condensate Alarm Enable | 2644 | 383 |  | Views.Details.Clg.Safeties | COS-En | 1709 | 797 |  |  | Condensate Alarm Enable | 2644 | 383 | 7107 | TRUE | TRUE | FALSE | 9 | MultiState |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 | [5 empty] | 0 = Disable 1 = Enable | 4
Value |  |  | Views.Details.Cooling.Safeties | Condensate Overflow Switch | 1714 | 277 |  | Views.Details.Clg.Safeties | COS | 1709 | 788 |  |  | Condensate Overflow Switch | 1714 | 277 | 7108 | TRUE | FALSE | FALSE | 9 | MultiState |  | Alarm/Normal | 1696 | [5 empty] | Alarm/Normal | 1696 | [5 empty] | 0 = Alarm 1 = Normal | 4
Group |  | FALSE | Views.Details.Cooling.Misc | Misc | 1714 | 18 |  | Views.Details.Clg.Misc | Misc | 1709 | 397
Value |  |  | Views.Details.Cooling.Misc | Maximum Temperature / Humidity Setpoint Offset | 1675 | 81 |  | Views.Details.Clg.Misc | MaxTempHumSpOff | 1709 | 104 |  |  | Maximum Temperature / Humidity Setpoint Offset | 1675 | 81 | 7013 | TRUE | TRUE | FALSE | 4 | Float | 10ths | delta deg F | 507:120 | 0 | 5 |  |  | 10ths | delta deg C | 507:359 | 0 | 3 |  |  |  |  | 4
Value |  |  | Views.Details.Cooling.Misc | Temperature/Humidity Setpoint | 1675 | 80 |  | Views.Details.Clg.Misc | TempHum-Sp | 1709 | 103 |  |  | Temperature/Humidity Setpoint | 1675 | 80 | 7012 | TRUE | TRUE | FALSE | 4 | Float | 1s | %RH | 507:29 | 20 | 80 |  |  | 1s | %RH | 507:29 | 20 | 80 |  |  |  |  | 4
Value |  |  | Views.Details.Cooling.Misc | Temperature/Humidity (Return) Control Enable | 1675 | 79 |  | Views.Details.Clg.Misc | TempHumCtrl-En | 1709 | 102 |  |  | Temperature/Humidity (Return) Control Enable | 1675 | 79 | 7011 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 4
Value |  |  | Views.Details.Cooling.Misc | Operational Space Humidity | 1675 | 23 |  | Views.Details.Clg.Misc | OprSH | 1709 | 39 |  |  | Operational Space Humidity | 1675 | 23 | 7017 | TRUE | FALSE | FALSE | 4 | Float | 10ths | %RH | 507:29 |  |  |  |  | 10ths | %RH | 507:29 | [6 empty] | 25
Value |  |  | Views.Details.Cooling.Misc | CV Occupied Cooling Setpoint | 1675 | 141 |  | Views.Details.Clg.Misc | ClgOcc-Sp | 1709 | 123 |  |  | CV Occupied Cooling Setpoint | 1675 | 141 | 7033 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 45 | 98 |  |  | 1s | deg C | 507:62 | 7 | 36 |  |  |  |  | 4
Value |  |  | Views.Details.Cooling.Misc | CV Operating Cooling Setpoint | 1675 | 144 |  | Views.Details.Clg.Misc | OprCVClg-Sp | 1709 | 125 |  |  | CV Operating Cooling Setpoint | 1675 | 144 | 7035 | TRUE | FALSE | FALSE | 4 | Float | 100ths | deg F | 507:64 |  |  |  |  | 100ths | deg C | 507:62 | [6 empty] | 4
Value |  |  | Views.Details.Cooling.Misc | SZ VAV Occupied Cooling Setpoint | 1675 | 644 |  | Views.Details.Clg.Misc | SZVAVClgOcc-Sp | 1709 | 656 |  |  | SZ VAV Occupied Cooling Setpoint | 1675 | 644 | 7048 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 45 | 98 |  |  | 1s | deg C | 507:62 | 7 | 36 |  |  |  |  | 4
Value |  |  | Views.Details.Cooling.Misc | VAV Operating Cooling Supply Air Temp Setpoint | 1675 | 140 |  | Views.Details.Clg.Misc | OprSZVAVClg-Sp | 1709 | 660 |  |  | SZ VAV Operating Cooling Setpoint | 1675 | 648 | 7050 | TRUE | FALSE | FALSE | 4 | Float | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 | [6 empty] | 4
Value |  |  | Views.Details.Cooling.Misc | Common Setpoint | 2596 | 0 |  | Views.Details.Clg.Misc | Common-SP | 1709 | 702 |  |  | Common Setpoint | 2596 | 0 | 7074 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 45 | 98 |  |  | 1s | deg C | 507:62 | 8 | 36 |  |  |  |  | 25
Value |  |  | Views.Details.Cooling.Misc | Auto Changeover | 1675 | 1469 |  | Views.Details.Clg.Misc | Auto Changeover | 1675 | 1469 |  |  | Auto Changeover | 1675 | 1469 | 7076 | TRUE | TRUE | FALSE | 4 | Float | 10ths | delta deg F | 507:120 | 2 | 5 |  |  | 10ths | delta deg C | 507:359 | 1.1 | 2.8 |  |  |  |  | 25
Value |  |  | Views.Details.Cooling.Misc | Temperature / Humidity Value per Degree Offset | 1675 | 82 |  | Views.Details.Clg.Misc | TempHumValPerDegOff | 1709 | 105 |  |  | Temperature / Humidity Value per Degree Offset | 1675 | 82 | 7014 | TRUE | TRUE | FALSE | 4 | Float | 1s | %RH | 507:29 | 1 | 10 |  |  | 1s | %RH | 507:29 | 1 | 10 |  |  |  |  | 4
Value |  |  | Views.Details.Cooling.Misc | Suction Superheat 1 | 2644 | 366 |  | Views.Details.Clg.Misc | SucSuperheat1 | 2645 | 374 |  |  | Suction Superheat 1 | 2644 | 366 | 7082 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 4
Value |  |  | Views.Details.Cooling.Misc | Saturated Suction Temperature 1 | 2644 | 374 |  | Views.Details.Clg.Misc | SatSucTemp1 | 2645 | 382 |  |  | Saturated Suction Temperature 1 | 2644 | 374 | 7078 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 4
Value |  |  | Views.Details.Cooling.Misc | Saturated Discharge Temperature 1 | 2644 | 370 |  | Views.Details.Clg.Misc | SatDischTemp1 | 2645 | 378 |  |  | Saturated Discharge Temperature 1 | 2644 | 370 | 7079 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 4
Value |  |  | Views.Details.Cooling.Misc | Saturated Suction Temperature 2 | 2644 | 375 |  | Views.Details.Clg.Misc | SatSucTemp2 | 2645 | 383 |  |  | Saturated Suction Temperature 2 | 2644 | 375 | 7081 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 4
Value |  |  | Views.Details.Cooling.Misc | Saturated Discharge Temperature 2 | 2644 | 371 |  | Views.Details.Clg.Misc | SatDischTemp2 | 2645 | 379 |  |  | Saturated Discharge Temperature 2 | 2644 | 371 | 7080 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 4
Value |  |  | Views.Details.Cooling.Misc | Circuit 1 High Pressure Unload Enable | 1714 | 254 |  | Views.Details.Clg.Misc | Cir1HighPresUnloadEn | 1709 | 754 |  |  | Circuit 1 High Pressure Unload Enable | 1714 | 254 | 7089 | TRUE | TRUE | FALSE | 9 | MultiState |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 | [5 empty] | 0 = Disable 1 = Enable | 4
Value |  |  | Views.Details.Cooling.Misc | Circuit 1 Low Pressure Unload Enable | 1714 | 255 |  | Views.Details.Clg.Misc | Cir1LowPresUnloadEn | 1709 | 755 |  |  | Circuit 1 Low Pressure Unload Enable | 1714 | 255 | 7090 | TRUE | TRUE | FALSE | 9 | MultiState |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 | [5 empty] | 0 = Disable 1 = Enable | 4
Value |  |  | Views.Details.Cooling.Misc | Circuit 2 High Pressure Unload Enable | 1714 | 256 |  | Views.Details.Clg.Misc | Cir2HighPresUnloadEn | 1709 | 756 |  |  | Circuit 2 High Pressure Unload Enable | 1714 | 256 | 7091 | TRUE | TRUE | FALSE | 9 | MultiState |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 | [5 empty] | 0 = Disable 1 = Enable | 4
Value |  |  | Views.Details.Cooling.Misc | Circuit 2 Low Pressure Unload Enable | 1714 | 257 |  | Views.Details.Clg.Misc | Cir2LowPresUnloadEn | 1709 | 757 |  |  | Circuit 2 Low Pressure Unload Enable | 1714 | 257 | 7092 | TRUE | TRUE | FALSE | 9 | MultiState |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 | [5 empty] | 0 = Disable 1 = Enable | 4
Group |  | FALSE | Views.Details.Heating | Heating | 1714 | 12 |  | Views.Details.Htg | Htg | 1709 | 392
Group |  | FALSE | Views.Details.Heating.Setup | Setup | 1714 | 29 |  | Views.Details.Htg.Setup | Setup | 1709 | 408
Value |  |  | Views.Details.Heating.Setup | Heating Control Type | 1675 | 107 |  | Views.Details.Htg.Setup | Htg-Type | 1709 | 6 |  |  | Heating Control Type | 1675 | 107 | 7006 | TRUE | TRUE | FALSE | 9 | MultiState |  | Heat Cool Type | 1608 | [5 empty] | Heat Cool Type | 1608 | [5 empty] | 0 = Staged 1 = Proportional | 1
Value |  |  | Views.Details.Heating.Setup | CV Occupied Heating Setpoint | 1675 | 212 |  | Views.Details.Htg.Setup | CVHtgOcc-SP | 1709 | 461 |  |  | CV Occupied Heating Setpoint | 1675 | 212 | 7023 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 46 | 99 |  |  | 1s | deg C | 507:62 | 8 | 37 |  |  |  |  | 13
Value |  |  | Views.Details.Heating.Setup | CV Unoccupied Heating Setpoint | 1675 | 213 |  | Views.Details.Htg.Setup | CVHtgUnocc-Sp | 1709 | 462 |  |  | CV Unoccupied Heating Setpoint | 1675 | 213 | 7024 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 45 | 98 |  |  | 1s | deg C | 507:62 | 7 | 36 |  |  |  |  | 13
Value |  |  | Views.Details.Heating.Setup | VAV Occupied Heating Setpoint | 1675 | 205 |  | Views.Details.Htg.Setup | VAVHtgOcc-SP | 1709 | 240 |  |  | VAV Occupied Heating Setpoint | 1675 | 205 | 7016 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 40 | 85 |  |  | 1s | deg C | 507:62 | 4 | 30 |  |  |  |  | 13
Value |  |  | Views.Details.Heating.Setup | VAV Unoccupied Heating Setpoint | 1675 | 207 |  | Views.Details.Htg.Setup | VAVHtgUnocc-Sp | 1709 | 242 |  |  | VAV Unoccupied Heating Setpoint | 1675 | 207 | 7018 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 45 | 98 |  |  | 1s | deg C | 507:62 | 7 | 36 |  |  |  |  | 13
Value |  |  | Views.Details.Heating.Setup | SZ VAV Occupied Heating Setpoint | 1675 | 643 |  | Views.Details.Htg.Setup | SZVAVHtgOcc-Sp | 1709 | 658 |  |  | SZ VAV Occupied Heating Setpoint | 1675 | 643 | 7047 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 46 | 99 |  |  | 1s | deg C | 507:62 | 8 | 37 |  |  |  |  | 13
Value |  |  | Views.Details.Heating.Setup | SZ VAV Unoccupied Heating Setpoint | 1675 | 645 |  | Views.Details.Htg.Setup | SZVAVHtgUnocc-Sp | 1709 | 659 |  |  | SZ VAV Unoccupied Heating Setpoint | 1675 | 645 | 7048 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 45 | 98 |  |  | 1s | deg C | 507:62 | 7 | 36 |  |  |  |  | 13
Value |  |  | Views.Details.Heating.Setup | Common Setpoint | 2596 | 0 |  | Views.Details.Htg.Setup | Common-SP | 1709 | 702 |  |  | Common Setpoint | 2596 | 0 | 7074 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 45 | 98 |  |  | 1s | deg C | 507:62 | 8 | 36 |  |  |  |  | 25
Value |  |  | Views.Details.Heating.Setup | Auto Changeover | 1675 | 1469 |  | Views.Details.Htg.Setup | Auto Changeover | 1675 | 1469 |  |  | Auto Changeover | 1675 | 1469 | 7076 | TRUE | TRUE | FALSE | 4 | Float | 10ths | delta deg F | 507:120 | 2 | 5 |  |  | 10ths | delta deg C | 507:359 | 1.1 | 2.8 |  |  |  |  | 25
Value |  |  | Views.Details.Heating.Setup | Heat Cool Setpoint Mode | 1714 | 212 |  | Views.Details.Htg.Setup | Heat Cool Setpoint Mode | 1714 | 212 |  |  | Heat Cool Setpoint Mode | 1714 | 212 | 7075 | TRUE | TRUE | FALSE | 9 | MultiState |  | Heat Cool Setpoint Mode | 2596 | [5 empty] | Heat Cool Setpoint Mode | 2596 | [5 empty] | 0 = Common Setpoint 1 = Individual Setpoints | 25
Value |  |  | Views.Details.Heating.Setup | Heating Adaptive Tuning Enable | 1675 | 485 |  | Views.Details.Htg.Setup | HtgAdapTunEn | 1709 | 616 |  |  | Heating Adaptive Tuning Enable | 1675 | 485 | 7041 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 13
Value |  |  | Views.Details.Heating.Setup | SAT Air Temp Limit for Heating Enabled | 1675 | 108 |  | Views.Details.Htg.Setup | SATHtgLimit-En | 1709 | 226 |  |  | SAT Air Temp Limit for Heating Enabled | 1675 | 108 | 7002 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 13
Value |  |  | Views.Details.Heating.Setup | SAT Air Temp Limit For Heating Setpoint | 1675 | 109 |  | Views.Details.Htg.Setup | SATHtgLimit-Sp | 1709 | 227 |  |  | SAT Air Temp Limit For Heating Setpoint | 1675 | 109 | 7003 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 100 | 180 |  |  | 1s | deg C | 507:62 | 38 | 82 |  |  |  |  | 13
Value |  |  | Views.Details.Heating.Setup | Outdoor Air Temp Heating Cutout Setpoint | 1675 | 110 |  | Views.Details.Htg.Setup | HtgOATCutout-Sp | 1709 | 228 |  |  | Outdoor Air Temp Heating Cutout Setpoint | 1675 | 110 | 7004 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 0 | 100 |  |  | 1s | deg C | 507:62 | -18 | 38 |  |  |  |  | 13
Value |  |  | Views.Details.Heating.Setup | Number of Gas Valves Installed | 1675 | 439 |  | Views.Details.Htg.Setup | #GasVlvs | 1709 | 550 |  |  | Number of Gas Valves Installed | 1675 | 439 | 7039 | TRUE | TRUE | FALSE | 4 | Float | 1s |  | 507:95 | 0 | 3 |  |  | 1s |  | 507:95 | 0 | 3 |  |  |  |  | 13
Value |  |  | Views.Details.Heating.Setup | Number of Limit Switches | 1675 | 490 |  | Views.Details.Htg.Setup | #LimSwtchs | 1709 | 622 |  |  | Number of Limit Switches | 1675 | 490 | 7042 | TRUE | FALSE | FALSE | 4 | Float | 1s |  | 507:95 |  |  |  |  | 1s |  | 507:95 | [6 empty] | 13
Value |  |  | Views.Details.Heating.Setup | Low Limit Enable | 1675 | 1405 |  | Views.Details.Htg.Setup | LL_Enable | 1709 | 692 |  |  | Low Limit Enable | 1675 | 1405 | 7052 | TRUE | TRUE | FALSE | 9 | MultiState |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 | [5 empty] | 0 = Disable 1 = Enable | 13
Value |  |  | Views.Details.Heating.Setup | Low Limit Upper SAT Setpoint | 1675 | 1406 |  | Views.Details.Htg.Setup | LL_UpSAT_SP | 1709 | 693 |  |  | Low Limit Upper SAT Setpoint | 1675 | 1406 | 7053 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 65 | 85 |  |  | 1s | deg C | 507:62 | 18 | 30 |  |  |  |  | 13
Value |  |  | Views.Details.Heating.Setup | Low Limit Lower SAT Setpoint | 1675 | 1407 |  | Views.Details.Htg.Setup | LL_LowSAT_SP | 1709 | 694 |  |  | Low Limit Lower SAT Setpoint | 1675 | 1407 | 7054 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 60 | 80 |  |  | 1s | deg C | 507:62 | 15 | 27 |  |  |  |  | 13
Value |  |  | Views.Details.Heating.Setup | Heating Manual Tuning | 1675 | 479 |  | Views.Details.Htg.Setup | HtgManualTune | 1709 | 691 |  |  | Operational Error Sigma | 1675 | 1076 | 7051 | TRUE | TRUE | FALSE | 4 | Float | 10ths | delta deg F | 507:120 | 1 | 2.5 |  |  | 10ths | delta deg C | 507:359 | 0.6 | 1.5 |  |  |  |  | 13
Value |  |  | Views.Details.Heating.Setup | Cooling Allowed During Heat Limit | 1714 | 230 |  | Views.Details.Htg.Setup | CoolDuringHeatLimit | 1709 | 727 |  |  | Cooling Allowed During Heat Limit | 1714 | 230 | 7060 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 4
Value |  |  | Views.Details.Heating.Setup | Heating Rapid Start Enable | 1714 | 268 |  | Views.Details.Htg.Setup | HtgRapidStartEn | 1709 | 768 |  |  | Heating Rapid Start Enable | 1714 | 268 | 7056 | TRUE | TRUE | FALSE | 9 | MultiState |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 | [5 empty] | 0 = Disable 1 = Enable | 13
Value |  |  | Views.Details.Heating.Setup | Heating Rapid Start Time | 1714 | 270 |  | Views.Details.Htg.Setup | HtgRapidStartTime | 1709 | 770 |  |  | Heating Rapid Start Time | 1714 | 270 | 7057 | TRUE | TRUE | FALSE | 4 | Float | 1s | minutes | 507:72 | 2 | 30 |  |  | 1s | minutes | 507:72 | 2 | 30 |  |  |  |  | 13
Group |  | FALSE | Views.Details.Heating.Service | Service | 1714 | 27 |  | Views.Details.Htg.Service | Service | 1709 | 406
Value |  |  | Views.Details.Heating.Service | Staged Heating Command | 1675 | 629 |  | Views.Details.Htg.Service | StgHtgCmd | 1709 | 649 |  |  | Staged Heating Command | 1675 | 629 | 7045 | TRUE | FALSE | FALSE | 4 | Float | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 | [6 empty] | 13
Value |  |  | Views.Details.Heating.Service | CV Operating Heating Setpoint | 1675 | 214 |  | Views.Details.Htg.Service | CVOprHtg-Sp | 1709 | 463 |  |  | CV Operating Heating Setpoint | 1675 | 214 | 7025 | TRUE | FALSE | FALSE | 4 | Float | 100ths | deg F | 507:64 |  |  |  |  | 100ths | deg C | 507:62 | [6 empty] | 13
Value |  |  | Views.Details.Heating.Service | VAV Operating Heating Setpoint | 1675 | 208 |  | Views.Details.Htg.Service | VAVOprHtg-Sp | 1709 | 243 |  |  | VAV Operating Heating Setpoint | 1675 | 208 | 7019 | TRUE | FALSE | FALSE | 4 | Float | 100ths | deg F | 507:64 |  |  |  |  | 100ths | deg C | 507:62 | [6 empty] | 13
Value |  |  | Views.Details.Heating.Service | Operating Heating Discharge Air Temp Setpoint | 2644 | 40 |  | Views.Details.Htg.Service | OprHtgDAT-SP | 2645 | 359 |  |  | SZ VAV Operating Heating Setpoint | 1675 | 647 | 7049 | TRUE | FALSE | FALSE | 4 | Float | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 | [6 empty] | 13
Value |  |  | Views.Details.Heating.Service | Heating Status | 1675 | 106 |  | Views.Details.Htg.Service | Htg-S | 1709 | 225 |  |  | Heating Status | 1675 | 106 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  | SE RTU Heating Control Status | 1742 | [5 empty] | SE RTU Heating Control Status | 1742 | [5 empty] | 0 = Off-Idle 1 = On-Defrost 2 = SAT Tempering 3 = Morning Warmup ... | 13
Value |  |  | Views.Details.Heating.Service | Operational Outdoor Air Temperature | 1675 | 36 |  | Views.Details.Htg.Service | OprOAT | 1709 | 52 |  |  | Operational Outdoor Air Temperature | 1675 | 36 | 7000 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 26
Value |  |  | Views.Details.Heating.Service | Operational Space Temperature | 1675 | 15 |  | Views.Details.Htg.Service | OprST | 1709 | 28 |  |  | Operational Space Temperature | 1675 | 15 | 7006 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 25
Value |  |  | Views.Details.Heating.Service | Return Air Temperature | 1675 | 65 |  | Views.Details.Htg.Service | RAT | 1709 | 297 |  |  | Return Air Temperature | 1675 | 65 | 7038 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 25
Value |  |  | Views.Details.Heating.Service | Supply Air Temperature | 1675 | 182 |  | Views.Details.Htg.Service | SAT | 1709 | 80 |  |  | Supply Air Temperature | 1675 | 182 | 7014 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 3
Value |  |  | Views.Details.Heating.Service | W1 - Thermostat | 1675 | 154 |  | Views.Details.Htg.Service | W1-Tstat | 1709 | 15 |  |  | W1 - Thermostat | 1675 | 154 | 7004 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 2
Value |  |  | Views.Details.Heating.Service | W2 - Thermostat | 1675 | 155 |  | Views.Details.Htg.Service | W2-Tstat | 1709 | 16 |  |  | W2 - Thermostat | 1675 | 155 | 7005 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 2
Value |  |  | Views.Details.Heating.Service | W3 - Thermostat | 1675 | 156 |  | Views.Details.Htg.Service | W3-Tstat | 1709 | 17 |  |  | W3 - Thermostat | 1675 | 156 | 7006 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 2
Value |  |  | Views.Details.Heating.Service | G - Thermostat | 1675 | 157 |  | Views.Details.Htg.Service | G-Tstat | 1709 | 18 |  |  | G - Thermostat | 1675 | 157 | 7007 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 2
Value |  |  | Views.Details.Heating.Service | Heating Stage 1 Status | 1714 | 103 |  | Views.Details.Htg.Service | H1-S | 1709 | 254 |  |  | Heat Stage Status | 1675 | 112 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  | SE RTU Heating Stage 1 Status | 1743 | [5 empty] | SE RTU Heating Stage 1 Status | 1743 | [5 empty] | 0 = Off-Idle 1 = On-Minimum Runtime Timer 2 = On-Normal Command 3 = Off-Heating Is Disabled ... | 15
Value |  |  | Views.Details.Heating.Service | Heating Stage Command 1 | 1714 | 149 |  | Views.Details.Htg.Service | H1 | 1709 | 251 |  |  | Heat Stage Command | 1675 | 111 | 7000 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 15
Value |  |  | Views.Details.Heating.Service | Heating Stage 1 Min On Time Remaining | 1714 | 105 |  | Views.Details.Htg.Service | H1OnTmr | 1709 | 260 |  |  | Heating Stage Min On Time Remaining | 1675 | 216 | 7003 | TRUE | FALSE | FALSE | 17 | SignedInteger | 1s | seconds | 507:73 |  |  |  |  | 1s | seconds | 507:73 | [6 empty] | 15
Value |  |  | Views.Details.Heating.Service | Heating Stage 1 Anti-Short Cycle Delay Time Remaining | 1714 | 106 |  | Views.Details.Htg.Service | H1ASCDTmr | 1709 | 263 |  |  | Heating Stage Anti-Short Cycle Delay Time Remaining | 1675 | 217 | 7004 | TRUE | FALSE | FALSE | 17 | SignedInteger | 1s | seconds | 507:73 |  |  |  |  | 1s | seconds | 507:73 | [6 empty] | 15
Value |  |  | Views.Details.Heating.Service | Heating Stage 1 Accumulated Runtime | 1714 | 108 |  | Views.Details.Htg.Service | H1RunTim | 1709 | 269 |  |  | Heat Stage Accumulated Runtime | 1675 | 116 | 7006 | TRUE | TRUE | FALSE | 4 | Float | 1s | hours | 507:71 | 0 | 10000 |  |  | 1s | hours | 507:71 | 0 | 10000 |  |  |  |  | 15
Value |  |  | Views.Details.Heating.Service | Heating Stage Command 2 | 1714 | 150 |  | Views.Details.Htg.Service | H2 | 1709 | 252 |  |  | Heat Stage Command | 1675 | 111 | 7000 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 16
Value |  |  | Views.Details.Heating.Service | Heating Stage 2 Status | 1714 | 109 |  | Views.Details.Htg.Service | H2-S | 1709 | 255 |  |  | Heat Stage Status | 1675 | 112 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  | SE RTU Heating Stage 1 Status | 1743 | [5 empty] | SE RTU Heating Stage 1 Status | 1743 | [5 empty] | 0 = Off-Idle 1 = On-Minimum Runtime Timer 2 = On-Normal Command 3 = Off-Heating Is Disabled ... | 16
Value |  |  | Views.Details.Heating.Service | Heating Stage 2 Min On Time Remaining | 1714 | 111 |  | Views.Details.Htg.Service | H2OnTmr | 1709 | 261 |  |  | Heating Stage Min On Time Remaining | 1675 | 216 | 7003 | TRUE | FALSE | FALSE | 17 | SignedInteger | 1s | seconds | 507:73 |  |  |  |  | 1s | seconds | 507:73 | [6 empty] | 16
Value |  |  | Views.Details.Heating.Service | Heating Stage 2 Anti-Short Cycle Delay Time Remaining | 1714 | 112 |  | Views.Details.Htg.Service | H2ASCDTmr | 1709 | 264 |  |  | Heating Stage Anti-Short Cycle Delay Time Remaining | 1675 | 217 | 7004 | TRUE | FALSE | FALSE | 17 | SignedInteger | 1s | seconds | 507:73 |  |  |  |  | 1s | seconds | 507:73 | [6 empty] | 16
Value |  |  | Views.Details.Heating.Service | Heating Stage 2 Accumulated Runtime | 1714 | 114 |  | Views.Details.Htg.Service | H2RunTim | 1709 | 270 |  |  | Heat Stage Accumulated Runtime | 1675 | 116 | 7006 | TRUE | TRUE | FALSE | 4 | Float | 1s | hours | 507:71 | 0 | 10000 |  |  | 1s | hours | 507:71 | 0 | 10000 |  |  |  |  | 16
Value |  |  | Views.Details.Heating.Service | Heating Stage Command 3 | 1714 | 151 |  | Views.Details.Htg.Service | H3 | 1709 | 253 |  |  | Heat Stage Command | 1675 | 111 | 7000 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 17
Value |  |  | Views.Details.Heating.Service | Heating Stage 3 Status | 1714 | 115 |  | Views.Details.Htg.Service | H3-S | 1709 | 256 |  |  | Heat Stage Status | 1675 | 112 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  | SE RTU Heating Stage 1 Status | 1743 | [5 empty] | SE RTU Heating Stage 1 Status | 1743 | [5 empty] | 0 = Off-Idle 1 = On-Minimum Runtime Timer 2 = On-Normal Command 3 = Off-Heating Is Disabled ... | 17
Value |  |  | Views.Details.Heating.Service | Heating Stage 3 Min On Time Remaining | 1714 | 117 |  | Views.Details.Htg.Service | H3OnTmr | 1709 | 262 |  |  | Heating Stage Min On Time Remaining | 1675 | 216 | 7003 | TRUE | FALSE | FALSE | 17 | SignedInteger | 1s | seconds | 507:73 |  |  |  |  | 1s | seconds | 507:73 | [6 empty] | 17
Value |  |  | Views.Details.Heating.Service | Heating Stage 3 Anti-Short Cycle Delay Time Remaining | 1714 | 118 |  | Views.Details.Htg.Service | H3ASCDTmr | 1709 | 265 |  |  | Heating Stage Anti-Short Cycle Delay Time Remaining | 1675 | 217 | 7004 | TRUE | FALSE | FALSE | 17 | SignedInteger | 1s | seconds | 507:73 |  |  |  |  | 1s | seconds | 507:73 | [6 empty] | 17
Value |  |  | Views.Details.Heating.Service | Heating Stage 3 Accumulated Runtime | 1714 | 120 |  | Views.Details.Htg.Service | H3RunTim | 1709 | 271 |  |  | Heat Stage Accumulated Runtime | 1675 | 116 | 7006 | TRUE | TRUE | FALSE | 4 | Float | 1s | hours | 507:71 | 0 | 10000 |  |  | 1s | hours | 507:71 | 0 | 10000 |  |  |  |  | 17
Group |  | FALSE | Views.Details.Heating.Safeties | Safeties | 1714 | 25 |  | Views.Details.Htg.Safeties | Safeties | 1709 | 404
Value |  |  | Views.Details.Heating.Safeties | Heat Limit1 Switch | 1675 | 121 |  | Views.Details.Htg.Safeties | Limit | 1709 | 233 |  |  | Heat Limit1 Switch | 1675 | 121 | 7009 | TRUE | FALSE | FALSE | 9 | MultiState |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 | [5 empty] | 0 = Normal 1 = Alarm | 13
Value |  |  | Views.Details.Heating.Safeties | Heat Limit1 Switch Lockout | 1675 | 122 |  | Views.Details.Htg.Safeties | LimitLO | 1709 | 234 |  |  | Heat Limit1 Switch Lockout | 1675 | 122 | 7010 | TRUE | FALSE | FALSE | 9 | MultiState |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 | [5 empty] | 0 = Normal 1 = Lockout | 13
Value |  |  | Views.Details.Heating.Safeties | Heat Limit2 Switch | 1675 | 123 |  | Views.Details.Htg.Safeties | Lim2 | 1709 | 235 |  |  | Heat Limit2 Switch | 1675 | 123 | 7011 | TRUE | FALSE | FALSE | 9 | MultiState |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 | [5 empty] | 0 = Normal 1 = Alarm | 13
Value |  |  | Views.Details.Heating.Safeties | Heat Limit2 Switch Lockout | 1675 | 124 |  | Views.Details.Htg.Safeties | Lim2LO | 1709 | 236 |  |  | Heat Limit2 Switch Lockout | 1675 | 124 | 7012 | TRUE | FALSE | FALSE | 9 | MultiState |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 | [5 empty] | 0 = Normal 1 = Lockout | 13
Value |  |  | Views.Details.Heating.Safeties | Heat Limit3 Switch | 1675 | 125 |  | Views.Details.Htg.Safeties | Lim3 | 1709 | 237 |  |  | Heat Limit3 Switch | 1675 | 125 | 7013 | TRUE | FALSE | FALSE | 9 | MultiState |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 | [5 empty] | 0 = Normal 1 = Alarm | 13
Value |  |  | Views.Details.Heating.Safeties | Heat Limit3 Switch Lockout | 1675 | 126 |  | Views.Details.Htg.Safeties | Lim3LO | 1709 | 238 |  |  | Heat Limit3 Switch Lockout | 1675 | 126 | 7014 | TRUE | FALSE | FALSE | 9 | MultiState |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 | [5 empty] | 0 = Normal 1 = Lockout | 13
Value |  |  | Views.Details.Heating.Safeties | Gas Valve1 Input | 1675 | 118 |  | Views.Details.Htg.Safeties | MV | 1709 | 230 |  |  | Gas Valve1 Input | 1675 | 118 | 7006 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 13
Value |  |  | Views.Details.Heating.Safeties | Gas Valve2 Input | 1675 | 119 |  | Views.Details.Htg.Safeties | GV2 | 1709 | 231 |  |  | Gas Valve2 Input | 1675 | 119 | 7007 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 13
Value |  |  | Views.Details.Heating.Safeties | Gas Valve3 Input | 1675 | 120 |  | Views.Details.Htg.Safeties | GV3 | 1709 | 232 |  |  | Gas Valve3 Input | 1675 | 120 | 7008 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 13
Group |  | FALSE | Views.Details.Heating.Proportional | Proportional | 1714 | 194 |  | Views.Details.Htg.Prop | Prop | 1709 | 637 | York RTU.Heating Control Type:Present Value = Proportional
Group |  | TRUE | Views.Details.Heating.Proportional.Setup | Setup | 1714 | 29 |  | Views.Details.Htg.Prop.Setup | Setup | 1709 | 408
Value |  |  | Views.Details.Heating.Proportional.Setup | Hydronic Heating Stage #1 Supply Air Setpoint | 1675 | 220 |  | Views.Details.Htg.Prop.Setup | HydH1SA-Sp | 1709 | 277 |  |  | Hydronic Heating Stage #1 Supply Air Setpoint | 1675 | 220 | 7002 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 80 | 180 |  |  | 1s | deg C | 507:62 | 27 | 82 |  |  |  |  | 18
Value |  |  | Views.Details.Heating.Proportional.Setup | Hydronic Heating Stage #2 Supply Air Setpoint | 1675 | 221 |  | Views.Details.Htg.Prop.Setup | HydH2SA-Sp | 1709 | 278 |  |  | Hydronic Heating Stage #2 Supply Air Setpoint | 1675 | 221 | 7003 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 80 | 180 |  |  | 1s | deg C | 507:62 | 27 | 82 |  |  |  |  | 18
Value |  |  | Views.Details.Heating.Proportional.Setup | Hydronic Heat SAT Tempering Enabled | 1675 | 222 |  | Views.Details.Htg.Prop.Setup | SATTempHydHt-En | 1709 | 279 |  |  | Hydronic Heat SAT Tempering Enabled | 1675 | 222 | 7004 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 18
Value |  |  | Views.Details.Heating.Proportional.Setup | Hydronic Heat SAT Tempering Setpoint | 1675 | 223 |  | Views.Details.Htg.Prop.Setup | SATTempHydHt-Sp | 1709 | 280 |  |  | Hydronic Heat SAT Tempering Setpoint | 1675 | 223 | 7005 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 40 | 60 |  |  | 1s | deg C | 507:62 | 4 | 15 |  |  |  |  | 18
Value |  |  | Views.Details.Heating.Proportional.Setup | Hydronic Heat Valve Reverse Acting | 1675 | 219 |  | Views.Details.Htg.Prop.Setup | HydReverse | 1709 | 276 |  |  | Hydronic Heat Valve Reverse Acting | 1675 | 219 | 7001 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 18
Group |  | TRUE | Views.Details.Heating.Proportional.Service | Service | 1714 | 27 |  | Views.Details.Htg.Prop.Service | Service | 1709 | 406
Value |  |  | Views.Details.Heating.Proportional.Service | CV Occupied Heating Setpoint | 1675 | 212 |  | Views.Details.Htg.Prop.Service | CVHtgOcc-SP | 1709 | 461 |  |  | CV Occupied Heating Setpoint | 1675 | 212 | 7023 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 46 | 99 |  |  | 1s | deg C | 507:62 | 8 | 37 |  |  |  |  | 13
Value |  |  | Views.Details.Heating.Proportional.Service | CV Unoccupied Heating Setpoint | 1675 | 213 |  | Views.Details.Htg.Prop.Service | CVHtgUnocc-Sp | 1709 | 462 |  |  | CV Unoccupied Heating Setpoint | 1675 | 213 | 7024 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 45 | 98 |  |  | 1s | deg C | 507:62 | 7 | 36 |  |  |  |  | 13
Value |  |  | Views.Details.Heating.Proportional.Service | CV Operating Heating Setpoint | 1675 | 214 |  | Views.Details.Htg.Prop.Service | CVOprHtg-Sp | 1709 | 463 |  |  | CV Operating Heating Setpoint | 1675 | 214 | 7025 | TRUE | FALSE | FALSE | 4 | Float | 100ths | deg F | 507:64 |  |  |  |  | 100ths | deg C | 507:62 | [6 empty] | 13
Value |  |  | Views.Details.Heating.Proportional.Service | VAV Operating Heating Setpoint | 1675 | 208 |  | Views.Details.Htg.Prop.Service | VAVOprHtg-Sp | 1709 | 243 |  |  | VAV Operating Heating Setpoint | 1675 | 208 | 7019 | TRUE | FALSE | FALSE | 4 | Float | 100ths | deg F | 507:64 |  |  |  |  | 100ths | deg C | 507:62 | [6 empty] | 13
Value |  |  | Views.Details.Heating.Proportional.Service | Operational Space Temperature | 1675 | 15 |  | Views.Details.Htg.Prop.Service | OprST | 1709 | 28 |  |  | Operational Space Temperature | 1675 | 15 | 7006 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 25
Value |  |  | Views.Details.Heating.Proportional.Service | Supply Air Temperature | 1675 | 182 |  | Views.Details.Htg.Prop.Service | SAT | 1709 | 80 |  |  | Supply Air Temperature | 1675 | 182 | 7014 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 3
Value |  |  | Views.Details.Heating.Proportional.Service | W1 - Thermostat | 1675 | 154 |  | Views.Details.Htg.Prop.Service | W1-Tstat | 1709 | 15 |  |  | W1 - Thermostat | 1675 | 154 | 7004 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 2
Value |  |  | Views.Details.Heating.Proportional.Service | W2 - Thermostat | 1675 | 155 |  | Views.Details.Htg.Prop.Service | W2-Tstat | 1709 | 16 |  |  | W2 - Thermostat | 1675 | 155 | 7005 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 2
Value |  |  | Views.Details.Heating.Proportional.Service | Hydronic Heat Valve % Command | 1675 | 218 |  | Views.Details.Htg.Prop.Service | HWV | 1709 | 275 |  |  | Hydronic Heat Valve % Command | 1675 | 218 | 7000 | TRUE | FALSE | FALSE | 4 | Float | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 | [6 empty] | 18
Value |  |  | Views.Details.Heating.Proportional.Service | Hydronic Heat Valve Reverse Acting | 1675 | 219 |  | Views.Details.Htg.Prop.Service | HydReverse | 1709 | 276 |  |  | Hydronic Heat Valve Reverse Acting | 1675 | 219 | 7001 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 18
Value |  |  | Views.Details.Heating.Proportional.Service | Hot Water Freeze Stat | 1675 | 203 |  | Views.Details.Htg.Prop.Service | FSHW | 1709 | 229 |  |  | Hot Water Freeze Stat | 1675 | 203 | 7005 | TRUE | FALSE | FALSE | 9 | MultiState |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 | [5 empty] | 0 = Normal 1 = Alarm | 13
Group |  | FALSE | Views.Details.Indoor Fan | Indoor Fan | 1714 | 16 |  | Views.Details.Fan | Fan | 1709 | 79
Group |  | TRUE | Views.Details.Indoor Fan.Setup | Setup | 1714 | 29 |  | Views.Details.Fan.Setup | Setup | 1709 | 408
Value |  |  | Views.Details.Indoor Fan.Setup | Fan Control Type | 1675 | 173 |  | Views.Details.Fan.Setup | FanCtl-Type | 1709 | 71 |  |  | Fan Control Type | 1675 | 173 | 7005 | TRUE | TRUE | FALSE | 9 | MultiState |  | SE RTU Fan Control Type | 1619 | [5 empty] | SE RTU Fan Control Type | 1619 | [5 empty] | 0 = Single Speed 1 = Not Used 2 = Fixed Variable 3 = Variable Speed | 3
Value |  |  | Views.Details.Indoor Fan.Setup | Continuous Fan Operation in Occupied Mode | 1675 | 186 |  | Views.Details.Fan.Setup | FanOnOcc | 1709 | 84 |  |  | Continuous Fan Operation in Occupied Mode | 1675 | 186 | 7018 | TRUE | TRUE | FALSE | 9 | MultiState |  | Yes/No | 1698 | [5 empty] | Yes/No | 1698 | [5 empty] | 0 = Yes 1 = No | 3
Value |  |  | Views.Details.Indoor Fan.Setup | Fan On Delay for Heat | 1675 | 178 |  | Views.Details.Fan.Setup | FanOnDlyHeat | 1709 | 76 |  |  | Fan On Delay for Heat | 1675 | 178 | 7010 | TRUE | TRUE | FALSE | 17 | SignedInteger | 1s | seconds | 507:73 | 0 | 30 |  |  | 1s | seconds | 507:73 | 0 | 30 |  |  |  |  | 3
Value |  |  | Views.Details.Indoor Fan.Setup | Fan Off Delay for Heat | 1675 | 179 |  | Views.Details.Fan.Setup | FanOffDlyHeat | 1709 | 77 |  |  | Fan Off Delay for Heat | 1675 | 179 | 7011 | TRUE | TRUE | FALSE | 17 | SignedInteger | 1s | seconds | 507:73 | 0 | 255 |  |  | 1s | seconds | 507:73 | 0 | 255 |  |  |  |  | 3
Value |  |  | Views.Details.Indoor Fan.Setup | Turn Off Continuous Fan Operation When Starting Heat | 1675 | 187 |  | Views.Details.Fan.Setup | FanOffStartHeat | 1709 | 85 |  |  | Turn Off Continuous Fan Operation When Starting Heat | 1675 | 187 | 7019 | TRUE | TRUE | FALSE | 9 | MultiState |  | Yes/No | 1698 | [5 empty] | Yes/No | 1698 | [5 empty] | 0 = Yes 1 = No | 3
Value |  |  | Views.Details.Indoor Fan.Setup | Fan On Delay for Cool | 1675 | 176 |  | Views.Details.Fan.Setup | FanOnDlyCool | 1709 | 74 |  |  | Fan On Delay for Cool | 1675 | 176 | 7008 | TRUE | TRUE | FALSE | 17 | SignedInteger | 1s | seconds | 507:73 | 0 | 30 |  |  | 1s | seconds | 507:73 | 0 | 30 |  |  |  |  | 3
Value |  |  | Views.Details.Indoor Fan.Setup | Fan Off Delay for Cool | 1675 | 177 |  | Views.Details.Fan.Setup | FanOffDlyCool | 1709 | 75 |  |  | Fan Off Delay for Cool | 1675 | 177 | 7009 | TRUE | TRUE | FALSE | 17 | SignedInteger | 1s | seconds | 507:73 | 0 | 255 |  |  | 1s | seconds | 507:73 | 0 | 255 |  |  |  |  | 3
Value |  |  | Views.Details.Indoor Fan.Setup | Occupied: No Heat or Cool % Command | 1675 | 188 |  | Views.Details.Fan.Setup | FanOnly-%Cmd | 1709 | 86 |  |  | Occupied: No Heat or Cool % Command | 1675 | 188 | 7020 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 3
Value |  |  | Views.Details.Indoor Fan.Setup | Occupied: One Stage of Cool % Command | 1675 | 189 |  | Views.Details.Fan.Setup | 1ClgStg-%Cmd | 1709 | 87 |  |  | Occupied: One Stage of Cool % Command | 1675 | 189 | 7021 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 3
Value |  |  | Views.Details.Indoor Fan.Setup | Occupied: Two Stage of Cool % Command | 1675 | 190 |  | Views.Details.Fan.Setup | 2ClgStg-%Cmd | 1709 | 88 |  |  | Occupied: Two Stage of Cool % Command | 1675 | 190 | 7022 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 3
Value |  |  | Views.Details.Indoor Fan.Setup | Occupied: Three Stage of Cool % Command | 1675 | 320 |  | Views.Details.Fan.Setup | 3ClgStg-%Cmd | 1709 | 442 |  |  | Occupied: Three Stage of Cool % Command | 1675 | 320 | 7027 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 3
Value |  |  | Views.Details.Indoor Fan.Setup | Occupied: Four Stage of Cool % Command | 1675 | 321 |  | Views.Details.Fan.Setup | 4ClgStg-%Cmd | 1709 | 443 |  |  | Occupied: Four Stage of Cool % Command | 1675 | 321 | 7028 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 3
Value |  |  | Views.Details.Indoor Fan.Setup | Occupied: One Stage of Heat % Command | 1675 | 191 |  | Views.Details.Fan.Setup | 1HtgStg-%Cmd | 1709 | 89 |  |  | Occupied: One Stage of Heat % Command | 1675 | 191 | 7023 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 3
Value |  |  | Views.Details.Indoor Fan.Setup | Occupied: Two Stage of Heat % Command | 1675 | 192 |  | Views.Details.Fan.Setup | 2HtgStg-%Cmd | 1709 | 90 |  |  | Occupied: Two Stage of Heat % Command | 1675 | 192 | 7024 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 3
Value |  |  | Views.Details.Indoor Fan.Setup | Occupied: Three Stage of Heat % Command | 1675 | 322 |  | Views.Details.Fan.Setup | 3HtgStg-%Cmd | 1709 | 444 |  |  | Occupied: Three Stage of Heat % Command | 1675 | 322 | 7029 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 3
Value |  |  | Views.Details.Indoor Fan.Setup | Dehumidification % Command | 1714 | 234 |  | Views.Details.Fan.Setup | Dehum%Cmd | 1709 | 731 |  |  | Dehumidification % Command | 1714 | 234 | 7042 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 3
Value |  |  | Views.Details.Indoor Fan.Setup | Low Ambient Fan Pre-run Time For Cooling | 1675 | 73 |  | Views.Details.Fan.Setup | LowAmbFanPrerunCool | 1709 | 96 |  |  | Low Ambient Fan Pre-run Time For Cooling | 1675 | 73 | 7005 | TRUE | TRUE | FALSE | 17 | SignedInteger | 1s | seconds | 507:73 | 0 | 255 |  |  | 1s | seconds | 507:73 | 0 | 255 |  |  |  |  | 4
Value |  |  | Views.Details.Indoor Fan.Setup | Air Proving Switch Setup | 1675 | 174 |  | Views.Details.Fan.Setup | APSSetup | 1709 | 72 |  |  | Air Proving Switch Setup | 1675 | 174 | 7006 | TRUE | TRUE | FALSE | 9 | MultiState |  | Fan Setup | 1622 | [5 empty] | Fan Setup | 1622 | [5 empty] | 0 = Constant Volume 1 = Variable Volume 2 = None | 3
Value |  |  | Views.Details.Indoor Fan.Setup | Dirty Filter Switch | 1675 | 180 |  | Views.Details.Fan.Setup | DFS | 1709 | 78 |  |  | Dirty Filter Switch | 1675 | 180 | 7012 | TRUE | FALSE | FALSE | 9 | MultiState |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 | [5 empty] | 0 = Normal 1 = Alarm | 3
Group |  | TRUE | Views.Details.Indoor Fan.Service | Service | 1714 | 27 |  | Views.Details.Fan.Service | Service | 1709 | 406
Value |  |  | Views.Details.Indoor Fan.Service | G - Thermostat | 1675 | 157 |  | Views.Details.Fan.Service | G-Tstat | 1709 | 18 |  |  | G - Thermostat | 1675 | 157 | 7007 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 2
Value |  |  | Views.Details.Indoor Fan.Service | Fan Status | 1675 | 168 |  | Views.Details.Fan.Service | Fan-S | 1709 | 66 |  |  | Fan Status | 1675 | 168 | 7000 | TRUE | FALSE | FALSE | 9 | MultiState |  | SE RTU Fan Status | 1739 | [5 empty] | SE RTU Fan Status | 1739 | [5 empty] | 0 = Off-Idle 1 = On-Purge 2 = On-Gas Valve or Limit Fault 3 = On-Defrost ... | 3
Value |  |  | Views.Details.Indoor Fan.Service | Fan Command | 1675 | 181 |  | Views.Details.Fan.Service | Fan | 1709 | 79 |  |  | Fan Command | 1675 | 181 | 7013 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 3
Value |  |  | Views.Details.Indoor Fan.Service | Fan Accumulated Runtime | 1675 | 172 |  | Views.Details.Fan.Service | Fan-RT | 1709 | 70 |  |  | Fan Accumulated Runtime | 1675 | 172 | 7004 | TRUE | TRUE | FALSE | 4 | Float | 1s | hours | 507:71 | 0 | 10000 |  |  | 1s | hours | 507:71 | 0 | 10000 |  |  |  |  | 3
Value |  |  | Views.Details.Indoor Fan.Service | Operating Fan Request | 1675 | 27 |  | Views.Details.Fan.Service | OprFanReq | 1709 | 43 |  |  | Operating Fan Request | 1675 | 27 | 7021 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 25
Value |  |  | Views.Details.Indoor Fan.Service | Fan Request Source | 1675 | 28 |  | Views.Details.Fan.Service | FanReqSrc | 1709 | 44 |  |  | Fan Request Source | 1675 | 28 | 7022 | TRUE | FALSE | FALSE | 9 | MultiState |  | Effective Input Source 2 | 1732 | [5 empty] | Effective Input Source 2 | 1732 | [5 empty] | 0 = Unreliable 1 = Local Input 2 = Network Sensor 3 = High Priority ... | 25
Value |  |  | Views.Details.Indoor Fan.Service | Air Proving Switch | 1675 | 175 |  | Views.Details.Fan.Service | APS | 1709 | 73 |  |  | Air Proving Switch | 1675 | 175 | 7007 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 3
Value |  |  | Views.Details.Indoor Fan.Service | Fan Overload | 1675 | 171 |  | Views.Details.Fan.Service | FanOvrload | 1709 | 69 |  |  | Fan Overload | 1675 | 171 | 7003 | TRUE | FALSE | FALSE | 9 | MultiState |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 | [5 empty] | 0 = Normal 1 = Alarm | 3
Value |  |  | Views.Details.Indoor Fan.Service | Fan VFD Fault | 1675 | 170 |  | Views.Details.Fan.Service | FanVFDFlt | 1709 | 68 |  |  | Fan VFD Fault | 1675 | 170 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 | [5 empty] | 0 = Normal 1 = Alarm | 3
Group |  | FALSE | Views.Details.Economizer | Economizer | 1714 | 8 |  | Views.Details.Econ | Econ | 1709 | 282 | York RTU.System Controllers.Econ Controller:Present Value <> Not Present
Group |  | TRUE | Views.Details.Economizer.Setup | Setup | 1714 | 29 |  | Views.Details.Econ.Setup | Setup | 1709 | 408
Value |  |  | Views.Details.Economizer.Setup | Economizer Enabled For Operation | 1675 | 50 |  | Views.Details.Econ.Setup | Econ-En | 1709 | 281 |  |  | Economizer Enabled For Operation | 1675 | 50 | 7000 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 19
Value |  |  | Views.Details.Economizer.Setup | Economizer Minimum Position Setpoint | 1675 | 292 |  | Views.Details.Econ.Setup | Econ-MinPos | 1709 | 381 |  |  | Economizer Minimum Position Setpoint | 1675 | 292 | 7017 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 19
Value |  |  | Views.Details.Economizer.Setup | Economizer Damper Minimum Position Low Speed Fan | 1675 | 327 |  | Views.Details.Econ.Setup | LowSpeedFan-MinPos | 1709 | 447 |  |  | Economizer Damper Minimum Position Low Speed Fan | 1675 | 327 | 7025 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 19
Value |  |  | Views.Details.Economizer.Setup | Low Ambient Economizer Minimum Position | 1675 | 59 |  | Views.Details.Econ.Setup | LowAmb-MinPos | 1709 | 290 |  |  | Low Ambient Economizer Minimum Position | 1675 | 59 | 7009 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 19
Value |  |  | Views.Details.Economizer.Setup | Low Ambient Economizer Setpoint | 1675 | 58 |  | Views.Details.Econ.Setup | LowAmb-Sp | 1709 | 289 |  |  | Low Ambient Economizer Setpoint | 1675 | 58 | 7008 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | -20 | 60 |  |  | 1s | deg C | 507:62 | -29 | 15 |  |  |  |  | 19
Value |  |  | Views.Details.Economizer.Setup | Free Cooling Selection | 1675 | 55 |  | Views.Details.Econ.Setup | FreeClg-Sel | 1709 | 286 |  |  | Free Cooling Selection | 1675 | 55 | 7005 | TRUE | TRUE | FALSE | 9 | MultiState |  | SE RTU Economizer Type | 3398 | [5 empty] | SE RTU Economizer Type | 3398 | [5 empty] | 0 = Dry Bulb Temperature 1 = Single Enthalpy 2 = Dual Enthalpy 3 = Auto 4 = Differential Dry Bulb | 19
Value |  |  | Views.Details.Economizer.Setup | Free Cooling Current Mode | 1675 | 54 |  | Views.Details.Econ.Setup | FreeClg-Mode | 1709 | 285 |  |  | Free Cooling Current Mode | 1675 | 54 | 7004 | TRUE | FALSE | FALSE | 9 | MultiState |  | Actual Economizer Type Advanced | 3338 | [5 empty] | Actual Economizer Type Advanced | 3338 | [5 empty] | 0 = Dry Bulb Temperature 1 = Differential Dry Bulb 2 = Single Enthalpy 3 = Dual Enthalpy 4 = Unreliable | 19
Value |  |  | Views.Details.Economizer.Setup | All Compressors Off in Free Cooling | 1675 | 77 |  | Views.Details.Econ.Setup | AllCompOff-Econ | 1709 | 100 |  |  | All Compressors Off in Free Cooling | 1675 | 77 | 7009 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 4
Value |  |  | Views.Details.Economizer.Setup | Economizer Outdoor Air Temp Enable Setpoint | 1675 | 56 |  | Views.Details.Econ.Setup | EconOAT-SpEn | 1709 | 287 |  |  | Economizer Outdoor Air Temp Enable Setpoint | 1675 | 56 | 7006 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 0 | 80 |  |  | 1s | deg C | 507:62 | -17.8 | 27 |  |  |  |  | 19
Value |  |  | Views.Details.Economizer.Setup | Economizer Outdoor Air Enthalpy Setpoint | 1675 | 57 |  | Views.Details.Econ.Setup | EconOAEnth-Sp | 1709 | 288 |  |  | Economizer Outdoor Air Enthalpy Setpoint | 1675 | 57 | 7007 | TRUE | TRUE | FALSE | 4 | Float | 1s | Btu/lb dry air | 507:24 | 10 | 50 |  |  | 1s | kJ/kg | 507:125 | 23 | 116 |  |  |  |  | 19
Value |  |  | Views.Details.Economizer.Setup | Demand Ventilation Mode of Operation | 1675 | 225 |  | Views.Details.Econ.Setup | DVent-Mode | 1709 | 298 |  |  | Demand Ventilation Mode of Operation | 1675 | 225 | 7000 | TRUE | TRUE | FALSE | 9 | MultiState |  | SE RTU DCV Mode | 1729 | [5 empty] | SE RTU DCV Mode | 1729 | [5 empty] | 0 = Disabled 1 = Controlled by IAQ 2 = Diff between IAQ and OAQ | 23
Value |  |  | Views.Details.Economizer.Setup | Demand Ventilation Maximum Economizer Position | 1675 | 226 |  | Views.Details.Econ.Setup | DVentMaxEconPos | 1709 | 299 |  |  | Demand Ventilation Maximum Economizer Position | 1675 | 226 | 7001 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 23
Value |  |  | Views.Details.Economizer.Setup | Demand Ventilation Indoor Air Quality Setpoint | 1675 | 227 |  | Views.Details.Econ.Setup | DVentIAQ-Sp | 1709 | 300 |  |  | Demand Ventilation Indoor Air Quality Setpoint | 1675 | 227 | 7002 | TRUE | TRUE | FALSE | 4 | Float | 1s | ppm | 507:96 | 0 | 5000 |  |  | 1s | ppm | 507:96 | 0 | 5000 |  |  |  |  | 23
Value |  |  | Views.Details.Economizer.Setup | Demand Ventilation Differential Setpoint | 1675 | 228 |  | Views.Details.Econ.Setup | DVentDiff-Sp | 1709 | 301 |  |  | Demand Ventilation Differential Setpoint | 1675 | 228 | 7003 | TRUE | TRUE | FALSE | 4 | Float | 1s | ppm | 507:96 | 0 | 5000 |  |  | 1s | ppm | 507:96 | 0 | 5000 |  |  |  |  | 23
Value |  |  | Views.Details.Economizer.Setup | Indoor Air Quality Sensor Range | 1675 | 166 |  | Views.Details.Econ.Setup | IAQRange | 1709 | 37 |  |  | Indoor Air Quality Sensor Range | 1675 | 166 | 7015 | TRUE | TRUE | FALSE | 4 | Float | 1s | ppm | 507:96 | 0 | 5000 |  |  | 1s | ppm | 507:96 | 0 | 5000 |  |  |  |  | 25
Value |  |  | Views.Details.Economizer.Setup | Outdoor Air Quality Sensor Range | 1675 | 48 |  | Views.Details.Econ.Setup | OAQRange | 1709 | 64 |  |  | Outdoor Air Quality Sensor Range | 1675 | 48 | 7012 | TRUE | TRUE | FALSE | 4 | Float | 10s | ppm | 507:96 | 0 | 5000 |  |  | 10s | ppm | 507:96 | 0 | 5000 |  |  |  |  | 26
Value |  |  | Views.Details.Economizer.Setup | Economizer Loading Enabled | 1675 | 76 |  | Views.Details.Econ.Setup | EconLoad-En | 1709 | 99 |  |  | Economizer Loading Enabled | 1675 | 76 | 7008 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 4
Value |  |  | Views.Details.Economizer.Setup | Fresh Air Intake Setpoint | 1675 | 255 |  | Views.Details.Econ.Setup | MOAFlow-Sp | 1709 | 329 |  |  | Fresh Air Intake Setpoint | 1675 | 255 | 7000 | TRUE | TRUE | FALSE | 4 | Float | 10s | cfm | 507:84 | 0 | 50000 |  |  | 10s | L/s | 507:87 | 0 | 25000 |  |  |  |  | 24
Value |  |  | Views.Details.Economizer.Setup | Fresh Air Intake Max Sensor Range | 1675 | 257 |  | Views.Details.Econ.Setup | MOA-Range | 1709 | 331 |  |  | Fresh Air Intake Max Sensor Range | 1675 | 257 | 7002 | TRUE | TRUE | FALSE | 4 | Float | 10s | cfm | 507:84 | 0 | 50000 |  |  | 10s | L/s | 507:87 | 0 | 25000 |  |  |  |  | 24
Value |  |  | Views.Details.Economizer.Setup | EconMech Setup | 1675 | 498 |  | Views.Details.Econ.Setup | EconMechStp | 1709 | 630 |  |  | EconMech Setup | 1675 | 498 | 7027 | TRUE | TRUE | FALSE | 9 | MultiState |  | SE RTU EconMech Setup | 1752 | [5 empty] | SE RTU EconMech Setup | 1752 | [5 empty] | 0 = Option A 1 = Option B | 19
Value |  |  | Views.Details.Economizer.Setup | Economizer Fault Detection Enable | 1675 | 626 |  | Views.Details.Econ.Setup | EconFltDetectEn | 1709 | 646 |  |  | Economizer Fault Detection Enable | 1675 | 626 | 7028 | TRUE | TRUE | FALSE | 9 | MultiState |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 | [5 empty] | 0 = Disable 1 = Enable | 19
Value |  |  | Views.Details.Economizer.Setup | Calibration Fault Detect Enable | 1714 | 226 |  | Views.Details.Econ.Setup | CalFaultDetectEn | 1709 | 723 |  |  | Calibration Fault Detect Enable | 1714 | 226 | 7032 | TRUE | TRUE | FALSE | 9 | MultiState |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 | [5 empty] | 0 = Disable 1 = Enable | 19
Value |  |  | Views.Details.Economizer.Setup | Mixed Air Temperature Cooling Limit | 2644 | 274 |  | Views.Details.Econ.Setup | MATClgLim | 2645 | 293 |  |  | Mixed Air Temperature Cooling Limit | 2644 | 274 | 7034 | TRUE | TRUE | FALSE | 9 | MultiState |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 | [5 empty] | 0 = Disable 1 = Enable | 19
Group |  | TRUE | Views.Details.Economizer.Service | Service | 1714 | 27 |  | Views.Details.Econ.Service | Service | 1709 | 406
Value |  |  | Views.Details.Economizer.Service | Cooling Status | 1675 | 69 |  | Views.Details.Econ.Service | Clg-S | 1709 | 93 |  |  | Cooling Status | 1675 | 69 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  | SE RTU Cooling Control Status | 1740 | [5 empty] | SE RTU Cooling Control Status | 1740 | [5 empty] | 0 = Off-Idle 1 = Thermostat Cooling 2 = Unoccupied Cooling 3 = Occupied Cooling ... | 4
Value |  |  | Views.Details.Economizer.Service | Economizer Status | 1675 | 53 |  | Views.Details.Econ.Service | Econ-S | 1709 | 284 |  |  | Economizer Status | 1675 | 53 | 7003 | TRUE | FALSE | FALSE | 9 | MultiState |  | SE RTU Economizer Status | 1738 | [5 empty] | SE RTU Economizer Status | 1738 | [5 empty] | 0 = Disabled 1 = Damper Not Functional 2 = Purge 3 = Unavailable-Sensor Fault ... | 19
Value |  |  | Views.Details.Economizer.Service | Econ Free Cooling Available | 1675 | 52 |  | Views.Details.Econ.Service | Econ-Free | 1709 | 283 |  |  | Econ Free Cooling Available | 1675 | 52 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 19
Value |  |  | Views.Details.Economizer.Service | Economizer Damper % Command | 1675 | 51 |  | Views.Details.Econ.Service | Econ | 1709 | 282 |  |  | Economizer Damper % Command | 1675 | 51 | 7001 | TRUE | FALSE | FALSE | 4 | Float | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 | [6 empty] | 19
Value |  |  | Views.Details.Economizer.Service | Supply Air Temperature | 1675 | 182 |  | Views.Details.Econ.Service | SAT | 1709 | 80 |  |  | Supply Air Temperature | 1675 | 182 | 7014 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 3
Value |  |  | Views.Details.Economizer.Service | Operational Outdoor Air Temperature | 1675 | 36 |  | Views.Details.Econ.Service | OprOAT | 1709 | 52 |  |  | Operational Outdoor Air Temperature | 1675 | 36 | 7000 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 26
Value |  |  | Views.Details.Economizer.Service | Outdoor Air Enthalpy | 1675 | 41 |  | Views.Details.Econ.Service | OA-Enth | 1709 | 57 |  |  | Outdoor Air Enthalpy | 1675 | 41 | 7005 | TRUE | FALSE | FALSE | 4 | Float | 1s | Btu/lb | 507:117 |  |  |  |  | 1s | kJ/kg | 507:125 | [6 empty] | 26
Value |  |  | Views.Details.Economizer.Service | Return Air Enthalpy | 1675 | 64 |  | Views.Details.Econ.Service | RA-Enth | 1709 | 296 |  |  | Return Air Enthalpy | 1675 | 64 | 7015 | TRUE | FALSE | FALSE | 4 | Float | 1s | Btu/lb | 507:117 |  |  |  |  | 1s | kJ/kg | 507:125 | [6 empty] | 19
Value |  |  | Views.Details.Economizer.Service | Operational Indoor Air Quality | 1675 | 165 |  | Views.Details.Econ.Service | OprIAQ | 1709 | 34 |  |  | Operational Indoor Air Quality | 1675 | 165 | 7012 | TRUE | FALSE | FALSE | 4 | Float | 10s | ppm | 507:96 |  |  |  |  | 10s | ppm | 507:96 | [6 empty] | 25
Value |  |  | Views.Details.Economizer.Service | Operational Outdoor Air Quality | 1675 | 45 |  | Views.Details.Econ.Service | OprOAQ | 1709 | 61 |  |  | Operational Outdoor Air Quality | 1675 | 45 | 7009 | TRUE | FALSE | FALSE | 4 | Float | 10s | ppm | 507:96 |  |  |  |  | 10s | ppm | 507:96 | [6 empty] | 26
Value |  |  | Views.Details.Economizer.Service | Fresh Air Intake Value | 1675 | 256 |  | Views.Details.Econ.Service | Fr Air | 1709 | 330 |  |  | Fresh Air Intake Value | 1675 | 256 | 7001 | TRUE | FALSE | FALSE | 4 | Float | 1s | cfm | 507:84 |  |  |  |  | 1s | L/s | 507:87 | [6 empty] | 24
Value |  |  | Views.Details.Economizer.Service | Economizer Damper Position | 1675 | 335 |  | Views.Details.Econ.Service | EconDampPos | 1709 | 449 |  |  | Economizer Damper Position | 1675 | 335 | 7011 | TRUE | FALSE | FALSE | 4 | Float | 1s | % open | 507:264 |  |  |  |  | 1s | % open | 507:264 | [6 empty] | 19
Value |  |  | Views.Details.Economizer.Service | FDD Economizer Alarm Delay | 1675 | 633 |  | Views.Details.Econ.Service | EconAlrmDly | 1709 | 653 |  |  | FDD Economizer Alarm Delay | 1675 | 633 | 7029 | TRUE | TRUE | FALSE | 4 | Float | 10s | seconds | 507:73 | 0 | 3600 |  |  | 10s | seconds | 507:73 | 0 | 3600 |  |  |  |  | 19
Value |  |  | Views.Details.Economizer.Service | FDD Economizer Damper Allowed Error | 1675 | 634 |  | Views.Details.Econ.Service | EconPosErr | 1709 | 654 |  |  | FDD Economizer Damper Allowed Error | 1675 | 634 | 7030 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 19
Value |  |  | Views.Details.Economizer.Service | FDD Damper Min Position Tolerance | 1675 | 635 |  | Views.Details.Econ.Service | EconMinErr | 1709 | 655 |  |  | FDD Damper Min Position Tolerance | 1675 | 635 | 7031 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 19
Group |  | FALSE | Views.Details.Demand Ventilation | Demand Ventilation | 1714 | 7 |  | Views.Details.DVent | DVent | 1709 | 389 | York RTU.System Controllers.Econ Controller:Present Value <> Not Present
Value |  |  | Views.Details.Demand Ventilation | Economizer Enabled For Operation | 1675 | 50 |  | Views.Details.DVent | Econ-En | 1709 | 281 |  |  | Economizer Enabled For Operation | 1675 | 50 | 7000 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 19
Value |  |  | Views.Details.Demand Ventilation | Demand Ventilation Mode of Operation | 1675 | 225 |  | Views.Details.DVent | DVent-Mode | 1709 | 298 |  |  | Demand Ventilation Mode of Operation | 1675 | 225 | 7000 | TRUE | TRUE | FALSE | 9 | MultiState |  | SE RTU DCV Mode | 1729 | [5 empty] | SE RTU DCV Mode | 1729 | [5 empty] | 0 = Disabled 1 = Controlled by IAQ 2 = Diff between IAQ and OAQ | 23
Value |  |  | Views.Details.Demand Ventilation | Demand Ventilation Maximum Economizer Position | 1675 | 226 |  | Views.Details.DVent | DVentMaxEconPos | 1709 | 299 |  |  | Demand Ventilation Maximum Economizer Position | 1675 | 226 | 7001 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 23
Value |  |  | Views.Details.Demand Ventilation | Demand Ventilation Indoor Air Quality Setpoint | 1675 | 227 |  | Views.Details.DVent | DVentIAQ-Sp | 1709 | 300 |  |  | Demand Ventilation Indoor Air Quality Setpoint | 1675 | 227 | 7002 | TRUE | TRUE | FALSE | 4 | Float | 1s | ppm | 507:96 | 0 | 5000 |  |  | 1s | ppm | 507:96 | 0 | 5000 |  |  |  |  | 23
Value |  |  | Views.Details.Demand Ventilation | Demand Ventilation Differential Setpoint | 1675 | 228 |  | Views.Details.DVent | DVentDiff-Sp | 1709 | 301 |  |  | Demand Ventilation Differential Setpoint | 1675 | 228 | 7003 | TRUE | TRUE | FALSE | 4 | Float | 1s | ppm | 507:96 | 0 | 5000 |  |  | 1s | ppm | 507:96 | 0 | 5000 |  |  |  |  | 23
Value |  |  | Views.Details.Demand Ventilation | Indoor Air Quality Sensor Range | 1675 | 166 |  | Views.Details.DVent | IAQRange | 1709 | 37 |  |  | Indoor Air Quality Sensor Range | 1675 | 166 | 7015 | TRUE | TRUE | FALSE | 4 | Float | 1s | ppm | 507:96 | 0 | 5000 |  |  | 1s | ppm | 507:96 | 0 | 5000 |  |  |  |  | 25
Value |  |  | Views.Details.Demand Ventilation | Outdoor Air Quality Sensor Range | 1675 | 48 |  | Views.Details.DVent | OAQRange | 1709 | 64 |  |  | Outdoor Air Quality Sensor Range | 1675 | 48 | 7012 | TRUE | TRUE | FALSE | 4 | Float | 10s | ppm | 507:96 | 0 | 5000 |  |  | 10s | ppm | 507:96 | 0 | 5000 |  |  |  |  | 26
Value |  |  | Views.Details.Demand Ventilation | Operational Indoor Air Quality | 1675 | 165 |  | Views.Details.DVent | OprIAQ | 1709 | 34 |  |  | Operational Indoor Air Quality | 1675 | 165 | 7012 | TRUE | FALSE | FALSE | 4 | Float | 10s | ppm | 507:96 |  |  |  |  | 10s | ppm | 507:96 | [6 empty] | 25
Value |  |  | Views.Details.Demand Ventilation | Operational Outdoor Air Quality | 1675 | 45 |  | Views.Details.DVent | OprOAQ | 1709 | 61 |  |  | Operational Outdoor Air Quality | 1675 | 45 | 7009 | TRUE | FALSE | FALSE | 4 | Float | 10s | ppm | 507:96 |  |  |  |  | 10s | ppm | 507:96 | [6 empty] | 26
Value |  |  | Views.Details.Demand Ventilation | Economizer Damper Position | 1675 | 335 |  | Views.Details.DVent | EconDampPos | 1709 | 449 |  |  | Economizer Damper Position | 1675 | 335 | 7011 | TRUE | FALSE | FALSE | 4 | Float | 1s | % open | 507:264 |  |  |  |  | 1s | % open | 507:264 | [6 empty] | 19
Group |  | FALSE | Views.Details.Air Monitor Station | Air Monitor Station | 1714 | 0 |  | Views.Details.AirMonStation | AirMonStation | 1709 | 382 | York RTU.System Controllers.Econ Controller:Present Value <> Not Present
Value |  |  | Views.Details.Air Monitor Station | Economizer Enabled For Operation | 1675 | 50 |  | Views.Details.AirMonStation | Econ-En | 1709 | 281 |  |  | Economizer Enabled For Operation | 1675 | 50 | 7000 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 19
Value |  |  | Views.Details.Air Monitor Station | Fresh Air Intake Enable | 1675 | 741 |  | Views.Details.AirMonStation | FrAir-En | 1709 | 664 |  |  | Fresh Air Intake Enable | 1675 | 741 | 7004 | TRUE | TRUE | FALSE | 9 | MultiState |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 | [5 empty] | 0 = Disable 1 = Enable | 24
Value |  |  | Views.Details.Air Monitor Station | Fresh Air Intake Setpoint | 1675 | 255 |  | Views.Details.AirMonStation | MOAFlow-Sp | 1709 | 329 |  |  | Fresh Air Intake Setpoint | 1675 | 255 | 7000 | TRUE | TRUE | FALSE | 4 | Float | 10s | cfm | 507:84 | 0 | 50000 |  |  | 10s | L/s | 507:87 | 0 | 25000 |  |  |  |  | 24
Value |  |  | Views.Details.Air Monitor Station | Fresh Air Intake Max Sensor Range | 1675 | 257 |  | Views.Details.AirMonStation | MOA-Range | 1709 | 331 |  |  | Fresh Air Intake Max Sensor Range | 1675 | 257 | 7002 | TRUE | TRUE | FALSE | 4 | Float | 10s | cfm | 507:84 | 0 | 50000 |  |  | 10s | L/s | 507:87 | 0 | 25000 |  |  |  |  | 24
Value |  |  | Views.Details.Air Monitor Station | Fresh Air Intake Value | 1675 | 256 |  | Views.Details.AirMonStation | Fr Air | 1709 | 330 |  |  | Fresh Air Intake Value | 1675 | 256 | 7001 | TRUE | FALSE | FALSE | 4 | Float | 1s | cfm | 507:84 |  |  |  |  | 1s | L/s | 507:87 | [6 empty] | 24
Value |  |  | Views.Details.Air Monitor Station | Economizer Damper Position | 1675 | 335 |  | Views.Details.AirMonStation | EconDampPos | 1709 | 449 |  |  | Economizer Damper Position | 1675 | 335 | 7011 | TRUE | FALSE | FALSE | 4 | Float | 1s | % open | 507:264 |  |  |  |  | 1s | % open | 507:264 | [6 empty] | 19
Value |  |  | Views.Details.Air Monitor Station | Fresh Air Range | 1675 | 1038 |  | Views.Details.AirMonStation | Control | 1709 | 387 |  |  | Fresh Air Range | 1675 | 1038 | 7005 | TRUE | TRUE | FALSE | 4 | Float | 10s | cfm | 507:84 | 0 | 5000 |  |  | 10s | L/s | 507:87 | 0 | 2500 |  |  |  |  | 24
Group |  | FALSE | Views.Details.Power Exhaust | Power Exhaust | 1714 | 23 |  | Views.Details.PowerEx | PowerEx | 1709 | 402 | York RTU.System Controllers.Econ Controller:Present Value <> Not Present
Group |  | TRUE | Views.Details.Power Exhaust.Setup | Setup | 1714 | 29 |  | Views.Details.PowerEx.Setup | Setup | 1709 | 408
Value |  |  | Views.Details.Power Exhaust.Setup | Exhaust Type | 1675 | 147 |  | Views.Details.PowerEx.Setup | ExFType | 1709 | 8 |  |  | Exhaust Type | 1675 | 147 | 7008 | TRUE | TRUE | FALSE | 9 | MultiState |  | SE RTU Exhaust Setup | 1639 | [5 empty] | SE RTU Exhaust Setup | 1639 | [5 empty] | 0 = None 1 = Non-Modulating 2 = Modulating Damper 3 = Variable Frequency Fan | 1
Value |  |  | Views.Details.Power Exhaust.Setup | Economizer Damper Position for Exhaust Fan to Turn On | 1675 | 245 |  | Views.Details.PowerEx.Setup | EconDmpPosFanOn | 1709 | 319 |  |  | Economizer Damper Position for Exhaust Fan to Turn On | 1675 | 245 | 7011 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 20 | 99 |  |  | 1s | % | 507:98 | 20 | 99 |  |  |  |  | 21
Value |  |  | Views.Details.Power Exhaust.Setup | Economizer Damper Position for Exhaust Fan to Turn Off | 1675 | 246 |  | Views.Details.PowerEx.Setup | EconDmpPosFanOff | 1709 | 320 |  |  | Economizer Damper Position for Exhaust Fan to Turn Off | 1675 | 246 | 7012 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 10 | 89 |  |  | 1s | % | 507:98 | 10 | 89 |  |  |  |  | 21
Value |  |  | Views.Details.Power Exhaust.Setup | Exhaust Damper Position for Exhaust Fan to Turn On | 1675 | 243 |  | Views.Details.PowerEx.Setup | ExDmpPosFanOn | 1709 | 317 |  |  | Exhaust Damper Position for Exhaust Fan to Turn On | 1675 | 243 | 7009 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 20 | 99 |  |  | 1s | % | 507:98 | 20 | 99 |  |  |  |  | 21
Value |  |  | Views.Details.Power Exhaust.Setup | Exhaust Damper Position for Exhaust Fan to Turn Off | 1675 | 244 |  | Views.Details.PowerEx.Setup | ExDmpPosFanOff | 1709 | 318 |  |  | Exhaust Damper Position for Exhaust Fan to Turn Off | 1675 | 244 | 7010 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 10 | 89 |  |  | 1s | % | 507:98 | 10 | 89 |  |  |  |  | 21
Value |  |  | Views.Details.Power Exhaust.Setup | Building Pressure Setpoint | 1675 | 240 |  | Views.Details.PowerEx.Setup | Bldg-Sp | 1709 | 314 |  |  | Building Pressure Setpoint | 1675 | 240 | 7006 | TRUE | TRUE | FALSE | 4 | Float | 1000ths | in wc | 507:58 | -0.25 | 0.25 |  |  | 1000ths | kPa | 507:54 | -0.07 | 0.07 |  |  |  |  | 21
Value |  |  | Views.Details.Power Exhaust.Setup | Duct Static Pressure | 1675 | 183 |  | Views.Details.PowerEx.Setup | DctPrs | 1709 | 81 |  |  | Duct Static Pressure | 1675 | 183 | 7015 | TRUE | FALSE | FALSE | 4 | Float | 100ths | in wc | 507:58 |  |  |  |  | 100ths | kPa | 507:54 | [6 empty] | 3
Group |  | TRUE | Views.Details.Power Exhaust.Service | Service | 1714 | 27 |  | Views.Details.PowerEx.Service | Service | 1709 | 406
Value |  |  | Views.Details.Power Exhaust.Service | Exhaust Fan Status | 1675 | 237 |  | Views.Details.PowerEx.Service | ExF-S | 1709 | 311 |  |  | Exhaust Fan Status | 1675 | 237 | 7003 | TRUE | FALSE | FALSE | 9 | MultiState |  | SE RTU Exhaust Fan | 1745 | [5 empty] | SE RTU Exhaust Fan | 1745 | [5 empty] | 0 = Off-Idle 1 = On-Normal Command 2 = Off-Disabled 3 = Off-VFD Fault ... | 21
Value |  |  | Views.Details.Power Exhaust.Service | Exhaust Fan Command | 1675 | 235 |  | Views.Details.PowerEx.Service | ExFan | 1709 | 309 |  |  | Exhaust Fan Command | 1675 | 235 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 21
Value |  |  | Views.Details.Power Exhaust.Service | Building Static Pressure | 1675 | 241 |  | Views.Details.PowerEx.Service | BldgPres | 1709 | 315 |  |  | Building Static Pressure | 1675 | 241 | 7007 | TRUE | FALSE | FALSE | 4 | Float | 1000ths | in wc | 507:58 |  |  |  |  | 1000ths | kPa | 507:54 | [6 empty] | 21
Value |  |  | Views.Details.Power Exhaust.Service | Exhaust Damper % Command | 1675 | 242 |  | Views.Details.PowerEx.Service | EAD-O | 1709 | 316 |  |  | Exhaust Damper % Command | 1675 | 242 | 7008 | TRUE | FALSE | FALSE | 4 | Float | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 | [6 empty] | 21
Value |  |  | Views.Details.Power Exhaust.Service | Exhaust Fan VFD % Command | 1675 | 236 |  | Views.Details.PowerEx.Service | ExFanVFD | 1709 | 310 |  |  | Exhaust Fan VFD % Command | 1675 | 236 | 7002 | TRUE | FALSE | FALSE | 4 | Float | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 | [6 empty] | 21
Value |  |  | Views.Details.Power Exhaust.Service | Exhaust Fan Accumulated Runtime | 1675 | 239 |  | Views.Details.PowerEx.Service | ExF-RunTim | 1709 | 313 |  |  | Exhaust Fan Accumulated Runtime | 1675 | 239 | 7005 | TRUE | FALSE | FALSE | 4 | Float | 1s | hours | 507:71 |  |  |  |  | 1s | hours | 507:71 | [6 empty] | 21
Value |  |  | Views.Details.Power Exhaust.Service | Exhaust Fan VFD Fault | 1675 | 238 |  | Views.Details.PowerEx.Service | ExFanVFDFlt | 1709 | 312 |  |  | Exhaust Fan VFD Fault | 1675 | 238 | 7004 | TRUE | FALSE | FALSE | 9 | MultiState |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 | [5 empty] | 0 = Normal 1 = Alarm | 21
Group |  | FALSE | Views.Details.FanVFD | FanVFD | 1709 | 67 |  | Views.Details.FanVFD | FanVFD | 1709 | 67
Group |  | TRUE | Views.Details.FanVFD.Setup | Setup | 1714 | 29 |  | Views.Details.FanVFD.Setup | Setup | 1709 | 408
Value |  |  | Views.Details.FanVFD.Setup | Fan Control Type | 1675 | 173 |  | Views.Details.FanVFD.Setup | FanCtl-Type | 1709 | 71 |  |  | Fan Control Type | 1675 | 173 | 7005 | TRUE | TRUE | FALSE | 9 | MultiState |  | SE RTU Fan Control Type | 1619 | [5 empty] | SE RTU Fan Control Type | 1619 | [5 empty] | 0 = Single Speed 1 = Not Used 2 = Fixed Variable 3 = Variable Speed | 3
Value |  |  | Views.Details.FanVFD.Setup | Duct Pressure Setpoint | 1675 | 184 |  | Views.Details.FanVFD.Setup | DctPrs-Sp | 1709 | 82 |  |  | Duct Pressure Setpoint | 1675 | 184 | 7016 | TRUE | TRUE | FALSE | 4 | Float | 100ths | in wc | 507:58 | 0 | 5 |  |  | 100ths | kPa | 507:54 | 0 | 1.25 |  |  |  |  | 3
Value |  |  | Views.Details.FanVFD.Setup | Duct Pressure Shutdown Setpoint | 1675 | 185 |  | Views.Details.FanVFD.Setup | DctShutdownSp | 1709 | 83 |  |  | Duct Pressure Shutdown Setpoint | 1675 | 185 | 7017 | TRUE | TRUE | FALSE | 4 | Float | 100ths | in wc | 507:58 | 0 | 5 |  |  | 100ths | kPa | 507:54 | 0 | 1.25 |  |  |  |  | 3
Value |  |  | Views.Details.FanVFD.Setup | VAV Cooling Supply Air Temp Upper Setpoint | 1675 | 137 |  | Views.Details.FanVFD.Setup | SATUp-Sp | 1709 | 119 |  |  | VAV Cooling Supply Air Temp Upper Setpoint | 1675 | 137 | 7029 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 41 | 70 |  |  | 1s | deg C | 507:62 | 5 | 21 |  |  |  |  | 4
Value |  |  | Views.Details.FanVFD.Setup | VAV Cooling Supply Air Temp Lower Setpoint | 1675 | 138 |  | Views.Details.FanVFD.Setup | SATLo-Sp | 1709 | 120 |  |  | VAV Cooling Supply Air Temp Lower Setpoint | 1675 | 138 | 7030 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 40 | 69 |  |  | 1s | deg C | 507:62 | 4 | 20 |  |  |  |  | 4
Value |  |  | Views.Details.FanVFD.Setup | VAV Supply Air Temp Reset Setpoint | 1675 | 139 |  | Views.Details.FanVFD.Setup | SATRst-Sp | 1709 | 121 |  |  | VAV Supply Air Temp Reset Setpoint | 1675 | 139 | 7031 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 40 | 85 |  |  | 1s | deg C | 507:62 | 4 | 30 |  |  |  |  | 4
Value |  |  | Views.Details.FanVFD.Setup | VAV Unoccupied Cooling Setpoint | 1675 | 740 |  | Views.Details.FanVFD.Setup | VAVClgUnocc-Sp | 1709 | 663 |  |  | VAV Unoccupied Cooling Setpoint | 1675 | 740 | 7052 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 46 | 99 |  |  | 1s | deg C | 507:62 | 8 | 37 |  |  |  |  | 4
Value |  |  | Views.Details.FanVFD.Setup | Morning Warmup Enabled | 1675 | 209 |  | Views.Details.FanVFD.Setup | MornW-En | 1709 | 244 |  |  | Morning Warmup Enabled | 1675 | 209 | 7020 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 13
Value |  |  | Views.Details.FanVFD.Setup | Morning Warmup/Return Air Temp Setpoint | 1675 | 210 |  | Views.Details.FanVFD.Setup | MornWRAT-Sp | 1709 | 245 |  |  | Morning Warmup/Return Air Temp Setpoint | 1675 | 210 | 7021 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 50 | 85 |  |  | 1s | deg C | 507:62 | 10 | 30 |  |  |  |  | 13
Value |  |  | Views.Details.FanVFD.Setup | VAV Occupied Heating Enabled | 1675 | 204 |  | Views.Details.FanVFD.Setup | HtgOcc-En | 1709 | 239 |  |  | VAV Occupied Heating Enabled | 1675 | 204 | 7015 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 13
Value |  |  | Views.Details.FanVFD.Setup | VAV Occupied Heating Setpoint | 1675 | 205 |  | Views.Details.FanVFD.Setup | VAVHtgOcc-SP | 1709 | 240 |  |  | VAV Occupied Heating Setpoint | 1675 | 205 | 7016 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 40 | 85 |  |  | 1s | deg C | 507:62 | 4 | 30 |  |  |  |  | 13
Value |  |  | Views.Details.FanVFD.Setup | Unoccupied Heating Enabled | 1675 | 206 |  | Views.Details.FanVFD.Setup | HtgUnocc-En | 1709 | 241 |  |  | Unoccupied Heating Enabled | 1675 | 206 | 7017 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 13
Value |  |  | Views.Details.FanVFD.Setup | VAV Unoccupied Heating Setpoint | 1675 | 207 |  | Views.Details.FanVFD.Setup | VAVHtgUnocc-Sp | 1709 | 242 |  |  | VAV Unoccupied Heating Setpoint | 1675 | 207 | 7018 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 45 | 98 |  |  | 1s | deg C | 507:62 | 7 | 36 |  |  |  |  | 13
Value |  |  | Views.Details.FanVFD.Setup | Morning Cooldown Enabled | 1675 | 375 |  | Views.Details.FanVFD.Setup | MornC-En | 1709 | 486 |  |  | Morning Cooldown Enabled | 1675 | 375 | 7034 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 13
Value |  |  | Views.Details.FanVFD.Setup | Morning Cooldown/Return Air Temp Setpoint | 1675 | 376 |  | Views.Details.FanVFD.Setup | MornCRAT-Sp | 1709 | 487 |  |  | Morning Cooldown/Return Air Temp Setpoint | 1675 | 376 | 7035 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 50 | 85 |  |  | 1s | deg C | 507:62 | 10 | 30 |  |  |  |  | 13
Value |  |  | Views.Details.FanVFD.Setup | Optimal Start Enabled | 1675 | 377 |  | Views.Details.FanVFD.Setup | OptStrt-En | 1709 | 488 |  |  | Optimal Start Enabled | 1675 | 377 | 7036 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 13
Value |  |  | Views.Details.FanVFD.Setup | Early Start Period | 1675 | 379 |  | Views.Details.FanVFD.Setup | EarlyStrtPeriod | 1709 | 490 |  |  | Early Start Period | 1675 | 379 | 7038 | TRUE | TRUE | FALSE | 4 | Float | 1s | minutes | 507:72 | 0 | 120 |  |  | 1s | minutes | 507:72 | 0 | 120 |  |  |  |  | 13
Value |  |  | Views.Details.FanVFD.Setup | Discharge Air Static Pressure Minimum | 2644 | 227 |  | Views.Details.FanVFD.Setup | DAP-Min | 2645 | 244 |  |  | Low Pressure Limit 1 | 1714 | 122 | 7038 | FALSE | TRUE | FALSE | 4 | Float | 100ths | in wc | 507:58 | 0.01 | 1 |  |  | 100ths | Pa | 507:53 | 2.5 | 250 |  |  |  |  | 3
Value |  |  | Views.Details.FanVFD.Setup | Discharge Air Static Pressure Alarm Delay | 2644 | 228 |  | Views.Details.FanVFD.Setup | DAP-AlmDly | 2645 | 245 |  |  | Time | 1709 | 342 | 7040 | FALSE | TRUE | FALSE | 18 | UnsignedInteger | 1s | seconds | 507:73 | 0 | 600 |  |  | 1s | seconds | 507:73 | 0 | 600 |  |  |  |  | 3
Value |  |  | Views.Details.FanVFD.Setup | COBP Occupied Heating Enabled | 1675 | 1456 |  | Views.Details.FanVFD.Setup | HtgOcc-En | 1709 | 239 |  |  | COBP Occupied Heating Enabled | 1675 | 1456 | 7055 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 13
Group |  | TRUE | Views.Details.FanVFD.Service | Service | 1714 | 27 |  | Views.Details.FanVFD.Service | Service | 1709 | 406
Value |  |  | Views.Details.FanVFD.Service | Fan % Command | 1675 | 169 |  | Views.Details.FanVFD.Service | FanVFD | 1709 | 67 |  |  | Fan % Command | 1675 | 169 | 7001 | TRUE | FALSE | FALSE | 4 | Float | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 | [6 empty] | 3
Value |  |  | Views.Details.FanVFD.Service | Duct Static Pressure | 1675 | 183 |  | Views.Details.FanVFD.Service | DctPrs | 1709 | 81 |  |  | Duct Static Pressure | 1675 | 183 | 7015 | TRUE | FALSE | FALSE | 4 | Float | 100ths | in wc | 507:58 |  |  |  |  | 100ths | kPa | 507:54 | [6 empty] | 3
Value |  |  | Views.Details.FanVFD.Service | Duct Pressure Setpoint | 1675 | 184 |  | Views.Details.FanVFD.Service | DctPrs-Sp | 1709 | 82 |  |  | Duct Pressure Setpoint | 1675 | 184 | 7016 | TRUE | TRUE | FALSE | 4 | Float | 100ths | in wc | 507:58 | 0 | 5 |  |  | 100ths | kPa | 507:54 | 0 | 1.25 |  |  |  |  | 3
Value |  |  | Views.Details.FanVFD.Service | VAV Operating Cooling Supply Air Temp Setpoint | 1675 | 140 |  | Views.Details.FanVFD.Service | OprVAVClg-Sp | 1709 | 122 |  |  | SZ VAV Operating Cooling Setpoint | 1675 | 648 | 7050 | TRUE | FALSE | FALSE | 4 | Float | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 | [6 empty] | 4
Value |  |  | Views.Details.FanVFD.Service | Supply Air Temperature | 1675 | 182 |  | Views.Details.FanVFD.Service | SAT | 1709 | 80 |  |  | Supply Air Temperature | 1675 | 182 | 7014 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 3
Value |  |  | Views.Details.FanVFD.Service | Staged Cooling Command | 1675 | 628 |  | Views.Details.FanVFD.Service | StgClgCmd | 1709 | 648 |  |  | Staged Cooling Command | 1675 | 628 | 7047 | TRUE | FALSE | FALSE | 4 | Float | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 | [6 empty] | 4
Value |  |  | Views.Details.FanVFD.Service | Cooling Status | 1675 | 69 |  | Views.Details.FanVFD.Service | Clg-S | 1709 | 93 |  |  | Cooling Status | 1675 | 69 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  | SE RTU Cooling Control Status | 1740 | [5 empty] | SE RTU Cooling Control Status | 1740 | [5 empty] | 0 = Off-Idle 1 = Thermostat Cooling 2 = Unoccupied Cooling 3 = Occupied Cooling ... | 4
Value |  |  | Views.Details.FanVFD.Service | Econ Free Cooling Available | 1675 | 52 |  | Views.Details.FanVFD.Service | Econ-Free | 1709 | 283 |  |  | Econ Free Cooling Available | 1675 | 52 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 19
Value |  |  | Views.Details.FanVFD.Service | Compressor Stage Command 1 | 1714 | 145 |  | Views.Details.FanVFD.Service | C1 | 1709 | 127 |  |  | Compressor Stage Command | 1675 | 84 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 5
Value |  |  | Views.Details.FanVFD.Service | Compressor Stage Command 2 | 1714 | 146 |  | Views.Details.FanVFD.Service | C2 | 1709 | 128 |  |  | Compressor Stage Command | 1675 | 84 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 7
Value |  |  | Views.Details.FanVFD.Service | Compressor Stage Command 3 | 1714 | 147 |  | Views.Details.FanVFD.Service | C3 | 1709 | 129 |  |  | Compressor Stage Command | 1675 | 84 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 9
Value |  |  | Views.Details.FanVFD.Service | Compressor Stage Command 4 | 1714 | 148 |  | Views.Details.FanVFD.Service | C4 | 1709 | 130 |  |  | Compressor Stage Command | 1675 | 84 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 11
Value |  |  | Views.Details.FanVFD.Service | VAV Operating Heating Setpoint | 1675 | 208 |  | Views.Details.FanVFD.Service | VAVOprHtg-Sp | 1709 | 243 |  |  | VAV Operating Heating Setpoint | 1675 | 208 | 7019 | TRUE | FALSE | FALSE | 4 | Float | 100ths | deg F | 507:64 |  |  |  |  | 100ths | deg C | 507:62 | [6 empty] | 13
Value |  |  | Views.Details.FanVFD.Service | Staged Heating Command | 1675 | 629 |  | Views.Details.FanVFD.Service | StgHtgCmd | 1709 | 649 |  |  | Staged Heating Command | 1675 | 629 | 7045 | TRUE | FALSE | FALSE | 4 | Float | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 | [6 empty] | 13
Value |  |  | Views.Details.FanVFD.Service | Operational Space Temperature | 1675 | 15 |  | Views.Details.FanVFD.Service | OprST | 1709 | 28 |  |  | Operational Space Temperature | 1675 | 15 | 7006 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 25
Value |  |  | Views.Details.FanVFD.Service | Heating Status | 1675 | 106 |  | Views.Details.FanVFD.Service | Htg-S | 1709 | 225 |  |  | Heating Status | 1675 | 106 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  | SE RTU Heating Control Status | 1742 | [5 empty] | SE RTU Heating Control Status | 1742 | [5 empty] | 0 = Off-Idle 1 = On-Defrost 2 = SAT Tempering 3 = Morning Warmup ... | 13
Value |  |  | Views.Details.FanVFD.Service | Heating Stage Command 1 | 1714 | 149 |  | Views.Details.FanVFD.Service | H1 | 1709 | 251 |  |  | Heat Stage Command | 1675 | 111 | 7000 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 15
Value |  |  | Views.Details.FanVFD.Service | Heating Stage Command 2 | 1714 | 150 |  | Views.Details.FanVFD.Service | H2 | 1709 | 252 |  |  | Heat Stage Command | 1675 | 111 | 7000 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 16
Value |  |  | Views.Details.FanVFD.Service | Heating Stage Command 3 | 1714 | 151 |  | Views.Details.FanVFD.Service | H3 | 1709 | 253 |  |  | Heat Stage Command | 1675 | 111 | 7000 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 17
Value |  |  | Views.Details.FanVFD.Service | VAV Box Heat Command | 1675 | 211 |  | Views.Details.FanVFD.Service | VAV Box | 1709 | 246 |  |  | VAV Box Heat Command | 1675 | 211 | 7022 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 13
Group |  | FALSE | Views.Details.Single Zone VAV | Single Zone VAV | 1714 | 195 |  | Views.Details.SZ VAV | SZ VAV | 1709 | 638 | York RTU.SZ VAV Enabled:Present Value <> Off
Group |  | TRUE | Views.Details.Single Zone VAV.Setup | Setup | 1714 | 29 |  | Views.Details.SZ VAV.Setup | Setup | 1709 | 408
Value |  |  | Views.Details.Single Zone VAV.Setup | SZ VAV Enabled | 1675 | 491 |  | Views.Details.SZ VAV.Setup | SZVAVEn | 1709 | 623 |  |  | SZ VAV Enabled | 1675 | 491 | 7020 | TRUE | TRUE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 1
Value |  |  | Views.Details.Single Zone VAV.Setup | SZ VAV Minimum Fan Speed | 1675 | 627 |  | Views.Details.SZ VAV.Setup | SZVAVMinFanSpd | 1709 | 647 |  |  | SZ VAV Minimum Fan Speed | 1675 | 627 | 7037 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 3
Value |  |  | Views.Details.Single Zone VAV.Setup | SZ VAV Occupied Cooling Setpoint | 1675 | 644 |  | Views.Details.SZ VAV.Setup | SZVAVClgOcc-Sp | 1709 | 656 |  |  | SZ VAV Occupied Cooling Setpoint | 1675 | 644 | 7048 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 45 | 98 |  |  | 1s | deg C | 507:62 | 7 | 36 |  |  |  |  | 4
Value |  |  | Views.Details.Single Zone VAV.Setup | SZ VAV Unoccupied Cooling Setpoint | 1675 | 646 |  | Views.Details.SZ VAV.Setup | SZVAVClgUnocc-Sp | 1709 | 657 |  |  | SZ VAV Unoccupied Cooling Setpoint | 1675 | 646 | 7049 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 45 | 98 |  |  | 1s | deg C | 507:62 | 7 | 36 |  |  |  |  | 4
Value |  |  | Views.Details.Single Zone VAV.Setup | SZ VAV Occupied Heating Setpoint | 1675 | 643 |  | Views.Details.SZ VAV.Setup | SZVAVHtgOcc-Sp | 1709 | 658 |  |  | SZ VAV Occupied Heating Setpoint | 1675 | 643 | 7047 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 46 | 99 |  |  | 1s | deg C | 507:62 | 8 | 37 |  |  |  |  | 13
Value |  |  | Views.Details.Single Zone VAV.Setup | SZ VAV Unoccupied Heating Setpoint | 1675 | 645 |  | Views.Details.SZ VAV.Setup | SZVAVHtgUnocc-Sp | 1709 | 659 |  |  | SZ VAV Unoccupied Heating Setpoint | 1675 | 645 | 7048 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 45 | 98 |  |  | 1s | deg C | 507:62 | 7 | 36 |  |  |  |  | 13
Value |  |  | Views.Details.Single Zone VAV.Setup | DAT Max Heating SP | 1675 | 492 |  | Views.Details.SZ VAV.Setup | DATMaxHtgSP | 1709 | 624 |  |  | DAT Max Heating SP | 1675 | 492 | 7043 | TRUE | TRUE | FALSE | 4 | Float | 10ths | deg F | 507:64 | 80 | 110 |  |  | 10ths | deg C | 507:62 | 26.6 | 43.4 |  |  |  |  | 13
Value |  |  | Views.Details.Single Zone VAV.Setup | DAT Satisfied SP | 1675 | 493 |  | Views.Details.SZ VAV.Setup | DATSatSP | 1709 | 625 |  |  | DAT Satisfied SP | 1675 | 493 | 7044 | TRUE | TRUE | FALSE | 4 | Float | 10ths | deg F | 507:64 | 65 | 75 |  |  | 10ths | deg C | 507:62 | 18.3 | 23.9 |  |  |  |  | 13
Value |  |  | Views.Details.Single Zone VAV.Setup | VAV Cooling Supply Air Temp Upper Setpoint | 1675 | 137 |  | Views.Details.SZ VAV.Setup | SATUp-Sp | 1709 | 119 |  |  | VAV Cooling Supply Air Temp Upper Setpoint | 1675 | 137 | 7029 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 41 | 70 |  |  | 1s | deg C | 507:62 | 5 | 21 |  |  |  |  | 4
Value |  |  | Views.Details.Single Zone VAV.Setup | VAV Cooling Supply Air Temp Lower Setpoint | 1675 | 138 |  | Views.Details.SZ VAV.Setup | SATLo-Sp | 1709 | 120 |  |  | VAV Cooling Supply Air Temp Lower Setpoint | 1675 | 138 | 7030 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 40 | 69 |  |  | 1s | deg C | 507:62 | 4 | 20 |  |  |  |  | 4
Group |  | TRUE | Views.Details.Single Zone VAV.Service | Service | 1714 | 27 |  | Views.Details.SZ VAV.Service | Service | 1709 | 406
Value |  |  | Views.Details.Single Zone VAV.Service | VAV Operating Cooling Supply Air Temp Setpoint | 1675 | 140 |  | Views.Details.SZ VAV.Service | OprSZVAVClg-Sp | 1709 | 660 |  |  | SZ VAV Operating Cooling Setpoint | 1675 | 648 | 7050 | TRUE | FALSE | FALSE | 4 | Float | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 | [6 empty] | 4
Value |  |  | Views.Details.Single Zone VAV.Service | SZ VAV Operating Heating Setpoint | 1675 | 647 |  | Views.Details.SZ VAV.Service | OprSZVAVHtg-Sp | 1709 | 661 |  |  | VAV Operating Heating Setpoint | 1675 | 208 | 7019 | TRUE | FALSE | FALSE | 4 | Float | 100ths | deg F | 507:64 |  |  |  |  | 100ths | deg C | 507:62 | [6 empty] | 13
Value |  |  | Views.Details.Single Zone VAV.Service | Operating Heating Discharge Air Temp Setpoint | 2644 | 40 |  | Views.Details.SZ VAV.Service | OprHtgDAT-SP | 2645 | 359 |  |  | SZ VAV Operating Heating Setpoint | 1675 | 647 | 7049 | TRUE | FALSE | FALSE | 4 | Float | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 | [6 empty] | 13
Value |  |  | Views.Details.Single Zone VAV.Service | SZ VAV Cooling Load | 1675 | 744 |  | Views.Details.SZ VAV.Service | SZVAVClgLd | 1709 | 665 |  |  | SZ VAV Cooling Load | 1675 | 744 | 7053 | TRUE | FALSE | FALSE | 4 | Float | 10ths | % | 507:98 |  |  |  |  | 10ths | % | 507:98 | [6 empty] | 4
Value |  |  | Views.Details.Single Zone VAV.Service | SZ VAV Heating Load | 1675 | 745 |  | Views.Details.SZ VAV.Service | SZVAVHtgLd | 1709 | 666 |  |  | SZ VAV Heating Load | 1675 | 745 | 7050 | TRUE | FALSE | FALSE | 4 | Float | 10ths | % | 507:98 |  |  |  |  | 10ths | % | 507:98 | [6 empty] | 13
Value |  |  | Views.Details.Single Zone VAV.Service | Operational Space Temperature | 1675 | 15 |  | Views.Details.SZ VAV.Service | OprST | 1709 | 28 |  |  | Operational Space Temperature | 1675 | 15 | 7006 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 25
Value |  |  | Views.Details.Single Zone VAV.Service | Supply Air Temperature | 1675 | 182 |  | Views.Details.SZ VAV.Service | SAT | 1709 | 80 |  |  | Supply Air Temperature | 1675 | 182 | 7014 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 3
Value |  |  | Views.Details.Single Zone VAV.Service | Fan % Command | 1675 | 169 |  | Views.Details.SZ VAV.Service | FanVFD | 1709 | 67 |  |  | Fan % Command | 1675 | 169 | 7001 | TRUE | FALSE | FALSE | 4 | Float | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 | [6 empty] | 3
Value |  |  | Views.Details.Single Zone VAV.Service | Economizer Damper % Command | 1675 | 51 |  | Views.Details.SZ VAV.Service | Econ | 1709 | 282 |  |  | Economizer Damper % Command | 1675 | 51 | 7001 | TRUE | FALSE | FALSE | 4 | Float | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 | [6 empty] | 19
Value |  |  | Views.Details.Single Zone VAV.Service | Compressor Stage Command 1 | 1714 | 145 |  | Views.Details.SZ VAV.Service | C1 | 1709 | 127 |  |  | Compressor Stage Command | 1675 | 84 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 5
Value |  |  | Views.Details.Single Zone VAV.Service | Compressor Stage Command 2 | 1714 | 146 |  | Views.Details.SZ VAV.Service | C2 | 1709 | 128 |  |  | Compressor Stage Command | 1675 | 84 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 7
Value |  |  | Views.Details.Single Zone VAV.Service | Compressor Stage Command 3 | 1714 | 147 |  | Views.Details.SZ VAV.Service | C3 | 1709 | 129 |  |  | Compressor Stage Command | 1675 | 84 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 9
Value |  |  | Views.Details.Single Zone VAV.Service | Compressor Stage Command 4 | 1714 | 148 |  | Views.Details.SZ VAV.Service | C4 | 1709 | 130 |  |  | Compressor Stage Command | 1675 | 84 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 11
Group |  | FALSE | Views.Details.Hot Gas Reheat | Hot Gas Reheat | 1714 | 13 |  | Views.Details.HGR | HGR | 1709 | 324 | York RTU.Hot Gas Reheat.HGR-Inst:Present Value = 1
Group |  | TRUE | Views.Details.Hot Gas Reheat.Setup | Setup | 1714 | 29 |  | Views.Details.HGR.Setup | Setup | 1709 | 408
Value |  |  | Views.Details.Hot Gas Reheat.Setup | Hot Gas Reheat Enabled For Operation | 1675 | 249 |  | Views.Details.HGR.Setup | HGR-En | 1709 | 323 |  |  | Hot Gas Reheat Enabled For Operation | 1675 | 249 | 7000 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 20
Value |  |  | Views.Details.Hot Gas Reheat.Setup | Hot Gas Reheat Alternate Operation Enabled | 1675 | 253 |  | Views.Details.HGR.Setup | HGRAlt-En | 1709 | 327 |  |  | Hot Gas Reheat Alternate Operation Enabled | 1675 | 253 | 7004 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 20
Value |  |  | Views.Details.Hot Gas Reheat.Setup | Hot Gas Reheat Alternate Operation Writeable | 1675 | 254 |  | Views.Details.HGR.Setup | HGRAltWrite | 1709 | 328 |  |  | Hot Gas Reheat Alternate Operation Writeable | 1675 | 254 | 7005 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 20
Value |  |  | Views.Details.Hot Gas Reheat.Setup | Hot Gas Reheat Humidity Setpoint | 1675 | 252 |  | Views.Details.HGR.Setup | HGRHum-Sp | 1709 | 326 |  |  | Hot Gas Reheat Humidity Setpoint | 1675 | 252 | 7003 | TRUE | TRUE | FALSE | 4 | Float | 1s | %RH | 507:29 | 0 | 100 |  |  | 1s | %RH | 507:29 | 0 | 100 |  |  |  |  | 20
Value |  |  | Views.Details.Hot Gas Reheat.Setup | HGR Enabled for Unoccupied Operation | 1675 | 603 |  | Views.Details.HGR.Setup | HGRUnocc-En | 1709 | 643 |  |  | HGR Enabled for Unoccupied Operation | 1675 | 603 | 7007 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 20
Value |  |  | Views.Details.Hot Gas Reheat.Setup | HGR Unoccupied Humidity Setpoint | 1675 | 602 |  | Views.Details.HGR.Setup | HGRUnoccHum-SP | 1709 | 642 |  |  | HGR Unoccupied Humidity Setpoint | 1675 | 602 | 7006 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 20
Value |  |  | Views.Details.Hot Gas Reheat.Setup | HGR Humidity Setpoint Differential | 1675 | 872 |  | Views.Details.HGR.Setup | HGR-Diff | 1709 | 669 |  |  | HGR Humidity Setpoint Differential | 1675 | 872 | 7008 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 1 | 10 |  |  | 1s | % | 507:98 | 1 | 10 |  |  |  |  | 20
Value |  |  | Views.Details.Hot Gas Reheat.Setup | Hybrid Mode | 1714 | 251 |  | Views.Details.HGR.Setup | Hybrid Mode | 1714 | 251 |  |  | Aux Mode | 1675 | 791 | 7009 | TRUE | TRUE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 20
Value |  |  | Views.Details.Hot Gas Reheat.Setup | Use DFS For Dehum | 1714 | 224 |  | Views.Details.HGR.Setup | Use DFS For Dehum | 1714 | 224 |  |  | Use DFS For Dehum | 1714 | 224 | 7010 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 20
Value |  |  | Views.Details.Hot Gas Reheat.Setup | Neutral Air ModHGR Enable | 1714 | 281 |  | Views.Details.HGR.Setup | NeuAirModHGR-En | 1709 | 792 |  |  | Neutral Air ModHGR Enable | 1714 | 281 | 7032 | TRUE | TRUE | FALSE | 9 | MultiState |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 | [5 empty] | 0 = Disable 1 = Enable | 20
Value |  |  | Views.Details.Hot Gas Reheat.Setup | Neutral Air ModHGR Offset | 1714 | 282 |  | Views.Details.HGR.Setup | NeuAirModHGR-Off | 1709 | 793 |  |  | Neutral Air ModHGR Offset | 1714 | 282 | 7033 | TRUE | TRUE | FALSE | 4 | Float | 1s | delta deg F | 507:120 | -10 | 10 |  |  | 1s | delta deg C | 507:359 | -6 | 6 |  |  |  |  | 20
Group |  | TRUE | Views.Details.Hot Gas Reheat.Service | Service | 1714 | 27 |  | Views.Details.HGR.Service | Service | 1709 | 406
Value |  |  | Views.Details.Hot Gas Reheat.Service | Staged Cooling Command | 1675 | 628 |  | Views.Details.HGR.Service | StgClgCmd | 1709 | 648 |  |  | Staged Cooling Command | 1675 | 628 | 7047 | TRUE | FALSE | FALSE | 4 | Float | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 | [6 empty] | 4
Value |  |  | Views.Details.Hot Gas Reheat.Service | CV Operating Cooling Setpoint | 1675 | 144 |  | Views.Details.HGR.Service | OprCVClg-Sp | 1709 | 125 |  |  | CV Operating Cooling Setpoint | 1675 | 144 | 7035 | TRUE | FALSE | FALSE | 4 | Float | 100ths | deg F | 507:64 |  |  |  |  | 100ths | deg C | 507:62 | [6 empty] | 4
Value |  |  | Views.Details.Hot Gas Reheat.Service | Operational Space Temperature | 1675 | 15 |  | Views.Details.HGR.Service | OprST | 1709 | 28 |  |  | Operational Space Temperature | 1675 | 15 | 7006 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 25
Value |  |  | Views.Details.Hot Gas Reheat.Service | Hot Gas Reheat Humidity Setpoint | 1675 | 252 |  | Views.Details.HGR.Service | HGRHum-Sp | 1709 | 326 |  |  | Hot Gas Reheat Humidity Setpoint | 1675 | 252 | 7003 | TRUE | TRUE | FALSE | 4 | Float | 1s | %RH | 507:29 | 0 | 100 |  |  | 1s | %RH | 507:29 | 0 | 100 |  |  |  |  | 20
Value |  |  | Views.Details.Hot Gas Reheat.Service | Operational Space Humidity | 1675 | 23 |  | Views.Details.HGR.Service | OprSH | 1709 | 39 |  |  | Operational Space Humidity | 1675 | 23 | 7017 | TRUE | FALSE | FALSE | 4 | Float | 10ths | %RH | 507:29 |  |  |  |  | 10ths | %RH | 507:29 | [6 empty] | 25
Value |  |  | Views.Details.Hot Gas Reheat.Service | Hot Gas Reheat Status | 1675 | 251 |  | Views.Details.HGR.Service | HGR-S | 1709 | 325 |  |  | Hot Gas Reheat Status | 1675 | 251 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  | SE RTU Hot Gas Reheat | 1744 | [5 empty] | SE RTU Hot Gas Reheat | 1744 | [5 empty] | 0 = Off-Idle 1 = On-Normal Command 2 = On-Alternate Operation Command 3 = Off-Disabled | 20
Value |  |  | Views.Details.Hot Gas Reheat.Service | Hot Gas Reheat Command | 1675 | 250 |  | Views.Details.HGR.Service | ModHGR | 1709 | 737 |  |  | Hot Gas Reheat Command | 1675 | 250 | 7027 | TRUE | FALSE | FALSE | 4 | Float | 10ths | % | 507:98 |  |  |  |  | 10ths | % | 507:98 | [6 empty] | 20
Value |  |  | Views.Details.Hot Gas Reheat.Service | Hot Gas Reheat Command | 1675 | 250 |  | Views.Details.HGR.Service | HGR | 1709 | 324 |  |  | Hot Gas Reheat Command | 1675 | 250 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 20
Value |  |  | Views.Details.Hot Gas Reheat.Service | Compressor Stage Command 1 | 1714 | 145 |  | Views.Details.HGR.Service | C1 | 1709 | 127 |  |  | Compressor Stage Command | 1675 | 84 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 5
Value |  |  | Views.Details.Hot Gas Reheat.Service | Compressor Stage Command 2 | 1714 | 146 |  | Views.Details.HGR.Service | C2 | 1709 | 128 |  |  | Compressor Stage Command | 1675 | 84 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 7
Value |  |  | Views.Details.Hot Gas Reheat.Service | Compressor Stage Command 3 | 1714 | 147 |  | Views.Details.HGR.Service | C3 | 1709 | 129 |  |  | Compressor Stage Command | 1675 | 84 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 9
Value |  |  | Views.Details.Hot Gas Reheat.Service | Compressor Stage Command 4 | 1714 | 148 |  | Views.Details.HGR.Service | C4 | 1709 | 130 |  |  | Compressor Stage Command | 1675 | 84 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 11
Value |  |  | Views.Details.Hot Gas Reheat.Service | Modulating Compressor Output | 2644 | 292 |  | Views.Details.HGR.Service | ModCompOut | 2645 | 311 |  |  | Modulating Compressor Output | 2644 | 292 | 7067 | TRUE | FALSE | FALSE | 4 | Float | 10ths | % | 507:98 | 0 | 100 |  |  | 10ths | % | 507:98 | 0 | 100 |  |  |  |  | 4
Value |  |  | Views.Details.Hot Gas Reheat.Service | Space Humidity RAH Input | 1675 | 25 |  | Views.Details.HGR.Service | RAH | 1709 | 41 |  |  | Space Humidity RAH Input | 1675 | 25 | 7019 | TRUE | FALSE | FALSE | 4 | Float | 10ths | %RH | 507:29 |  |  |  |  | 10ths | %RH | 507:29 | [6 empty] | 25
Value |  |  | Views.Details.Hot Gas Reheat.Service | Operational Outdoor Air Temperature | 1675 | 36 |  | Views.Details.HGR.Service | OprOAT | 1709 | 52 |  |  | Operational Outdoor Air Temperature | 1675 | 36 | 7000 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 26
Group |  | FALSE | Views.Details.Mod Hot Gas Reheat | Mod Hot Gas Reheat | 1714 | 252 |  | Views.Details.ModHGR | ModHGR | 1709 | 737 | York RTU.Hot Gas Reheat.HGR-Inst:Present Value > 1
Group |  | TRUE | Views.Details.Mod Hot Gas Reheat.Setup | Setup | 1714 | 29 |  | Views.Details.ModHGR.Setup | Setup | 1709 | 408
Value |  |  | Views.Details.Mod Hot Gas Reheat.Setup | Hot Gas Reheat Enabled For Operation | 1675 | 249 |  | Views.Details.ModHGR.Setup | HGR-En | 1709 | 323 |  |  | Hot Gas Reheat Enabled For Operation | 1675 | 249 | 7000 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 20
Value |  |  | Views.Details.Mod Hot Gas Reheat.Setup | Dehumidify In Satisfied | 1714 | 228 |  | Views.Details.ModHGR.Setup | SatisfiedDehum | 1709 | 726 |  |  | Dehumidify In Satisfied | 1714 | 228 | 7012 | TRUE | TRUE | FALSE | 9 | MultiState |  | False/True | 1701 | [5 empty] | False/True | 1701 | [5 empty] | 0 = False 1 = True | 20
Value |  |  | Views.Details.Mod Hot Gas Reheat.Setup | Hot Gas Reheat Humidity Setpoint | 1675 | 252 |  | Views.Details.ModHGR.Setup | HGRHum-Sp | 1709 | 326 |  |  | Hot Gas Reheat Humidity Setpoint | 1675 | 252 | 7003 | TRUE | TRUE | FALSE | 4 | Float | 1s | %RH | 507:29 | 0 | 100 |  |  | 1s | %RH | 507:29 | 0 | 100 |  |  |  |  | 20
Value |  |  | Views.Details.Mod Hot Gas Reheat.Setup | HGR Enabled for Unoccupied Operation | 1675 | 603 |  | Views.Details.ModHGR.Setup | HGRUnocc-En | 1709 | 643 |  |  | HGR Enabled for Unoccupied Operation | 1675 | 603 | 7007 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 20
Value |  |  | Views.Details.Mod Hot Gas Reheat.Setup | HGR Unoccupied Humidity Setpoint | 1675 | 602 |  | Views.Details.ModHGR.Setup | HGRUnoccHum-SP | 1709 | 642 |  |  | HGR Unoccupied Humidity Setpoint | 1675 | 602 | 7006 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 20
Value |  |  | Views.Details.Mod Hot Gas Reheat.Setup | HGR Humidity Setpoint Differential | 1675 | 872 |  | Views.Details.ModHGR.Setup | HGR-Diff | 1709 | 669 |  |  | HGR Humidity Setpoint Differential | 1675 | 872 | 7008 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 1 | 10 |  |  | 1s | % | 507:98 | 1 | 10 |  |  |  |  | 20
Value |  |  | Views.Details.Mod Hot Gas Reheat.Setup | Use DFS For Dehum | 1714 | 224 |  | Views.Details.ModHGR.Setup | Use DFS For Dehum | 1714 | 224 |  |  | Use DFS For Dehum | 1714 | 224 | 7010 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 20
Value |  |  | Views.Details.Mod Hot Gas Reheat.Setup | VAV Cooling Supply Air Temp Upper Setpoint | 1675 | 137 |  | Views.Details.ModHGR.Setup | SATUp-Sp | 1709 | 119 |  |  | VAV Cooling Supply Air Temp Upper Setpoint | 1675 | 137 | 7019 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 41 | 70 |  |  | 1s | deg C | 507:62 | 5 | 21 |  |  |  |  | 20
Value |  |  | Views.Details.Mod Hot Gas Reheat.Setup | VAV Cooling Supply Air Temp Lower Setpoint | 1675 | 138 |  | Views.Details.ModHGR.Setup | SATLo-Sp | 1709 | 120 |  |  | VAV Cooling Supply Air Temp Lower Setpoint | 1675 | 138 | 7020 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 40 | 69 |  |  | 1s | deg C | 507:62 | 4 | 20 |  |  |  |  | 20
Value |  |  | Views.Details.Mod Hot Gas Reheat.Setup | VAV Supply Air Temp Reset Setpoint | 1675 | 139 |  | Views.Details.ModHGR.Setup | SATRst-Sp | 1709 | 121 |  |  | VAV Supply Air Temp Reset Setpoint | 1675 | 139 | 7021 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 40 | 85 |  |  | 1s | deg C | 507:62 | 4 | 30 |  |  |  |  | 20
Value |  |  | Views.Details.Mod Hot Gas Reheat.Setup | Dehum Evap Low Setpoint | 1714 | 229 |  | Views.Details.ModHGR.Setup | DehumEvapLowSp | 1709 | 725 |  |  | Dehum Evap Low Setpoint | 1714 | 229 | 7018 | TRUE | TRUE | FALSE | 4 | Float | 10ths | deg F | 507:64 | 40 |  |  | 7017 | 10ths | deg C | 507:62 | 4 |  |  | 7017 |  |  | 20
Value |  |  | Views.Details.Mod Hot Gas Reheat.Setup | Occupied Cooling Setpoint | 1675 | 562 |  | Views.Details.ModHGR.Setup | ClgOcc-Sp | 1709 | 123 |  |  | Occupied Cooling Setpoint | 1675 | 562 | 7022 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 45 | 98 |  |  | 1s | deg C | 507:62 | 7 | 36 |  |  |  |  | 20
Value |  |  | Views.Details.Mod Hot Gas Reheat.Setup | Dehumidification % Command | 1714 | 234 |  | Views.Details.ModHGR.Setup | Dehum%Cmd | 1709 | 731 |  |  | Dehumidification % Command | 1714 | 234 | 7011 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 20
Value |  |  | Views.Details.Mod Hot Gas Reheat.Setup | HGR Mod Valve Min Setpoint | 1714 | 274 |  | Views.Details.ModHGR.Setup | HGRModVlvMinSP | 1709 | 783 |  |  | Min Heating Setpoint | 1675 | 1448 | 7014 | TRUE | TRUE | FALSE | 4 | Float | 10ths | % | 507:98 | 0 | 100 |  |  | 10ths | % | 507:98 | 0 | 100 |  |  |  |  | 20
Value |  |  | Views.Details.Mod Hot Gas Reheat.Setup | HGR Mod Valve Max Setpoint | 1714 | 275 |  | Views.Details.ModHGR.Setup | HGRModVlvMaxSP | 1709 | 782 |  |  | Max Heating Setpoint | 1675 | 514 | 7013 | TRUE | TRUE | FALSE | 4 | Float | 10ths | % | 507:98 | 0 | 100 |  |  | 10ths | % | 507:98 | 0 | 100 |  |  |  |  | 20
Value |  |  | Views.Details.Mod Hot Gas Reheat.Setup | Condenser Fan 2 OAT Cutout Setpoint | 1714 | 235 |  | Views.Details.ModHGR.Setup | CondFan2OATCutoutSP | 1709 | 732 |  |  | Condenser Fan 2 OAT Cutout Setpoint | 1714 | 235 | 7023 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 50 | 80 |  |  | 1s | deg C | 507:62 | 10 | 27 |  |  |  |  | 20
Value |  |  | Views.Details.Mod Hot Gas Reheat.Setup | Condenser Fan 2 Max Pos Cutout Enable | 1714 | 253 |  | Views.Details.ModHGR.Setup | CondFan2MaxPosCutoutEn | 1709 | 753 |  |  | Condenser Fan 2 Max Pos Cutout Enable | 1714 | 253 | 7030 | TRUE | TRUE | FALSE | 9 | MultiState |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 | [5 empty] | 0 = Disable 1 = Enable | 20
Value |  |  | Views.Details.Mod Hot Gas Reheat.Setup | Modulating HGR Valve Full Open Allowed | 1714 | 231 |  | Views.Details.ModHGR.Setup | ModHGRFullOpenAllowed | 1709 | 728 |  |  | Modulating HGR Valve Full Open Allowed | 1714 | 231 | 7024 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 20
Value |  |  | Views.Details.Mod Hot Gas Reheat.Setup | Use OprST for HGR | 1714 | 272 |  | Views.Details.ModHGR.Setup | UseOprSTforHGR | 1709 | 777 |  |  | Use OprST for HGR | 1714 | 272 | 7031 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 20
Group |  | TRUE | Views.Details.Mod Hot Gas Reheat.Service | Service | 1714 | 27 |  | Views.Details.ModHGR.Service | Service | 1709 | 406
Value |  |  | Views.Details.Mod Hot Gas Reheat.Service | Staged Cooling Command | 1675 | 628 |  | Views.Details.ModHGR.Service | StgClgCmd | 1709 | 648 |  |  | Staged Cooling Command | 1675 | 628 | 7047 | TRUE | FALSE | FALSE | 4 | Float | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 | [6 empty] | 4
Value |  |  | Views.Details.Mod Hot Gas Reheat.Service | CV Operating Cooling Setpoint | 1675 | 144 |  | Views.Details.ModHGR.Service | OprCVClg-Sp | 1709 | 125 |  |  | CV Operating Cooling Setpoint | 1675 | 144 | 7035 | TRUE | FALSE | FALSE | 4 | Float | 100ths | deg F | 507:64 |  |  |  |  | 100ths | deg C | 507:62 | [6 empty] | 4
Value |  |  | Views.Details.Mod Hot Gas Reheat.Service | Operational Space Temperature | 1675 | 15 |  | Views.Details.ModHGR.Service | OprST | 1709 | 28 |  |  | Operational Space Temperature | 1675 | 15 | 7006 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 25
Value |  |  | Views.Details.Mod Hot Gas Reheat.Service | Operational Evap Temperature Sp | 1714 | 232 |  | Views.Details.ModHGR.Service | OprEvapTempSp | 1709 | 729 |  |  | Operational Evap Temperature Sp | 1714 | 232 | 7015 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 | 0 | 100 |  |  | 10ths | deg C | 507:62 | 0 | 100 |  |  |  |  | 20
Value |  |  | Views.Details.Mod Hot Gas Reheat.Service | Evaporator Coil Temp | 1675 | 100 |  | Views.Details.ModHGR.Service | Evaporator Coil Temp | 1675 | 100 |  |  | Evaporator Coil Temp | 1675 | 100 | 7026 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 20
Value |  |  | Views.Details.Mod Hot Gas Reheat.Service | Hot Gas Reheat Humidity Setpoint | 1675 | 252 |  | Views.Details.ModHGR.Service | HGRHum-Sp | 1709 | 326 |  |  | Hot Gas Reheat Humidity Setpoint | 1675 | 252 | 7003 | TRUE | TRUE | FALSE | 4 | Float | 1s | %RH | 507:29 | 0 | 100 |  |  | 1s | %RH | 507:29 | 0 | 100 |  |  |  |  | 20
Value |  |  | Views.Details.Mod Hot Gas Reheat.Service | Operational Space Humidity | 1675 | 23 |  | Views.Details.ModHGR.Service | OprSH | 1709 | 39 |  |  | Operational Space Humidity | 1675 | 23 | 7017 | TRUE | FALSE | FALSE | 4 | Float | 10ths | %RH | 507:29 |  |  |  |  | 10ths | %RH | 507:29 | [6 empty] | 25
Value |  |  | Views.Details.Mod Hot Gas Reheat.Service | Hot Gas Reheat Status | 1675 | 251 |  | Views.Details.ModHGR.Service | HGR-S | 1709 | 325 |  |  | Hot Gas Reheat Status | 1675 | 251 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  | SE RTU Hot Gas Reheat | 1744 | [5 empty] | SE RTU Hot Gas Reheat | 1744 | [5 empty] | 0 = Off-Idle 1 = On-Normal Command 2 = On-Alternate Operation Command 3 = Off-Disabled | 20
Value |  |  | Views.Details.Mod Hot Gas Reheat.Service | Operational HGR Temperature Sp | 1714 | 233 |  | Views.Details.ModHGR.Service | OprHGRTempSp | 1709 | 730 |  |  | Operational HGR Temperature Sp | 1714 | 233 | 7016 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 | 0 | 100 |  |  | 10ths | deg C | 507:62 | 0 | 100 |  |  |  |  | 20
Value |  |  | Views.Details.Mod Hot Gas Reheat.Service | Supply Air Temperature | 1675 | 182 |  | Views.Details.ModHGR.Service | SAT | 1709 | 80 |  |  | Supply Air Temperature | 1675 | 182 | 7028 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 20
Value |  |  | Views.Details.Mod Hot Gas Reheat.Service | Hot Gas Reheat Command | 1675 | 250 |  | Views.Details.ModHGR.Service | ModHGR | 1709 | 737 |  |  | Hot Gas Reheat Command | 1675 | 250 | 7027 | TRUE | FALSE | FALSE | 4 | Float | 10ths | % | 507:98 |  |  |  |  | 10ths | % | 507:98 | [6 empty] | 20
Value |  |  | Views.Details.Mod Hot Gas Reheat.Service | Hot Gas Reheat Bleed Valve Command | 2644 | 238 |  | Views.Details.ModHGR.Service | Hot Gas Reheat Bleed Valve Command | 2644 | 238 |  |  | Hot Gas Reheat Bleed Valve Command | 2644 | 238 | 7029 | TRUE | FALSE | FALSE | 9 | MultiState |  | Close/Open | 939 | [5 empty] | Close/Open | 939 | [5 empty] | 0 = Close 1 = Open | 20
Value |  |  | Views.Details.Mod Hot Gas Reheat.Service | Compressor Stage Command 1 | 1714 | 145 |  | Views.Details.ModHGR.Service | C1 | 1709 | 127 |  |  | Compressor Stage Command | 1675 | 84 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 5
Value |  |  | Views.Details.Mod Hot Gas Reheat.Service | Compressor Stage Command 2 | 1714 | 146 |  | Views.Details.ModHGR.Service | C2 | 1709 | 128 |  |  | Compressor Stage Command | 1675 | 84 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 7
Value |  |  | Views.Details.Mod Hot Gas Reheat.Service | Compressor Stage Command 3 | 1714 | 147 |  | Views.Details.ModHGR.Service | C3 | 1709 | 129 |  |  | Compressor Stage Command | 1675 | 84 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 9
Value |  |  | Views.Details.Mod Hot Gas Reheat.Service | Compressor Stage Command 4 | 1714 | 148 |  | Views.Details.ModHGR.Service | C4 | 1709 | 130 |  |  | Compressor Stage Command | 1675 | 84 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 11
Value |  |  | Views.Details.Mod Hot Gas Reheat.Service | Modulating Compressor Output | 2644 | 292 |  | Views.Details.ModHGR.Service | ModCompOut | 2645 | 311 |  |  | Modulating Compressor Output | 2644 | 292 | 7067 | TRUE | FALSE | FALSE | 4 | Float | 10ths | % | 507:98 | 0 | 100 |  |  | 10ths | % | 507:98 | 0 | 100 |  |  |  |  | 4
Value |  |  | Views.Details.Mod Hot Gas Reheat.Service | Space Humidity RAH Input | 1675 | 25 |  | Views.Details.ModHGR.Service | RAH | 1709 | 41 |  |  | Space Humidity RAH Input | 1675 | 25 | 7019 | TRUE | FALSE | FALSE | 4 | Float | 10ths | %RH | 507:29 |  |  |  |  | 10ths | %RH | 507:29 | [6 empty] | 25
Value |  |  | Views.Details.Mod Hot Gas Reheat.Service | Operational Outdoor Air Temperature | 1675 | 36 |  | Views.Details.ModHGR.Service | OprOAT | 1709 | 52 |  |  | Operational Outdoor Air Temperature | 1675 | 36 | 7000 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 26
Group |  | FALSE | Views.Details.Heat Pump | Heat Pump | 1714 | 180 |  | Views.Details.HeatPmp | HeatPmp | 1709 | 618 | York RTU.Heat Pump Control.Number of Heat Pump Stages Installed:Present Value > 0
Value |  |  | Views.Details.Heat Pump | Number of Heat Pump Stages Installed | 1675 | 380 |  | Views.Details.HeatPmp | #HtPumpStgs | 1709 | 491 |  |  | Number of Heat Pump Stages Installed | 1675 | 380 | 7000 | TRUE | TRUE | FALSE | 4 | Float | 1s |  | 507:95 | 0 | 2 |  |  | 1s |  | 507:95 | 0 | 2 |  |  |  |  | 38
Value |  |  | Views.Details.Heat Pump | Test Defrost Enable | 1675 | 382 |  | Views.Details.HeatPmp | TestDefrostEnable | 1709 | 493 |  |  | Test Defrost Enable | 1675 | 382 | 7002 | TRUE | TRUE | FALSE | 9 | MultiState |  | False/True | 1701 | [5 empty] | False/True | 1701 | [5 empty] | 0 = False 1 = True | 38
Value |  |  | Views.Details.Heat Pump | Compressor Delay Enable | 1675 | 383 |  | Views.Details.HeatPmp | CompDelayEnable | 1709 | 494 |  |  | Compressor Delay Enable | 1675 | 383 | 7003 | TRUE | TRUE | FALSE | 9 | MultiState |  | False/True | 1701 | [5 empty] | False/True | 1701 | [5 empty] | 0 = False 1 = True | 38
Value |  |  | Views.Details.Heat Pump | Defrost Curve Selection | 1675 | 384 |  | Views.Details.HeatPmp | DefrostCurveSel | 1709 | 495 |  |  | Defrost Curve Selection | 1675 | 384 | 7004 | TRUE | TRUE | FALSE | 9 | MultiState |  | SE RTU Defrost Curves | 1665 | [5 empty] | SE RTU Defrost Curves | 1665 | [5 empty] | 0 = Curve 1 1 = Curve 2 2 = Curve 3 3 = Curve 4 ... | 38
Value |  |  | Views.Details.Heat Pump | Reversing Valve | 1675 | 482 |  | Views.Details.HeatPmp | RevVlv | 1709 | 613 |  |  | Reversing Valve | 1675 | 482 | 7011 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 38
Value |  |  | Views.Details.Heat Pump | Auxiliary Heat | 1675 | 483 |  | Views.Details.HeatPmp | AuxHtg | 1709 | 614 |  |  | Auxiliary Heat | 1675 | 483 | 7012 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 38
Value |  |  | Views.Details.Heat Pump | Mode | 1675 | 484 |  | Views.Details.HeatPmp | Mode | 1709 | 615 |  |  | Mode | 1675 | 484 | 7013 | TRUE | FALSE | FALSE | 9 | MultiState |  | Heating/Cooling | 350 | [5 empty] | Heating/Cooling | 350 | [5 empty] | 0 = Heating 1 = Cooling | 38
Value |  |  | Views.Details.Heat Pump | OAT Defrost Permission | 1714 | 227 |  | Views.Details.HeatPmp | OATDefPerm | 1709 | 724 |  |  | OAT Defrost Permission | 1714 | 227 | 7015 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 45 | 60 |  |  | 1s | deg C | 507:62 | 7 | 16 |  |  |  |  | 38
Value |  |  | Views.Details.Heat Pump | Operational Outdoor Air Temperature | 1675 | 36 |  | Views.Details.HeatPmp | OprOAT | 1709 | 52 |  |  | Operational Outdoor Air Temperature | 1675 | 36 | 7000 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 26
Value |  |  | Views.Details.Heat Pump | Condenser Coil Temp 1 | 1714 | 45 |  | Views.Details.HeatPmp | CC1 | 1709 | 184 |  |  | Condenser Coil Temp | 1675 | 102 | 7016 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 5
Value |  |  | Views.Details.Heat Pump | Condenser Coil Temp 2 | 1714 | 61 |  | Views.Details.HeatPmp | CC2 | 1709 | 185 |  |  | Condenser Coil Temp | 1675 | 102 | 7016 | TRUE | FALSE | FALSE | 4 | Float | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 | [6 empty] | 7
Value |  |  | Views.Details.Heat Pump | OAT Heat Pump Cutout | 1714 | 273 |  | Views.Details.HeatPmp | OATHPCutout | 1709 | 780 |  |  | OAT Heat Pump Cutout | 1714 | 273 | 7017 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | -20 | 50 |  |  | 1s | deg C | 507:62 | -29 | 10 |  |  |  |  | 38
Value |  |  | Views.Details.Heat Pump | Dual Fuel HP Enable | 1714 | 283 |  | Views.Details.HeatPmp | DualFuelHP-En | 1709 | 794 |  |  | Dual Fuel HP Enable | 1714 | 283 | 7018 | TRUE | TRUE | FALSE | 9 | MultiState |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 | [5 empty] | 0 = Disable 1 = Enable | 38
Value |  |  | Views.Details.Heat Pump | Dual Fuel OAT HP Cutout | 1714 | 285 |  | Views.Details.HeatPmp | DualFuelOATHPCutout | 1709 | 796 |  |  | Dual Fuel OAT HP Cutout | 1714 | 285 | 7019 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 0 | 65 |  |  | 1s | deg C | 507:62 | -18 | 18 |  |  |  |  | 38
Value |  |  | Views.Details.Heat Pump | Reversing Valve Delay | 1714 | 284 |  | Views.Details.HeatPmp | RevVlvDelay | 1709 | 795 |  |  | Reversing Valve Delay | 1714 | 284 | 7020 | TRUE | TRUE | FALSE | 4 | Float | 1s | seconds | 507:73 | 0 | 60 |  |  | 1s | seconds | 507:73 | 0 | 60 |  |  |  |  | 38
Group |  | FALSE | Views.Details.ERV | ERV | 1675 | 1016 |  | Views.Details.ERV | ERV | 1675 | 1016 | York RTU.System Controllers.Econ Controller:Present Value <> Not Present
Value |  |  | Views.Details.ERV | ERV Enabled | 1675 | 247 |  | Views.Details.ERV | ERV-En | 1709 | 321 |  |  | ERV Enabled | 1675 | 247 | 7013 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 21
Value |  |  | Views.Details.ERV | ERV Unoccupied Fan Enabled | 1675 | 248 |  | Views.Details.ERV | ERVUnoccFan-En | 1709 | 322 |  |  | ERV Unoccupied Fan Enabled | 1675 | 248 | 7014 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 21
Value |  |  | Views.Details.ERV | Fan Control Type | 1675 | 173 |  | Views.Details.ERV | FanCtl-Type | 1709 | 71 |  |  | Fan Control Type | 1675 | 173 | 7005 | TRUE | TRUE | FALSE | 9 | MultiState |  | SE RTU Fan Control Type | 1619 | [5 empty] | SE RTU Fan Control Type | 1619 | [5 empty] | 0 = Single Speed 1 = Not Used 2 = Fixed Variable 3 = Variable Speed | 3
Value |  |  | Views.Details.ERV | Fan Command | 1675 | 181 |  | Views.Details.ERV | Fan | 1709 | 79 |  |  | Fan Command | 1675 | 181 | 7013 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 3
Value |  |  | Views.Details.ERV | Econ Free Cooling Available | 1675 | 52 |  | Views.Details.ERV | Econ-Free | 1709 | 283 |  |  | Econ Free Cooling Available | 1675 | 52 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 19
Value |  |  | Views.Details.ERV | Exhaust Fan Command | 1675 | 235 |  | Views.Details.ERV | ExFan | 1709 | 309 |  |  | Exhaust Fan Command | 1675 | 235 | 7001 | TRUE | FALSE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 21
Group |  | FALSE | Views.Details.Load Shed | Load Shed | 1714 | 162 |  | Views.Details.T24LoadShed | T24LoadShed | 1709 | 532
Value |  |  | Views.Details.Load Shed | Load Shed Rate Limit | 1675 | 422 |  | Views.Details.T24LoadShed | LoadShedRateLim | 1709 | 529 |  |  | Load Shed Rate Limit | 1675 | 422 | 7044 | TRUE | TRUE | FALSE | 4 | Float | 1000ths | deg F/min | 507:94 | 0 | 1 |  |  | 1000ths | deg C/min | 507:92 | 0 | 1 |  |  |  |  | 25
Value |  |  | Views.Details.Load Shed | Load Shed Adjust | 1675 | 423 |  | Views.Details.T24LoadShed | LoadShedAdjust | 1709 | 530 |  |  | Load Shed Adjust | 1675 | 423 | 7045 | TRUE | TRUE | FALSE | 4 | Float | 10ths | delta deg F | 507:120 | 0 | 8 |  |  | 10ths | delta deg C | 507:359 | 0 | 4.4 |  |  |  |  | 25
Value |  |  | Views.Details.Load Shed | Load Shed Active | 1675 | 421 |  | Views.Details.T24LoadShed | LoadShedEnable | 1709 | 528 |  |  | Load Shed Active | 1675 | 421 | 7043 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 25
Group |  | FALSE | Views.Details.Verasys | Verasys | 1675 | 1690 |  | Views.Details.Verasys | Verasys | 1675 | 1690 | York RTU.CCS Online:Present Value = Yes
Value |  |  | Views.Details.Verasys | Rooftop Controller Type | 1675 | 466 |  | Views.Details.Verasys | CntrlType | 1709 | 639 |  |  | Rooftop Controller Type | 1675 | 466 | 7017 | TRUE | TRUE | FALSE | 9 | MultiState |  | LCCS Controller Type | 1244 | [5 empty] | LCCS Controller Type | 1244 | [5 empty] | 0 = Changeover Bypass 1 = VAV 2 = Constant Volume 3 = TEC | 1
Value |  |  | Views.Details.Verasys | VZC Online | 1675 | 1689 |  | Views.Details.Verasys | VZC Online | 1675 | 1689 |  |  | VZC Online | 1675 | 1689 | 7021 | TRUE | FALSE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 39
Value |  |  | Views.Details.Verasys | COBP Mode | 1709 | 778 |  | Views.Details.Verasys | COBP Mode | 1709 | 778 |  |  | COBP Mode | 1709 | 778 | 7022 | TRUE | FALSE | FALSE | 9 | MultiState |  | Heat Cool Mode | 1243 | [5 empty] | Heat Cool Mode | 1243 | [5 empty] | 0 = Heat 1 = Cool 2 = Fan Only 3 = Balancing ... | 39
Value |  |  | Views.Details.Verasys | COBP Supply Air Temperature Setpoint | 1675 | 601 |  | Views.Details.Verasys | COBP SAT SP | 1709 | 779 |  |  | COBP Supply Air Temperature Setpoint | 1675 | 601 | 7023 | TRUE | FALSE | FALSE | 4 | Float | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 | [6 empty] | 39
Value |  |  | Views.Details.Verasys | Operating State | 1675 | 459 |  | Views.Details.Verasys | Operating State | 1675 | 459 |  |  | Operating State | 1675 | 459 | 7002 | TRUE | FALSE | FALSE | 9 | MultiState |  | Heat Cool Mode | 1243 | [5 empty] | Heat Cool Mode | 1243 | [5 empty] | 0 = Heat 1 = Cool 2 = Fan Only 3 = Balancing ... | 39
Value |  |  | Views.Details.Verasys | VAV Cooling Supply Air Temp Lower Setpoint | 1675 | 138 |  | Views.Details.Verasys | SATLo-Sp | 1709 | 120 |  |  | VAV Cooling Supply Air Temp Lower Setpoint | 1675 | 138 | 7030 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 40 | 69 |  |  | 1s | deg C | 507:62 | 4 | 20 |  |  |  |  | 4
Value |  |  | Views.Details.Verasys | Economizer Minimum Position Setpoint | 1675 | 292 |  | Views.Details.Verasys | Econ-MinPos | 1709 | 381 |  |  | Economizer Minimum Position Setpoint | 1675 | 292 | 7017 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 19
View | TRUE |  | Views.Clone | Clone | 1712 | 5
Group |  | FALSE | Views.Clone.Full Clone | Full Clone | 1712 | 6 |  |  | Full Clone | 1708 | 7
Value |  |  | Views.Clone.Full Clone | Device Name | 1675 | 326 |  |  | DevName | 1709 | 446 |  |  | Device Name | 1675 | 326 | 7009 | TRUE | TRUE | FALSE | 7 | String | [14 empty] | 30 |  | 29
Value |  |  | Views.Clone.Full Clone | Unit Name | 1675 | 1 |  |  | Name | 1709 | 1 |  |  | Unit Name | 1675 | 1 | 7001 | TRUE | TRUE | FALSE | 7 | String | [14 empty] | 30 |  | 1
Value |  |  | Views.Clone.Full Clone | Unit Model Number | 1675 | 3 |  |  | Model# | 1709 | 2 |  |  | Unit Model Number | 1675 | 3 | 7002 | TRUE | TRUE | FALSE | 7 | String | [14 empty] | 40 |  | 1
Value |  |  | Views.Clone.Full Clone | Unit Serial Number | 1675 | 4 |  |  | Serial# | 1709 | 3 |  |  | Unit Serial Number | 1675 | 4 | 7003 | TRUE | TRUE | FALSE | 7 | String | [14 empty] | 40 |  | 1
Value |  |  | Views.Clone.Full Clone | Model Name | 1675 | 448 |  |  | ModelName | 1709 | 583 |  |  | Model Name | 1675 | 448 | 7014 | TRUE | FALSE | FALSE | 7 | String | [14 empty] | 30 |  | 1
Value |  |  | Views.Clone.Full Clone | Fan Accumulated Runtime | 1675 | 172 |  |  | Fan-RT | 1709 | 70 |  |  | Fan Accumulated Runtime | 1675 | 172 | 7004 | TRUE | TRUE | FALSE | 4 | Float | 1s | hours | 507:71 | 0 | 10000 |  |  | 1s | hours | 507:71 | 0 | 10000 |  |  |  |  | 3
Value |  |  | Views.Clone.Full Clone | Compressor Stage Accumulated Runtime 1 | 1714 | 43 |  |  | C1RunTim | 1709 | 140 |  |  | Compressor Stage Accumulated Runtime | 1675 | 90 | 7005 | TRUE | TRUE | FALSE | 4 | Float | 1s | hours | 507:71 | 0 | 10000 |  |  | 1s | hours | 507:71 | 0 | 10000 |  |  |  |  | 5
Value |  |  | Views.Clone.Full Clone | Compressor Stage Accumulated Runtime 2 | 1714 | 59 |  |  | C2RunTim | 1709 | 141 |  |  | Compressor Stage Accumulated Runtime | 1675 | 90 | 7005 | TRUE | TRUE | FALSE | 4 | Float | 1s | hours | 507:71 | 0 | 10000 |  |  | 1s | hours | 507:71 | 0 | 10000 |  |  |  |  | 7
Value |  |  | Views.Clone.Full Clone | Compressor Stage Accumulated Runtime 3 | 1714 | 75 |  |  | C3RunTim | 1709 | 142 |  |  | Compressor Stage Accumulated Runtime | 1675 | 90 | 7005 | TRUE | TRUE | FALSE | 4 | Float | 1s | hours | 507:71 | 0 | 10000 |  |  | 1s | hours | 507:71 | 0 | 10000 |  |  |  |  | 9
Value |  |  | Views.Clone.Full Clone | Compressor Stage Accumulated Runtime 4 | 1714 | 91 |  |  | C4RunTim | 1709 | 143 |  |  | Compressor Stage Accumulated Runtime | 1675 | 90 | 7005 | TRUE | TRUE | FALSE | 4 | Float | 1s | hours | 507:71 | 0 | 10000 |  |  | 1s | hours | 507:71 | 0 | 10000 |  |  |  |  | 11
Value |  |  | Views.Clone.Full Clone | Heating Stage 1 Accumulated Runtime | 1714 | 108 |  |  | H1RunTim | 1709 | 269 |  |  | Heat Stage Accumulated Runtime | 1675 | 116 | 7006 | TRUE | TRUE | FALSE | 4 | Float | 1s | hours | 507:71 | 0 | 10000 |  |  | 1s | hours | 507:71 | 0 | 10000 |  |  |  |  | 15
Value |  |  | Views.Clone.Full Clone | Heating Stage 2 Accumulated Runtime | 1714 | 114 |  |  | H2RunTim | 1709 | 270 |  |  | Heat Stage Accumulated Runtime | 1675 | 116 | 7006 | TRUE | TRUE | FALSE | 4 | Float | 1s | hours | 507:71 | 0 | 10000 |  |  | 1s | hours | 507:71 | 0 | 10000 |  |  |  |  | 16
Value |  |  | Views.Clone.Full Clone | Heating Stage 3 Accumulated Runtime | 1714 | 120 |  |  | H3RunTim | 1709 | 271 |  |  | Heat Stage Accumulated Runtime | 1675 | 116 | 7006 | TRUE | TRUE | FALSE | 4 | Float | 1s | hours | 507:71 | 0 | 10000 |  |  | 1s | hours | 507:71 | 0 | 10000 |  |  |  |  | 17
Value |  |  | Views.Clone.Full Clone | Time Zone | 1675 | 278 |  |  | TimeZone | 1709 | 349 |  |  | Time Zone | 1675 | 278 | 7007 | TRUE | TRUE | FALSE | 9 | MultiState |  | SE RTU Time Zone | 1731 | [5 empty] | SE RTU Time Zone | 1731 | [5 empty] | 51 = Eastern 53 = Central 57 = Mountain 58 = Pacific ... | 30
Value |  |  | Views.Clone.Full Clone | Address | 1675 | 282 |  |  | Address | 1709 | 352 |  |  | Address | 1675 | 282 | 7001 | TRUE | TRUE | FALSE | 17 | SignedInteger | 1s |  | 507:95 | 4 | 127 |  |  | 1s |  | 507:95 | 4 | 127 |  |  |  |  | 31
Value |  |  | Views.Clone.Full Clone | Device OID | 1675 | 283 |  |  | DeviceId | 1709 | 353 |  |  | Device OID | 1675 | 283 | 7002 | TRUE | TRUE | FALSE | 2 | UnsignedLong | 1s |  | 507:95 | 0 | 4194302 |  |  | 1s |  | 507:95 | 0 | 4194302 |  |  |  |  | 31
Group |  | FALSE | Views.Clone.Partial Clone 1 | Partial Clone 1 | 1712 | 7 |  |  | Partial Clone | 1708 | 8
Value |  |  | Views.Clone.Partial Clone 1 | Duct Pressure Setpoint | 1675 | 184 |  |  | DctPrs-Sp | 1709 | 82 |  |  | Duct Pressure Setpoint | 1675 | 184 | 7016 | TRUE | TRUE | FALSE | 4 | Float | 100ths | in wc | 507:58 | 0 | 5 |  |  | 100ths | kPa | 507:54 | 0 | 1.25 |  |  |  |  | 3
Value |  |  | Views.Clone.Partial Clone 1 | Duct Pressure Shutdown Setpoint | 1675 | 185 |  |  | DctShutdownSp | 1709 | 83 |  |  | Duct Pressure Shutdown Setpoint | 1675 | 185 | 7017 | TRUE | TRUE | FALSE | 4 | Float | 100ths | in wc | 507:58 | 0 | 5 |  |  | 100ths | kPa | 507:54 | 0 | 1.25 |  |  |  |  | 3
Value |  |  | Views.Clone.Partial Clone 1 | Continuous Fan Operation in Occupied Mode | 1675 | 186 |  |  | FanOnOcc | 1709 | 84 |  |  | Continuous Fan Operation in Occupied Mode | 1675 | 186 | 7018 | TRUE | TRUE | FALSE | 9 | MultiState |  | Yes/No | 1698 | [5 empty] | Yes/No | 1698 | [5 empty] | 0 = Yes 1 = No | 3
Value |  |  | Views.Clone.Partial Clone 1 | Turn Off Continuous Fan Operation When Starting Heat | 1675 | 187 |  |  | FanOffStartHeat | 1709 | 85 |  |  | Turn Off Continuous Fan Operation When Starting Heat | 1675 | 187 | 7019 | TRUE | TRUE | FALSE | 9 | MultiState |  | Yes/No | 1698 | [5 empty] | Yes/No | 1698 | [5 empty] | 0 = Yes 1 = No | 3
Value |  |  | Views.Clone.Partial Clone 1 | Occupied: No Heat or Cool % Command | 1675 | 188 |  |  | FanOnly-%Cmd | 1709 | 86 |  |  | Occupied: No Heat or Cool % Command | 1675 | 188 | 7020 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 3
Value |  |  | Views.Clone.Partial Clone 1 | Occupied: One Stage of Cool % Command | 1675 | 189 |  |  | 1ClgStg-%Cmd | 1709 | 87 |  |  | Occupied: One Stage of Cool % Command | 1675 | 189 | 7021 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 3
Value |  |  | Views.Clone.Partial Clone 1 | Occupied: Two Stage of Cool % Command | 1675 | 190 |  |  | 2ClgStg-%Cmd | 1709 | 88 |  |  | Occupied: Two Stage of Cool % Command | 1675 | 190 | 7022 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 3
Value |  |  | Views.Clone.Partial Clone 1 | Occupied: Three Stage of Cool % Command | 1675 | 320 |  |  | 3ClgStg-%Cmd | 1709 | 442 |  |  | Occupied: Three Stage of Cool % Command | 1675 | 320 | 7027 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 3
Value |  |  | Views.Clone.Partial Clone 1 | Occupied: Four Stage of Cool % Command | 1675 | 321 |  |  | 4ClgStg-%Cmd | 1709 | 443 |  |  | Occupied: Four Stage of Cool % Command | 1675 | 321 | 7028 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 3
Value |  |  | Views.Clone.Partial Clone 1 | Occupied: One Stage of Heat % Command | 1675 | 191 |  |  | 1HtgStg-%Cmd | 1709 | 89 |  |  | Occupied: One Stage of Heat % Command | 1675 | 191 | 7023 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 3
Value |  |  | Views.Clone.Partial Clone 1 | Occupied: Two Stage of Heat % Command | 1675 | 192 |  |  | 2HtgStg-%Cmd | 1709 | 90 |  |  | Occupied: Two Stage of Heat % Command | 1675 | 192 | 7024 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 3
Value |  |  | Views.Clone.Partial Clone 1 | Occupied: Three Stage of Heat % Command | 1675 | 322 |  |  | 3HtgStg-%Cmd | 1709 | 444 |  |  | Occupied: Three Stage of Heat % Command | 1675 | 322 | 7029 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 3
Value |  |  | Views.Clone.Partial Clone 1 | VAV Cooling Supply Air Temp Upper Setpoint | 1675 | 137 |  |  | SATUp-Sp | 1709 | 119 |  |  | VAV Cooling Supply Air Temp Upper Setpoint | 1675 | 137 | 7029 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 41 | 70 |  |  | 1s | deg C | 507:62 | 5 | 21 |  |  |  |  | 4
Value |  |  | Views.Clone.Partial Clone 1 | VAV Cooling Supply Air Temp Lower Setpoint | 1675 | 138 |  |  | SATLo-Sp | 1709 | 120 |  |  | VAV Cooling Supply Air Temp Lower Setpoint | 1675 | 138 | 7030 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 40 | 69 |  |  | 1s | deg C | 507:62 | 4 | 20 |  |  |  |  | 4
Value |  |  | Views.Clone.Partial Clone 1 | VAV Supply Air Temp Reset Setpoint | 1675 | 139 |  |  | SATRst-Sp | 1709 | 121 |  |  | VAV Supply Air Temp Reset Setpoint | 1675 | 139 | 7031 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 40 | 85 |  |  | 1s | deg C | 507:62 | 4 | 30 |  |  |  |  | 4
Value |  |  | Views.Clone.Partial Clone 1 | CV Occupied Cooling Setpoint | 1675 | 141 |  |  | ClgOcc-Sp | 1709 | 123 |  |  | CV Occupied Cooling Setpoint | 1675 | 141 | 7033 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 45 | 98 |  |  | 1s | deg C | 507:62 | 7 | 36 |  |  |  |  | 4
Value |  |  | Views.Clone.Partial Clone 1 | CV Unoccupied Cooling Setpoint | 1675 | 142 |  |  | ClgUnocc-Sp | 1709 | 124 |  |  | CV Unoccupied Cooling Setpoint | 1675 | 142 | 7034 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 46 | 99 |  |  | 1s | deg C | 507:62 | 8 | 37 |  |  |  |  | 4
Value |  |  | Views.Clone.Partial Clone 1 | VAV Occupied Heating Enabled | 1675 | 204 |  |  | HtgOcc-En | 1709 | 239 |  |  | VAV Occupied Heating Enabled | 1675 | 204 | 7015 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 13
Value |  |  | Views.Clone.Partial Clone 1 | VAV Occupied Heating Setpoint | 1675 | 205 |  |  | VAVHtgOcc-SP | 1709 | 240 |  |  | VAV Occupied Heating Setpoint | 1675 | 205 | 7016 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 40 | 85 |  |  | 1s | deg C | 507:62 | 4 | 30 |  |  |  |  | 13
Value |  |  | Views.Clone.Partial Clone 1 | Unoccupied Heating Enabled | 1675 | 206 |  |  | HtgUnocc-En | 1709 | 241 |  |  | Unoccupied Heating Enabled | 1675 | 206 | 7017 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 13
Value |  |  | Views.Clone.Partial Clone 1 | VAV Unoccupied Heating Setpoint | 1675 | 207 |  |  | VAVHtgUnocc-Sp | 1709 | 242 |  |  | VAV Unoccupied Heating Setpoint | 1675 | 207 | 7018 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 45 | 98 |  |  | 1s | deg C | 507:62 | 7 | 36 |  |  |  |  | 13
Value |  |  | Views.Clone.Partial Clone 1 | SZ VAV Occupied Cooling Setpoint | 1675 | 644 |  |  | SZVAVClgOcc-Sp | 1709 | 656 |  |  | SZ VAV Occupied Cooling Setpoint | 1675 | 644 | 7048 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 45 | 98 |  |  | 1s | deg C | 507:62 | 7 | 36 |  |  |  |  | 4
Value |  |  | Views.Clone.Partial Clone 1 | SZ VAV Unoccupied Cooling Setpoint | 1675 | 646 |  |  | SZVAVClgUnocc-Sp | 1709 | 657 |  |  | SZ VAV Unoccupied Cooling Setpoint | 1675 | 646 | 7049 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 45 | 98 |  |  | 1s | deg C | 507:62 | 7 | 36 |  |  |  |  | 4
Value |  |  | Views.Clone.Partial Clone 1 | Morning Warmup Enabled | 1675 | 209 |  |  | MornW-En | 1709 | 244 |  |  | Morning Warmup Enabled | 1675 | 209 | 7020 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 13
Value |  |  | Views.Clone.Partial Clone 1 | Morning Warmup/Return Air Temp Setpoint | 1675 | 210 |  |  | MornWRAT-Sp | 1709 | 245 |  |  | Morning Warmup/Return Air Temp Setpoint | 1675 | 210 | 7021 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 50 | 85 |  |  | 1s | deg C | 507:62 | 10 | 30 |  |  |  |  | 13
Value |  |  | Views.Clone.Partial Clone 1 | CV Occupied Heating Setpoint | 1675 | 212 |  |  | CVHtgOcc-SP | 1709 | 461 |  |  | CV Occupied Heating Setpoint | 1675 | 212 | 7023 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 46 | 99 |  |  | 1s | deg C | 507:62 | 8 | 37 |  |  |  |  | 13
Value |  |  | Views.Clone.Partial Clone 1 | CV Unoccupied Heating Setpoint | 1675 | 213 |  |  | CVHtgUnocc-Sp | 1709 | 462 |  |  | CV Unoccupied Heating Setpoint | 1675 | 213 | 7024 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 45 | 98 |  |  | 1s | deg C | 507:62 | 7 | 36 |  |  |  |  | 13
Value |  |  | Views.Clone.Partial Clone 1 | Low Ambient Economizer Setpoint | 1675 | 58 |  |  | LowAmb-Sp | 1709 | 289 |  |  | Low Ambient Economizer Setpoint | 1675 | 58 | 7008 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | -20 | 60 |  |  | 1s | deg C | 507:62 | -29 | 15 |  |  |  |  | 19
Value |  |  | Views.Clone.Partial Clone 1 | Low Ambient Economizer Minimum Position | 1675 | 59 |  |  | LowAmb-MinPos | 1709 | 290 |  |  | Low Ambient Economizer Minimum Position | 1675 | 59 | 7009 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 19
Value |  |  | Views.Clone.Partial Clone 1 | Language | 1675 | 267 |  |  | Language | 1709 | 337 |  |  | Language | 1675 | 267 | 7000 | TRUE | TRUE | FALSE | 9 | MultiState |  | SE RTU Languages | 1730 | [5 empty] | SE RTU Languages | 1730 | [5 empty] | 7 = English 10 = French 28 = Spanish | 29
Value |  |  | Views.Clone.Partial Clone 1 | Units | 1675 | 268 |  |  | Units | 1709 | 338 |  |  | Units | 1675 | 268 | 7001 | TRUE | TRUE | FALSE | 9 | MultiState |  | Unit Set | 869 | [5 empty] | Unit Set | 869 | [5 empty] | 0 = IP 1 = SI | 29
Value |  |  | Views.Clone.Partial Clone 1 | BAS Communication | 1675 | 270 |  |  | BASCom | 1709 | 340 |  |  | BAS Communication | 1675 | 270 | 7003 | TRUE | FALSE | FALSE | 9 | MultiState |  | BAS Communication | 1724 | [5 empty] | BAS Communication | 1724 | [5 empty] | 0 = Not Installed 1 = BACnet 2 = N2 3 = Modbus | 29
Value |  |  | Views.Clone.Partial Clone 1 | Occupancy Mode | 1675 | 161 |  |  | OccMode | 1709 | 24 |  |  | Occupancy Mode | 1675 | 161 | 7002 | TRUE | TRUE | FALSE | 9 | MultiState |  | SE Occupancy Mode | 1728 | [5 empty] | SE Occupancy Mode | 1728 | [5 empty] | 0 = Schedule 1 = External | 25
Value |  |  | Views.Clone.Partial Clone 1 | SZ VAV Enabled | 1675 | 491 |  |  | SZVAVEn | 1709 | 623 |  |  | SZ VAV Enabled | 1675 | 491 | 7020 | TRUE | TRUE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 1
Value |  |  | Views.Clone.Partial Clone 1 | OAT Cooling Cutout Enabled | 1675 | 127 |  |  | ClgOATCutout-En | 1709 | 97 |  |  | OAT Cooling Cutout Enabled | 1675 | 127 | 7006 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 4
Value |  |  | Views.Clone.Partial Clone 1 | OAT Cooling Cutout | 1675 | 74 |  |  | ClgOATCutout | 1709 | 98 |  |  | OAT Cooling Cutout | 1675 | 74 | 7007 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 0 | 100 |  |  | 1s | deg C | 507:62 | -18 | 38 |  |  |  |  | 4
Value |  |  | Views.Clone.Partial Clone 1 | SAT Limit for Cooling Enable | 1675 | 143 |  |  | SATCoolLimit-En | 1709 | 106 |  |  | SAT Limit for Cooling Enable | 1675 | 143 | 7015 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 4
Value |  |  | Views.Clone.Partial Clone 1 | SAT Limit for Cooling Setpoint | 1675 | 75 |  |  | SATCoolLimit-Sp | 1709 | 107 |  |  | SAT Limit for Cooling Setpoint | 1675 | 75 | 7016 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 40 | 65 |  |  | 1s | deg C | 507:62 | 4 | 18 |  |  |  |  | 4
Value |  |  | Views.Clone.Partial Clone 1 | SZ VAV Minimum Fan Speed | 1675 | 627 |  |  | SZVAVMinFanSpd | 1709 | 647 |  |  | SZ VAV Minimum Fan Speed | 1675 | 627 | 7037 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 3
Value |  |  | Views.Clone.Partial Clone 1 | Space Temperature Setpoint Offset Range | 1675 | 34 |  |  | SSORange | 1709 | 50 |  |  | Space Temperature Setpoint Offset Range | 1675 | 34 | 7028 | TRUE | TRUE | FALSE | 4 | Float | 10ths | delta deg F | 507:120 | 0 | 5 |  |  | 10ths | delta deg C | 507:359 | 0 | 3 |  |  |  |  | 25
Value |  |  | Views.Clone.Partial Clone 1 | Off During Unoccupied | 1675 | 501 |  |  | OffDurUnocc | 1709 | 633 |  |  | Off During Unoccupied | 1675 | 501 | 7059 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 25
Value |  |  | Views.Clone.Partial Clone 1 | Common Setpoint | 2596 | 0 |  |  | Common-SP | 1709 | 702 |  |  | Common Setpoint | 2596 | 0 | 7074 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 45 | 98 |  |  | 1s | deg C | 507:62 | 8 | 36 |  |  |  |  | 25
Value |  |  | Views.Clone.Partial Clone 1 | Heat Cool Setpoint Mode | 1714 | 212 |  |  | Heat Cool Setpoint Mode | 1714 | 212 |  |  | Heat Cool Setpoint Mode | 1714 | 212 | 7075 | TRUE | TRUE | FALSE | 9 | MultiState |  | Heat Cool Setpoint Mode | 2596 | [5 empty] | Heat Cool Setpoint Mode | 2596 | [5 empty] | 0 = Common Setpoint 1 = Individual Setpoints | 25
Value |  |  | Views.Clone.Partial Clone 1 | Auto Changeover | 1675 | 1469 |  |  | Auto Changeover | 1675 | 1469 |  |  | Auto Changeover | 1675 | 1469 | 7076 | TRUE | TRUE | FALSE | 4 | Float | 10ths | delta deg F | 507:120 | 2 | 5 |  |  | 10ths | delta deg C | 507:359 | 1.1 | 2.8 |  |  |  |  | 25
Value |  |  | Views.Clone.Partial Clone 1 | Hydronic Heating Stage #1 Supply Air Setpoint | 1675 | 220 |  |  | HydH1SA-Sp | 1709 | 277 |  |  | Hydronic Heating Stage #1 Supply Air Setpoint | 1675 | 220 | 7002 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 80 | 180 |  |  | 1s | deg C | 507:62 | 27 | 82 |  |  |  |  | 18
Value |  |  | Views.Clone.Partial Clone 1 | Hydronic Heating Stage #2 Supply Air Setpoint | 1675 | 221 |  |  | HydH2SA-Sp | 1709 | 278 |  |  | Hydronic Heating Stage #2 Supply Air Setpoint | 1675 | 221 | 7003 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 80 | 180 |  |  | 1s | deg C | 507:62 | 27 | 82 |  |  |  |  | 18
Value |  |  | Views.Clone.Partial Clone 1 | Thermostat Only Control Enabled | 1675 | 160 |  |  | Tstat-Only | 1709 | 21 |  |  | Thermostat Only Control Enabled | 1675 | 160 | 7010 | TRUE | TRUE | FALSE | 9 | MultiState |  | No/Yes | 854 | [5 empty] | No/Yes | 854 | [5 empty] | 0 = No 1 = Yes | 2
Value |  |  | Views.Clone.Partial Clone 1 | Economizer Minimum Position Setpoint | 1675 | 292 |  |  | Econ-MinPos | 1709 | 381 |  |  | Economizer Minimum Position Setpoint | 1675 | 292 | 7017 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 19
Value |  |  | Views.Clone.Partial Clone 1 | Economizer Damper Minimum Position Low Speed Fan | 1675 | 327 |  |  | LowSpeedFan-MinPos | 1709 | 447 |  |  | Economizer Damper Minimum Position Low Speed Fan | 1675 | 327 | 7025 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 19
Value |  |  | Views.Clone.Partial Clone 1 | Free Cooling Selection | 1675 | 55 |  |  | FreeClg-Sel | 1709 | 286 |  |  | Free Cooling Selection | 1675 | 55 | 7005 | TRUE | TRUE | FALSE | 9 | MultiState |  | SE RTU Economizer Type | 3398 | [5 empty] | SE RTU Economizer Type | 3398 | [5 empty] | 0 = Dry Bulb Temperature 1 = Single Enthalpy 2 = Dual Enthalpy 3 = Auto 4 = Differential Dry Bulb | 19
Value |  |  | Views.Clone.Partial Clone 1 | Economizer Outdoor Air Temp Enable Setpoint | 1675 | 56 |  |  | EconOAT-SpEn | 1709 | 287 |  |  | Economizer Outdoor Air Temp Enable Setpoint | 1675 | 56 | 7006 | TRUE | TRUE | FALSE | 4 | Float | 1s | deg F | 507:64 | 0 | 80 |  |  | 1s | deg C | 507:62 | -17.8 | 27 |  |  |  |  | 19
Value |  |  | Views.Clone.Partial Clone 1 | Economizer Outdoor Air Enthalpy Setpoint | 1675 | 57 |  |  | EconOAEnth-Sp | 1709 | 288 |  |  | Economizer Outdoor Air Enthalpy Setpoint | 1675 | 57 | 7007 | TRUE | TRUE | FALSE | 4 | Float | 1s | Btu/lb dry air | 507:24 | 10 | 50 |  |  | 1s | kJ/kg | 507:125 | 23 | 116 |  |  |  |  | 19
Value |  |  | Views.Clone.Partial Clone 1 | Demand Ventilation Maximum Economizer Position | 1675 | 226 |  |  | DVentMaxEconPos | 1709 | 299 |  |  | Demand Ventilation Maximum Economizer Position | 1675 | 226 | 7001 | TRUE | TRUE | FALSE | 4 | Float | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  |  |  | 23
Value |  |  | Views.Clone.Partial Clone 1 | Demand Ventilation Indoor Air Quality Setpoint | 1675 | 227 |  |  | DVentIAQ-Sp | 1709 | 300 |  |  | Demand Ventilation Indoor Air Quality Setpoint | 1675 | 227 | 7002 | TRUE | TRUE | FALSE | 4 | Float | 1s | ppm | 507:96 | 0 | 5000 |  |  | 1s | ppm | 507:96 | 0 | 5000 |  |  |  |  | 23
Value |  |  | Views.Clone.Partial Clone 1 | Demand Ventilation Differential Setpoint | 1675 | 228 |  |  | DVentDiff-Sp | 1709 | 301 |  |  | Demand Ventilation Differential Setpoint | 1675 | 228 | 7003 | TRUE | TRUE | FALSE | 4 | Float | 1s | ppm | 507:96 | 0 | 5000 |  |  | 1s | ppm | 507:96 | 0 | 5000 |  |  |  |  | 23
Value |  |  | Views.Clone.Partial Clone 1 | Indoor Air Quality Sensor Range | 1675 | 166 |  |  | IAQRange | 1709 | 37 |  |  | Indoor Air Quality Sensor Range | 1675 | 166 | 7015 | TRUE | TRUE | FALSE | 4 | Float | 1s | ppm | 507:96 | 0 | 5000 |  |  | 1s | ppm | 507:96 | 0 | 5000 |  |  |  |  | 25
Value |  |  | Views.Clone.Partial Clone 1 | Outdoor Air Quality Sensor Range | 1675 | 48 |  |  | OAQRange | 1709 | 64 |  |  | Outdoor Air Quality Sensor Range | 1675 | 48 | 7012 | TRUE | TRUE | FALSE | 4 | Float | 10s | ppm | 507:96 | 0 | 5000 |  |  | 10s | ppm | 507:96 | 0 | 5000 |  |  |  |  | 26
Value |  |  | Views.Clone.Partial Clone 1 | Fresh Air Intake Setpoint | 1675 | 255 |  |  | MOAFlow-Sp | 1709 | 329 |  |  | Fresh Air Intake Setpoint | 1675 | 255 | 7000 | TRUE | TRUE | FALSE | 4 | Float | 10s | cfm | 507:84 | 0 | 50000 |  |  | 10s | L/s | 507:87 | 0 | 25000 |  |  |  |  | 24
Value |  |  | Views.Clone.Partial Clone 1 | Fresh Air Intake Max Sensor Range | 1675 | 257 |  |  | MOA-Range | 1709 | 331 |  |  | Fresh Air Intake Max Sensor Range | 1675 | 257 | 7002 | TRUE | TRUE | FALSE | 4 | Float | 10s | cfm | 507:84 | 0 | 50000 |  |  | 10s | L/s | 507:87 | 0 | 25000 |  |  |  |  | 24
Value |  |  | Views.Clone.Partial Clone 1 | EconMech Setup | 1675 | 498 |  |  | EconMechStp | 1709 | 630 |  |  | EconMech Setup | 1675 | 498 | 7027 | TRUE | TRUE | FALSE | 9 | MultiState |  | SE RTU EconMech Setup | 1752 | [5 empty] | SE RTU EconMech Setup | 1752 | [5 empty] | 0 = Option A 1 = Option B | 19
Value |  |  | Views.Clone.Partial Clone 1 | Economizer Fault Detection Enable | 1675 | 626 |  |  | EconFltDetectEn | 1709 | 646 |  |  | Economizer Fault Detection Enable | 1675 | 626 | 7028 | TRUE | TRUE | FALSE | 9 | MultiState |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 | [5 empty] | 0 = Disable 1 = Enable | 19
Group |  | FALSE | Views.Clone.Network Override | Network Override | 1712 | 9 |  |  | Network Override | 1712 | 9
Value |  |  | Views.Clone.Network Override | Network Override Space Temperature | 1675 | 18 |  |  | NetST | 1709 | 33 |  |  | Network Override Space Temperature | 1675 | 18 | 7011 | TRUE | TRUE | FALSE | 4 | Float | 10ths | deg F | 507:64 | 0 | 100 |  |  | 10ths | deg C | 507:62 | 4 | 38 |  |  |  |  | 25
Value |  |  | Views.Clone.Network Override | Network Override Indoor Air Quality | 1675 | 22 |  |  | NetIAQ | 1709 | 38 |  |  | Network Override Indoor Air Quality | 1675 | 22 | 7016 | TRUE | TRUE | FALSE | 4 | Float | 10s | ppm | 507:96 | 0 | 5000 |  |  | 10s | ppm | 507:96 | 0 | 5000 |  |  |  |  | 25
Value |  |  | Views.Clone.Network Override | Network Override Zone Humidity | 1675 | 26 |  |  | NetSH | 1709 | 42 |  |  | Network Override Zone Humidity | 1675 | 26 | 7020 | TRUE | TRUE | FALSE | 4 | Float | 10ths | %RH | 507:29 | 0 | 100 |  |  | 10ths | %RH | 507:29 | 0 | 100 |  |  |  |  | 25
Value |  |  | Views.Clone.Network Override | Network Override Fan Request | 1675 | 29 |  |  | NetFanReq | 1709 | 45 |  |  | Network Override Fan Request | 1675 | 29 | 7023 | TRUE | TRUE | FALSE | 9 | MultiState |  | Off/On | 647 | [5 empty] | Off/On | 647 | [5 empty] | 0 = Off 1 = On | 25
Value |  |  | Views.Clone.Network Override | Network Override Space Setpoint Offset | 1675 | 33 |  |  | NetSSO | 1709 | 49 |  |  | Network Override Space Setpoint Offset | 1675 | 33 | 7027 | TRUE | TRUE | FALSE | 4 | Float | 10ths | delta deg F | 507:120 | -5 | 5 |  |  | 10ths | delta deg C | 507:359 | -3 | 3 |  |  |  |  | 25
Value |  |  | Views.Clone.Network Override | Network Override Outdoor Air Temperature | 1675 | 39 |  |  | NetOAT | 1709 | 55 |  |  | Network Override Outdoor Air Temperature | 1675 | 39 | 7003 | TRUE | TRUE | FALSE | 4 | Float | 10ths | deg F | 507:64 | -50 | 125 |  |  | 10ths | deg C | 507:62 | -18 | 52 |  |  |  |  | 26
Value |  |  | Views.Clone.Network Override | Network Override Outdoor Air Humidity | 1675 | 44 |  |  | NetOAH | 1709 | 60 |  |  | Network Override Outdoor Air Humidity | 1675 | 44 | 7008 | TRUE | TRUE | FALSE | 4 | Float | 10ths | %RH | 507:29 | 0 | 100 |  |  | 10ths | %RH | 507:29 | 0 | 100 |  |  |  |  | 26
Value |  |  | Views.Clone.Network Override | Network Override Outdoor Air Quality | 1675 | 49 |  |  | NetOAQ | 1709 | 65 |  |  | Network Override Outdoor Air Quality | 1675 | 49 | 7013 | TRUE | TRUE | FALSE | 4 | Float | 10s | ppm | 507:96 | 0 | 5000 |  |  | 10s | ppm | 507:96 | 0 | 5000 |  |  |  |  | 26
Value |  |  | Views.Clone.Network Override | Network Override Purge Command | 1675 | 261 |  |  | NetPurge | 1709 | 335 |  |  | Network Override Purge Command | 1675 | 261 | 7003 | TRUE | TRUE | FALSE | 9 | MultiState |  | False/True | 1701 | [5 empty] | False/True | 1701 | [5 empty] | 0 = False 1 = True | 27
View | TRUE |  | Views.BACnet Objects | BACnet Objects | 1712 | 8
View | FALSE |  | Views.Trend | Trend | 1712 | 24
Group |  | FALSE | Views.Trend.Status | Status | 1712 | 0 |  |  | Status | 1712 | 0
Trend |  |  | Views.Trend.Status | Unit Status | 1675 | 0 |  |  | Unit-S | 1709 | 0 | [27 empty] | 101011
Trend |  |  | Views.Trend.Status | Fan Status | 1675 | 168 |  |  | Fan-S | 1709 | 66 | [27 empty] | 101027
Trend |  |  | Views.Trend.Status | Cooling Status | 1675 | 69 |  |  | Clg-S | 1709 | 93 | [27 empty] | 101035
Trend |  |  | Views.Trend.Status | Heating Status | 1675 | 106 |  |  | Htg-S | 1709 | 225 | [27 empty] | 101116
Trend |  |  | Views.Trend.Status | Economizer Status | 1675 | 53 |  |  | Econ-S | 1709 | 284 | [27 empty] | 101134
Trend |  |  | Views.Trend.Status | Hot Gas Reheat Status | 1675 | 251 |  |  | HGR-S | 1709 | 325 | [27 empty] | 101143
Trend |  |  | Views.Trend.Status | Operational Occupancy | 1675 | 10 |  |  | OprOcc | 1709 | 23 | [27 empty] | 101021
Trend |  |  | Views.Trend.Status | Operational Space Temperature | 1675 | 15 |  |  | OprST | 1709 | 28 | [27 empty] | 101022
Trend |  |  | Views.Trend.Status | Supply Air Temperature | 1675 | 182 |  |  | SAT | 1709 | 80 | [27 empty] | 101032
Trend |  |  | Views.Trend.Status | Mixed Air Temperature | 1675 | 62 |  |  | MAT | 1709 | 293 | [27 empty] | 101135
Trend |  |  | Views.Trend.Status | Operational Outdoor Air Temperature | 1675 | 36 |  |  | OprOAT | 1709 | 52 | [27 empty] | 101025
Trend |  |  | Views.Trend.Status | Return Air Temperature | 1675 | 65 |  |  | RAT | 1709 | 297 | [27 empty] | 101147
Group |  | FALSE | Views.Trend.Cooling | Cooling | 1714 | 6 |  |  | Cooling | 1714 | 6
Group |  | FALSE | Views.Trend.Cooling.Status | Status | 1712 | 0 |  |  | Status | 1712 | 0
Trend |  |  | Views.Trend.Cooling.Status | Cooling Status | 1675 | 69 |  |  | Clg-S | 1709 | 93 | [27 empty] | 101035
Trend |  |  | Views.Trend.Cooling.Status | Supply Air Temperature | 1675 | 182 |  |  | SAT | 1709 | 80 | [27 empty] | 101032
Trend |  |  | Views.Trend.Cooling.Status | Operating Cooling Setpoint | 1675 | 1176 |  |  | OprClg-Sp | 2645 | 440 | [27 empty] | 101039
Trend |  |  | Views.Trend.Cooling.Status | SZ VAV Operating Cooling Setpoint | 1675 | 648 |  |  | OprSZVAVClg-Sp | 1709 | 660 | [27 empty] | 101149
Group |  | FALSE | Views.Trend.Cooling.Stage 1 | Stage 1 | 1714 | 31 |  |  | Stage 1 | 1714 | 31
Trend |  |  | Views.Trend.Cooling.Stage 1 | Y1 - Thermostat | 1675 | 150 |  |  | Y1-Tstat | 1709 | 11 | [27 empty] | 101012
Trend |  |  | Views.Trend.Cooling.Stage 1 | Compressor Stage 1 Status | 1714 | 39 |  |  | Compressor Stage 1 Status | 1714 | 39 | [27 empty] | 101041
Trend |  |  | Views.Trend.Cooling.Stage 1 | Compressor Stage Command 1 | 1714 | 145 |  |  | Compressor Stage Command 1 | 1714 | 145 | [27 empty] | 101040
Trend |  |  | Views.Trend.Cooling.Stage 1 | Modulating Compressor Output | 2644 | 292 |  |  | ModCompOut | 2645 | 311 | [27 empty] | 101152
Group |  | FALSE | Views.Trend.Cooling.Stage 2 | Stage 2 | 1714 | 32 |  |  | Stage 2 | 1714 | 32 | York RTU.Cooling Control.Number of Cooling Stages Installed:Present Value > 1
Trend |  |  | Views.Trend.Cooling.Stage 2 | Y2 - Thermostat | 1675 | 151 |  |  | Y2-Tstat | 1709 | 12 | [27 empty] | 101013
Trend |  |  | Views.Trend.Cooling.Stage 2 | Compressor Stage 2 Status | 1714 | 55 |  |  | Compressor Stage 2 Status | 1714 | 55 | [27 empty] | 101051
Trend |  |  | Views.Trend.Cooling.Stage 2 | Compressor Stage Command 2 | 1714 | 146 |  |  | Compressor Stage Command 2 | 1714 | 146 | [27 empty] | 101050
Group |  | FALSE | Views.Trend.Cooling.Stage 3 | Stage 3 | 1714 | 33 |  |  | Stage 3 | 1714 | 33 | York RTU.Cooling Control.Number of Cooling Stages Installed:Present Value > 2
Trend |  |  | Views.Trend.Cooling.Stage 3 | Y3 - Thermostat | 1675 | 152 |  |  | Y3-Tstat | 1709 | 13 | [27 empty] | 101014
Trend |  |  | Views.Trend.Cooling.Stage 3 | Compressor Stage 3 Status | 1714 | 71 |  |  | Compressor Stage 3 Status | 1714 | 71 | [27 empty] | 101061
Trend |  |  | Views.Trend.Cooling.Stage 3 | Compressor Stage Command 3 | 1714 | 147 |  |  | Compressor Stage Command 3 | 1714 | 147 | [27 empty] | 101060
Group |  | FALSE | Views.Trend.Cooling.Stage 4 | Stage 4 | 1714 | 34 |  |  | Stage 4 | 1714 | 34 | York RTU.Cooling Control.Number of Cooling Stages Installed:Present Value > 3
Trend |  |  | Views.Trend.Cooling.Stage 4 | Y4 - Thermostat | 1675 | 153 |  |  | Y4-Tstat | 1709 | 14 | [27 empty] | 101015
Trend |  |  | Views.Trend.Cooling.Stage 4 | Compressor Stage 4 Status | 1714 | 87 |  |  | Compressor Stage 4 Status | 1714 | 87 | [27 empty] | 101071
Trend |  |  | Views.Trend.Cooling.Stage 4 | Compressor Stage Command 4 | 1714 | 148 |  |  | Compressor Stage Command 4 | 1714 | 148 | [27 empty] | 101070
Group |  | FALSE | Views.Trend.Heating | Heating | 1714 | 12 |  |  | Heating | 1714 | 12
Group |  | FALSE | Views.Trend.Heating.Status | Status | 1712 | 0 |  |  | Status | 1712 | 0
Trend |  |  | Views.Trend.Heating.Status | Heating Status | 1675 | 106 |  |  | Htg-S | 1709 | 225 | [27 empty] | 101116
Trend |  |  | Views.Trend.Heating.Status | Supply Air Temperature | 1675 | 182 |  |  | SAT | 1709 | 80 | [27 empty] | 101032
Trend |  |  | Views.Trend.Heating.Status | Operating Heating Setpoint | 1675 | 1175 |  |  | OprHtg-Sp | 2645 | 441 | [27 empty] | 101124
Group |  | FALSE | Views.Trend.Heating.Stage 1 | Stage 1 | 1714 | 31 |  |  | Stage 1 | 1714 | 31 | York RTU.Heating Control.Staged Heat Control.Number of Heating Stages Installed:Present Value > 0
Trend |  |  | Views.Trend.Heating.Stage 1 | W1 - Thermostat | 1675 | 154 |  |  | W1-Tstat | 1709 | 15 | [27 empty] | 101016
Trend |  |  | Views.Trend.Heating.Stage 1 | Heating Stage Command 1 | 1714 | 149 |  |  | Heating Stage Command 1 | 1714 | 149 | [27 empty] | 101125
Trend |  |  | Views.Trend.Heating.Stage 1 | Heating Stage 1 Enabled | 1714 | 104 |  |  | Heating Stage 1 Enabled | 1714 | 104 | [27 empty] | 101126
Group |  | FALSE | Views.Trend.Heating.Stage 2 | Stage 2 | 1714 | 32 |  |  | Stage 2 | 1714 | 32 | York RTU.Heating Control.Staged Heat Control.Number of Heating Stages Installed:Present Value > 1
Trend |  |  | Views.Trend.Heating.Stage 2 | W2 - Thermostat | 1675 | 155 |  |  | W2-Tstat | 1709 | 16 | [27 empty] | 101017
Trend |  |  | Views.Trend.Heating.Stage 2 | Heating Stage Command 2 | 1714 | 150 |  |  | Heating Stage Command 2 | 1714 | 150 | [27 empty] | 101127
Trend |  |  | Views.Trend.Heating.Stage 2 | Heating Stage 2 Status | 1714 | 109 |  |  | Heating Stage 2 Status | 1714 | 109 | [27 empty] | 101128
Group |  | FALSE | Views.Trend.Heating.Stage 3 | Stage 3 | 1714 | 33 |  |  | Stage 3 | 1714 | 33 | York RTU.Heating Control.Staged Heat Control.Number of Heating Stages Installed:Present Value > 2
Trend |  |  | Views.Trend.Heating.Stage 3 | W3 - Thermostat | 1675 | 156 |  |  | W3-Tstat | 1709 | 17 | [27 empty] | 101018
Trend |  |  | Views.Trend.Heating.Stage 3 | Heating Stage Command 3 | 1714 | 151 |  |  | Heating Stage Command 3 | 1714 | 151 | [27 empty] | 101129
Trend |  |  | Views.Trend.Heating.Stage 3 | Heating Stage 3 Status | 1714 | 115 |  |  | Heating Stage 3 Status | 1714 | 115 | [27 empty] | 101130
Group |  | FALSE | Views.Trend.Fan | Fan | 1714 | 10 |  |  | Fan | 1714 | 10
Group |  | FALSE | Views.Trend.Fan.Indoor Fan | Indoor Fan | 1714 | 16 |  |  | Indoor Fan | 1714 | 16
Trend |  |  | Views.Trend.Fan.Indoor Fan | G - Thermostat | 1675 | 157 |  |  | G-Tstat | 1709 | 18 | [27 empty] | 101019
Trend |  |  | Views.Trend.Fan.Indoor Fan | Fan Status | 1675 | 168 |  |  | Fan-S | 1709 | 66 | [27 empty] | 101027
Trend |  |  | Views.Trend.Fan.Indoor Fan | Fan Command | 1675 | 181 |  |  | Fan | 1709 | 79 | [27 empty] | 101031
Trend |  |  | Views.Trend.Fan.Indoor Fan | Fan % Command | 1675 | 169 |  |  | FanVFD | 1709 | 67 | [27 empty] | 101028
Trend |  |  | Views.Trend.Fan.Indoor Fan | Air Proving Switch | 1675 | 175 |  |  | APS | 1709 | 73 | [27 empty] | 101029
Group |  | FALSE | Views.Trend.Fan.Exhaust Fan | Exhaust Fan | 1790 | 0 |  |  | Exhaust Fan | 1790 | 0 | York RTU.Exhaust Type:Present Value <> None
Trend |  |  | Views.Trend.Fan.Exhaust Fan | Exhaust Fan Command | 1675 | 235 |  |  | ExFan | 1709 | 309 | [27 empty] | 101138
Trend |  |  | Views.Trend.Fan.Exhaust Fan | Exhaust Fan VFD % Command | 1675 | 236 |  |  | ExFanVFD | 1709 | 310 | [27 empty] | 101139
Group |  | FALSE | Views.Trend.Fan.Condenser Fans | Condenser Fans | 1714 | 213 |  |  | Condenser Fans | 1714 | 213
Trend |  |  | Views.Trend.Fan.Condenser Fans | Condenser Fan 1 | 1675 | 128 |  |  | CN-Fan | 1709 | 109 | [27 empty] | 101036
Trend |  |  | Views.Trend.Fan.Condenser Fans | Condenser Fan 2 | 1675 | 129 |  |  | CF2 | 1709 | 110 | [27 empty] | 101037
Trend |  |  | Views.Trend.Fan.Condenser Fans | Modulating Condenser Fan 1 Output | 2644 | 293 |  |  | ModCondFan1Out | 2645 | 312 | [27 empty] | 101150
Trend |  |  | Views.Trend.Fan.Condenser Fans | Modulating Condenser Fan 2 Output | 2644 | 294 |  |  | ModCondFan2Out | 2645 | 313 | [27 empty] | 101151
Group |  | FALSE | Views.Trend.Sensors | Sensors | 1714 | 26 |  |  | Sensors | 1714 | 26
Trend |  |  | Views.Trend.Sensors | Space Temperature Input | 1675 | 164 |  |  | ST | 1709 | 32 | [27 empty] | 101010
Trend |  |  | Views.Trend.Sensors | Supply Air Temperature | 1675 | 182 |  |  | SAT | 1709 | 80 | [27 empty] | 101032
Trend |  |  | Views.Trend.Sensors | Mixed Air Temperature | 1675 | 62 |  |  | MAT | 1709 | 293 | [27 empty] | 101135
Trend |  |  | Views.Trend.Sensors | Operational Space Temperature | 1675 | 15 |  |  | OprST | 1709 | 28 | [27 empty] | 101022
Trend |  |  | Views.Trend.Sensors | Operational Indoor Air Quality | 1675 | 165 |  |  | OprIAQ | 1709 | 34 | [27 empty] | 101023
Trend |  |  | Views.Trend.Sensors | Operational Space Humidity | 1675 | 23 |  |  | OprSH | 1709 | 39 | [27 empty] | 101024
Trend |  |  | Views.Trend.Sensors | Operational Outdoor Air Temperature | 1675 | 36 |  |  | OprOAT | 1709 | 52 | [27 empty] | 101025
Trend |  |  | Views.Trend.Sensors | Operational Outdoor Air Quality | 1675 | 45 |  |  | OprOAQ | 1709 | 61 | [27 empty] | 101026
Group |  | FALSE | Views.Trend.Economizer | Economizer | 1714 | 8 |  |  | Economizer | 1714 | 8 | York RTU.System Controllers.Econ Controller:Present Value <> Not Present
Trend |  |  | Views.Trend.Economizer | Economizer Damper % Command | 1675 | 51 |  |  | Econ | 1709 | 282 | [27 empty] | 101132
Trend |  |  | Views.Trend.Economizer | Econ Free Cooling Available | 1675 | 52 |  |  | Econ-Free | 1709 | 283 | [27 empty] | 101133
Trend |  |  | Views.Trend.Economizer | Economizer Status | 1675 | 53 |  |  | Econ-S | 1709 | 284 | [27 empty] | 101134
Trend |  |  | Views.Trend.Economizer | Return Air Enthalpy | 1675 | 64 |  |  | RA-Enth | 1709 | 296 | [27 empty] | 101137
Trend |  |  | Views.Trend.Economizer | Building Pressure Setpoint | 1675 | 240 |  |  | Bldg-Sp | 1709 | 314 | [27 empty] | 101140
Trend |  |  | Views.Trend.Economizer | Building Static Pressure | 1675 | 241 |  |  | BldgPres | 1709 | 315 | [27 empty] | 101141
Group |  | FALSE | Views.Trend.Misc | Misc | 1714 | 18 |  |  | Misc | 1714 | 18
Group |  | FALSE | Views.Trend.Misc.Heat Pump | Heat Pump | 1714 | 180 |  |  | Heat Pump | 1714 | 180 | York RTU.Heat Pump Control.Number of Heat Pump Stages Installed:Present Value > 0
Trend |  |  | Views.Trend.Misc.Heat Pump | Reversing Valve | 1675 | 482 |  |  | RevVlv | 1709 | 613 | [27 empty] | 101131
Group |  | FALSE | Views.Trend.Misc.Hot Gas Reheat | Hot Gas Reheat | 1714 | 13 |  |  | Hot Gas Reheat | 1714 | 13 | York RTU.Hot Gas Reheat.Hot Gas Reheat Enabled For Operation:Present Value = Yes
Trend |  |  | Views.Trend.Misc.Hot Gas Reheat | Hot Gas Reheat Command | 1675 | 250 |  |  | HGR | 1709 | 324 | [27 empty] | 101142
Trend |  |  | Views.Trend.Misc.Hot Gas Reheat | Hot Gas Reheat Status | 1675 | 251 |  |  | HGR-S | 1709 | 325 | [27 empty] | 101143
Trend |  |  | Views.Trend.Misc.Hot Gas Reheat | Hot Gas Reheat Humidity Setpoint | 1675 | 252 |  |  | HGRHum-Sp | 1709 | 326 | [27 empty] | 101144
Group |  | FALSE | Views.Trend.Misc.Demand Ventilation | Demand Ventilation | 1714 | 7 |  |  | Demand Ventilation | 1714 | 7
Trend |  |  | Views.Trend.Misc.Demand Ventilation | Fresh Air Intake Setpoint | 1675 | 255 |  |  | MOAFlow-Sp | 1709 | 329 | [27 empty] | 101145
Trend |  |  | Views.Trend.Misc.Demand Ventilation | Fresh Air Intake Value | 1675 | 256 |  |  | Fr Air | 1709 | 330 | [27 empty] | 101146
Group |  | FALSE | Views.Trend.Fault | Fault | 1714 | 214 |  |  | Fault | 1714 | 214
Group |  | FALSE | Views.Trend.Fault.Misc | Misc | 1714 | 18 |  |  | Misc | 1714 | 18
Trend |  |  | Views.Trend.Fault.Misc | X-OUT | 1675 | 159 |  |  | X-Out | 1709 | 20 | [27 empty] | 101020
Trend |  |  | Views.Trend.Fault.Misc | Dirty Filter Switch | 1675 | 180 |  |  | DFS | 1709 | 78 | [27 empty] | 101030
Trend |  |  | Views.Trend.Fault.Misc | A2L Leak Detector Alarm | 1714 | 276 |  |  | A2LLeakAlarm | 1709 | 787 | [27 empty] | 101165
Trend |  |  | Views.Trend.Fault.Misc | A2L Leak Detector Alarm-Lockout | 1714 | 280 |  |  | A2LLeakAlarm-LO | 1709 | 791 | [27 empty] | 101166
Trend |  |  | Views.Trend.Fault.Misc | Condensate Overflow Switch | 1714 | 277 |  |  | COS | 1709 | 788 | [27 empty] | 101167
Group |  | FALSE | Views.Trend.Fault.Heating Stage 1 | Heating Stage 1 | 1714 | 215 |  |  | Heating Stage 1 | 1714 | 215 | York RTU.Heating Control.Staged Heat Control.Number of Heating Stages Installed:Present Value > 0
Trend |  |  | Views.Trend.Fault.Heating Stage 1 | Heat Limit1 Switch | 1675 | 121 |  |  | Limit | 1709 | 233 | [27 empty] | 101117
Trend |  |  | Views.Trend.Fault.Heating Stage 1 | Heat Limit1 Switch Lockout | 1675 | 122 |  |  | LimitLO | 1709 | 234 | [27 empty] | 101118
Group |  | FALSE | Views.Trend.Fault.Heating Stage 2 | Heating Stage 2 | 1714 | 216 |  |  | Heating Stage 2 | 1714 | 216 | York RTU.Heating Control.Staged Heat Control.Number of Heating Stages Installed:Present Value > 1
Trend |  |  | Views.Trend.Fault.Heating Stage 2 | Heat Limit2 Switch | 1675 | 123 |  |  | Lim2 | 1709 | 235 | [27 empty] | 101119
Trend |  |  | Views.Trend.Fault.Heating Stage 2 | Heat Limit2 Switch Lockout | 1675 | 124 |  |  | Lim2LO | 1709 | 236 | [27 empty] | 101120
Group |  | FALSE | Views.Trend.Fault.Heating Stage 3 | Heating Stage 3 | 1714 | 217 |  |  | Heating Stage 3 | 1714 | 217 | York RTU.Heating Control.Staged Heat Control.Number of Heating Stages Installed:Present Value > 2
Trend |  |  | Views.Trend.Fault.Heating Stage 3 | Heat Limit3 Switch | 1675 | 125 |  |  | Lim3 | 1709 | 237 | [27 empty] | 101121
Trend |  |  | Views.Trend.Fault.Heating Stage 3 | Heat Limit3 Switch Lockout | 1675 | 126 |  |  | Lim3LO | 1709 | 238 | [27 empty] | 101122
Group |  | FALSE | Views.Trend.Fault.Cooling Stage 1 | Cooling Stage 1 | 1714 | 218 |  |  | Cooling Stage 1 | 1714 | 218
Trend |  |  | Views.Trend.Fault.Cooling Stage 1 | High Pressure Limit | 1675 | 93 |  |  | HPS1 | 1709 | 156 | [27 empty] | 101042
Trend |  |  | Views.Trend.Fault.Cooling Stage 1 | High Pressure Lockout | 1675 | 94 |  |  | HPS1-LO | 1709 | 160 | [27 empty] | 101043
Trend |  |  | Views.Trend.Fault.Cooling Stage 1 | Low Pressure Limit | 1675 | 95 |  |  | LPS1 | 1709 | 164 | [27 empty] | 101044
Trend |  |  | Views.Trend.Fault.Cooling Stage 1 | Low Pressure Lockout | 1675 | 96 |  |  | LPS1-LO | 1709 | 168 | [27 empty] | 101045
Trend |  |  | Views.Trend.Fault.Cooling Stage 1 | Freeze Condition | 1675 | 97 |  |  | FS1 | 1709 | 172 | [27 empty] | 101046
Trend |  |  | Views.Trend.Fault.Cooling Stage 1 | Freeze Condition Lockout | 1675 | 98 |  |  | FS1-LO | 1709 | 176 | [27 empty] | 101047
Trend |  |  | Views.Trend.Fault.Cooling Stage 1 | Evaporator Coil Temp | 1675 | 100 |  |  | EC1 | 1709 | 180 | [27 empty] | 101048
Trend |  |  | Views.Trend.Fault.Cooling Stage 1 | Condenser Coil Temp | 1675 | 102 |  |  | CC1 | 1709 | 184 | [27 empty] | 101049
Group |  | FALSE | Views.Trend.Fault.Cooling Stage 2 | Cooling Stage 2 | 1714 | 219 |  |  | Cooling Stage 2 | 1714 | 219 | York RTU.Cooling Control.Number of Cooling Stages Installed:Present Value > 1
Trend |  |  | Views.Trend.Fault.Cooling Stage 2 | High Pressure Limit | 1675 | 93 |  |  | HPS2 | 1709 | 157 | [27 empty] | 101052
Trend |  |  | Views.Trend.Fault.Cooling Stage 2 | High Pressure Lockout | 1675 | 94 |  |  | HPS2-LO | 1709 | 161 | [27 empty] | 101053
Trend |  |  | Views.Trend.Fault.Cooling Stage 2 | Low Pressure Limit | 1675 | 95 |  |  | LPS2 | 1709 | 165 | [27 empty] | 101054
Trend |  |  | Views.Trend.Fault.Cooling Stage 2 | Low Pressure Lockout | 1675 | 96 |  |  | LPS2-LO | 1709 | 169 | [27 empty] | 101055
Trend |  |  | Views.Trend.Fault.Cooling Stage 2 | Freeze Condition | 1675 | 97 |  |  | FS2 | 1709 | 173 | [27 empty] | 101056
Trend |  |  | Views.Trend.Fault.Cooling Stage 2 | Freeze Condition Lockout | 1675 | 98 |  |  | FS2-LO | 1709 | 177 | [27 empty] | 101057
Trend |  |  | Views.Trend.Fault.Cooling Stage 2 | Evaporator Coil Temp | 1675 | 100 |  |  | EC2 | 1709 | 181 | [27 empty] | 101058
Trend |  |  | Views.Trend.Fault.Cooling Stage 2 | Condenser Coil Temp | 1675 | 102 |  |  | CC2 | 1709 | 185 | [27 empty] | 101059
Group |  | FALSE | Views.Trend.Fault.Cooling Stage 3 | Cooling Stage 3 | 1714 | 220 |  |  | Cooling Stage 3 | 1714 | 220 | York RTU.Cooling Control.Number of Cooling Stages Installed:Present Value > 2
Trend |  |  | Views.Trend.Fault.Cooling Stage 3 | High Pressure Limit | 1675 | 93 |  |  | HPS3 | 1709 | 158 | [27 empty] | 101062
Trend |  |  | Views.Trend.Fault.Cooling Stage 3 | High Pressure Lockout | 1675 | 94 |  |  | HPS3-LO | 1709 | 162 | [27 empty] | 101063
Trend |  |  | Views.Trend.Fault.Cooling Stage 3 | Low Pressure Limit | 1675 | 95 |  |  | LPS3 | 1709 | 166 | [27 empty] | 101064
Trend |  |  | Views.Trend.Fault.Cooling Stage 3 | Low Pressure Lockout | 1675 | 96 |  |  | LPS3-LO | 1709 | 170 | [27 empty] | 101065
Trend |  |  | Views.Trend.Fault.Cooling Stage 3 | Freeze Condition | 1675 | 97 |  |  | FS3 | 1709 | 174 | [27 empty] | 101066
Trend |  |  | Views.Trend.Fault.Cooling Stage 3 | Freeze Condition Lockout | 1675 | 98 |  |  | FS3-LO | 1709 | 178 | [27 empty] | 101067
Trend |  |  | Views.Trend.Fault.Cooling Stage 3 | Evaporator Coil Temp | 1675 | 100 |  |  | EC3 | 1709 | 182 | [27 empty] | 101068
Trend |  |  | Views.Trend.Fault.Cooling Stage 3 | Condenser Coil Temp | 1675 | 102 |  |  | CC3 | 1709 | 186 | [27 empty] | 101069
Group |  | FALSE | Views.Trend.Fault.Cooling Stage 4 | Cooling Stage 4 | 1714 | 221 |  |  | Cooling Stage 4 | 1714 | 221 | York RTU.Cooling Control.Number of Cooling Stages Installed:Present Value > 3
Trend |  |  | Views.Trend.Fault.Cooling Stage 4 | High Pressure Limit | 1675 | 93 |  |  | HPS4 | 1709 | 159 | [27 empty] | 101072
Trend |  |  | Views.Trend.Fault.Cooling Stage 4 | High Pressure Lockout | 1675 | 94 |  |  | HPS4-LO | 1709 | 163 | [27 empty] | 101073
Trend |  |  | Views.Trend.Fault.Cooling Stage 4 | Low Pressure Limit | 1675 | 95 |  |  | LPS4 | 1709 | 167 | [27 empty] | 101074
Trend |  |  | Views.Trend.Fault.Cooling Stage 4 | Low Pressure Lockout | 1675 | 96 |  |  | LPS4-LO | 1709 | 171 | [27 empty] | 101075
Trend |  |  | Views.Trend.Fault.Cooling Stage 4 | Freeze Condition | 1675 | 97 |  |  | FS4 | 1709 | 175 | [27 empty] | 101076
Trend |  |  | Views.Trend.Fault.Cooling Stage 4 | Freeze Condition Lockout | 1675 | 98 |  |  | FS4-LO | 1709 | 179 | [27 empty] | 101077
Trend |  |  | Views.Trend.Fault.Cooling Stage 4 | Evaporator Coil Temp | 1675 | 100 |  |  | EC4 | 1709 | 183 | [27 empty] | 101078
Trend |  |  | Views.Trend.Fault.Cooling Stage 4 | Condenser Coil Temp | 1675 | 102 |  |  | CC4 | 1709 | 187 | [27 empty] | 101079
Group |  | FALSE | Views.Trend.Diagnostics | Diagnostics | 1714 | 198 |  |  | Diagnostics | 1714 | 198 | York RTU.System Controllers.FDD Manager Controller:Present Value <> Not Present
Group |  | FALSE | Views.Trend.Diagnostics.Cooling Stage 1 | Cooling Stage 1 | 1714 | 218 |  |  | Cooling Stage 1 | 1714 | 218
Trend |  |  | Views.Trend.Diagnostics.Cooling Stage 1 | Suction Pressure | 1675 | 194 |  |  | SLP-1 | 1709 | 188 | [27 empty] | 101080
Trend |  |  | Views.Trend.Diagnostics.Cooling Stage 1 | Liquid Pressure | 1675 | 195 |  |  | LLP-1 | 1709 | 192 | [27 empty] | 101081
Trend |  |  | Views.Trend.Diagnostics.Cooling Stage 1 | Discharge Line Pressure 1 | 2644 | 378 |  |  | DLP1 | 2645 | 386 | [27 empty] | 101153
Trend |  |  | Views.Trend.Diagnostics.Cooling Stage 1 | Suction Temperature | 1675 | 196 |  |  | SLT-1 | 1709 | 196 | [27 empty] | 101082
Trend |  |  | Views.Trend.Diagnostics.Cooling Stage 1 | Liquid Temperature | 1675 | 197 |  |  | LLT-1 | 1709 | 200 | [27 empty] | 101083
Trend |  |  | Views.Trend.Diagnostics.Cooling Stage 1 | Discharge Line Temperature 1 | 2644 | 380 |  |  | DLT1 | 2645 | 388 | [27 empty] | 101154
Trend |  |  | Views.Trend.Diagnostics.Cooling Stage 1 | Suction Superheat 1 | 2644 | 366 |  |  | SucSuperheat1 | 2645 | 374 | [27 empty] | 101164
Group |  | FALSE | Views.Trend.Diagnostics.Cooling Stage 2 | Cooling Stage 2 | 1714 | 219 |  |  | Cooling Stage 2 | 1714 | 219 | York RTU.Cooling Control.Number of Cooling Stages Installed:Present Value > 1
Trend |  |  | Views.Trend.Diagnostics.Cooling Stage 2 | Suction Pressure | 1675 | 194 |  |  | SLP-2 | 1709 | 189 | [27 empty] | 101089
Trend |  |  | Views.Trend.Diagnostics.Cooling Stage 2 | Liquid Pressure | 1675 | 195 |  |  | LLP-2 | 1709 | 193 | [27 empty] | 101090
Trend |  |  | Views.Trend.Diagnostics.Cooling Stage 2 | Discharge Line Pressure 2 | 2644 | 379 |  |  | DLP2 | 2645 | 387 | [27 empty] | 101155
Trend |  |  | Views.Trend.Diagnostics.Cooling Stage 2 | Suction Temperature | 1675 | 196 |  |  | SLT-2 | 1709 | 197 | [27 empty] | 101091
Trend |  |  | Views.Trend.Diagnostics.Cooling Stage 2 | Liquid Temperature | 1675 | 197 |  |  | LLT-2 | 1709 | 201 | [27 empty] | 101092
Trend |  |  | Views.Trend.Diagnostics.Cooling Stage 2 | Discharge Line Temperature 2 | 2644 | 381 |  |  | DLT2 | 2645 | 389 | [27 empty] | 101156
Group |  | FALSE | Views.Trend.Diagnostics.Cooling Stage 3 | Cooling Stage 3 | 1714 | 220 |  |  | Cooling Stage 3 | 1714 | 220 | York RTU.Cooling Control.Number of Cooling Stages Installed:Present Value > 2
Trend |  |  | Views.Trend.Diagnostics.Cooling Stage 3 | Suction Pressure | 1675 | 194 |  |  | SLP-3 | 1709 | 190 | [27 empty] | 101098
Trend |  |  | Views.Trend.Diagnostics.Cooling Stage 3 | Liquid Pressure | 1675 | 195 |  |  | LLP-3 | 1709 | 194 | [27 empty] | 101099
Trend |  |  | Views.Trend.Diagnostics.Cooling Stage 3 | Suction Temperature | 1675 | 196 |  |  | SLT-3 | 1709 | 198 | [27 empty] | 101100
Trend |  |  | Views.Trend.Diagnostics.Cooling Stage 3 | Liquid Temperature | 1675 | 197 |  |  | LLT-3 | 1709 | 202 | [27 empty] | 101101
Group |  | FALSE | Views.Trend.Diagnostics.Cooling Stage 4 | Cooling Stage 4 | 1714 | 221 |  |  | Cooling Stage 4 | 1714 | 221 | York RTU.Cooling Control.Number of Cooling Stages Installed:Present Value > 3
Trend |  |  | Views.Trend.Diagnostics.Cooling Stage 4 | Suction Pressure | 1675 | 194 |  |  | SLP-4 | 1709 | 191 | [27 empty] | 101107
Trend |  |  | Views.Trend.Diagnostics.Cooling Stage 4 | Liquid Pressure | 1675 | 195 |  |  | LLP-4 | 1709 | 195 | [27 empty] | 101108
Trend |  |  | Views.Trend.Diagnostics.Cooling Stage 4 | Suction Temperature | 1675 | 196 |  |  | SLT-4 | 1709 | 199 | [27 empty] | 101109
Trend |  |  | Views.Trend.Diagnostics.Cooling Stage 4 | Liquid Temperature | 1675 | 197 |  |  | LLT-4 | 1709 | 203 | [27 empty] | 101110
View | FALSE |  | Views.Set Schedule | Set Schedule | 1712 | 25 |  | Views.Schedule | Schedule | 1712 | 52
Schedule |  |  | Views.Set Schedule | Occupancy Schedule | 1667 | 2 |  | Views.Schedule | Occupancy Schedule | 1667 | 2 | [27 empty] | 10133

## FC-Bus BACnet
Model Fullname | Attribute | Object Type | Object Id | Object Name | Obj. Name SetId | Obj. Name EnumId | Obj. Custom Name | Enum Set / Range | Remarks | Write-able | Data Type Id | Display Prec. (IP) | Unit (IP) | Unit Id (IP) | Min Value (IP) | Max Value (IP) | Min Prop. (IP) | Max Prop. (IP) | Display Prec. (SI) | Unit (SI) | Unit Id (SI) | Min Value (SI) | Max Value (SI) | Min Prop. (SI) | Max Prop. (SI) | Prop. Id | EM Object Id
York RTU | Heating Control Type | MV | 29501 | Htg-Type | 1709 | 6 |  | 0 = Staged 1 = Proportional |  | TRUE | 9 |  | Heat Cool Type | 1608 | [5 empty] | Heat Cool Type | 1608 |  |  |  |  | 7006 | 1
York RTU | Exhaust Type | MV | 29503 | ExFType | 1709 | 8 |  | 0 = None 1 = Non-Modulating 2 = Modulating Damper 3 = Variable Frequency Fan |  | TRUE | 9 |  | SE RTU Exhaust Setup | 1639 | [5 empty] | SE RTU Exhaust Setup | 1639 |  |  |  |  | 7008 | 1
York RTU.Thermostat Control | Y1 - Thermostat | MV | 29504 | Y1-Tstat | 1709 | 11 |  | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7000 | 2
York RTU.Thermostat Control | Y2 - Thermostat | MV | 29505 | Y2-Tstat | 1709 | 12 |  | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7001 | 2
York RTU.Thermostat Control | Y3 - Thermostat | MV | 29506 | Y3-Tstat | 1709 | 13 |  | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7002 | 2
York RTU.Thermostat Control | Y4 - Thermostat | MV | 29507 | Y4-Tstat | 1709 | 14 |  | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7003 | 2
York RTU.Thermostat Control | W1 - Thermostat | MV | 29508 | W1-Tstat | 1709 | 15 |  | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7004 | 2
York RTU.Thermostat Control | W2 - Thermostat | MV | 29509 | W2-Tstat | 1709 | 16 |  | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7005 | 2
York RTU.Thermostat Control | W3 - Thermostat | MV | 29510 | W3-Tstat | 1709 | 17 |  | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7006 | 2
York RTU.Thermostat Control | G - Thermostat | MV | 29511 | G-Tstat | 1709 | 18 |  | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7007 | 2
York RTU.Thermostat Control | Local Occupancy Input - Thermostat | MV | 29512 | Occ-Tstat | 1709 | 19 |  | 0 = On 1 = Off |  | FALSE | 9 |  | On/Off | 1686 | [5 empty] | On/Off | 1686 |  |  |  |  | 7008 | 2
York RTU.Thermostat Control | X-OUT | MV | 29513 | X-Out | 1709 | 20 |  | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7009 | 2
York RTU.Thermostat Control | Thermostat Only Control Enabled | MV | 29514 | Tstat-Only | 1709 | 21 |  | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7010 | 2
York RTU.HVAC Zone | Occupancy Input Source | MV | 29515 | OccSrc | 1709 | 22 |  | 0 = Local Input 1 = Local Network Sensor 2 = BAS Network Request 3 = Local Schedule 4 = Temporary Occupancy |  | FALSE | 9 |  | Effective Occupancy Source | 1668 | [5 empty] | Effective Occupancy Source | 1668 |  |  |  |  | 7000 | 25
York RTU.HVAC Zone | Occupancy Input | MV | 29516 | OCC | 1709 | 380 |  | 0 = Occupied 1 = Unoccupied |  | FALSE | 9 |  | SE RTU Unocc/Occ | 1658 | [5 empty] | SE RTU Unocc/Occ | 1658 |  |  |  |  | 7030 | 25
York RTU.HVAC Zone | Operational Occupancy | MV | 29517 | OprOcc | 1709 | 23 |  | 0 = Occupied 1 = UnOccupied 2 = Bypass 3 = Standby |  | FALSE | 9 |  | Occ Effective | 345 | [5 empty] | Occ Effective | 345 |  |  |  |  | 7001 | 25
York RTU.HVAC Zone | Occupancy Mode | MV | 29518 | OccMode | 1709 | 24 |  | 0 = Schedule 1 = External |  | TRUE | 9 |  | SE Occupancy Mode | 1728 | [5 empty] | SE Occupancy Mode | 1728 |  |  |  |  | 7002 | 25
York RTU.HVAC Zone | Network Temporary Occupancy Request | MV | 29519 | NetTempOcc | 1709 | 25 |  | 0 = False 1 = True |  | TRUE | 9 |  | False/True | 1701 | [5 empty] | False/True | 1701 |  |  |  |  | 7003 | 25
York RTU.HVAC Zone | Network Occupancy Request | MV | 29520 | NetOcc | 1709 | 26 |  | 0 = Occupied 1 = UnOccupied 2 = Not Set |  | TRUE | 9 |  | Occ Sensor | 344 | [5 empty] | Occ Sensor | 344 |  |  |  |  | 7004 | 25
York RTU.HVAC Zone | Temporary Occupancy Timeout | AV | 29521 | TempOccTimeout | 1709 | 27 |  | 30 ... 600 minutes |  | TRUE | 17 | 1s | minutes | 507:72 | 30 | 600 |  |  | 1s | minutes | 507:72 | 30 | 600 |  |  | 7005 | 25
York RTU.HVAC Zone | Operational Space Temperature | AV | 29522 | OprST | 1709 | 28 |  | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7006 | 25
York RTU.HVAC Zone | Space Temperature Source | MV | 29523 | STSrc | 1709 | 29 |  | 0 = Unreliable 1 = Return Air Temp 2 = Local Input 3 = Network Sensor ... |  | FALSE | 9 |  | Effective Input Source | 1715 | [5 empty] | Effective Input Source | 1715 |  |  |  |  | 7007 | 25
York RTU.HVAC Zone | Space Temperature Alarm Setpoint Offset | AV | 29524 | STAlarmOffset | 1709 | 30 |  | 0 ... 25 delta deg F (0 ... 14 delta deg C) |  | TRUE | 4 | 1s | delta deg F | 507:120 | 0 | 25 |  |  | 1s | delta deg C | 507:359 | 0 | 14 |  |  | 7008 | 25
York RTU.HVAC Zone | Space Temperature Alarm Time Delay | AV | 29525 | STAlarmDelay | 1709 | 31 |  | 0 ... 120 minutes |  | TRUE | 17 | 1s | minutes | 507:72 | 0 | 120 |  |  | 1s | minutes | 507:72 | 0 | 120 |  |  | 7009 | 25
York RTU.HVAC Zone | Network Override Space Temperature | AV | 29526 | NetST | 1709 | 33 |  | 0 ... 100 deg F (4 ... 38 deg C) |  | TRUE | 4 | 10ths | deg F | 507:64 | 0 | 100 |  |  | 10ths | deg C | 507:62 | 4 | 38 |  |  | 7011 | 25
York RTU.HVAC Zone | Operational Indoor Air Quality | AV | 29527 | OprIAQ | 1709 | 34 |  | ppm |  | FALSE | 4 | 10s | ppm | 507:96 |  |  |  |  | 10s | ppm | 507:96 |  |  |  |  | 7012 | 25
York RTU.HVAC Zone | Indoor Air Quality Source | MV | 29528 | IAQSrc | 1709 | 35 |  | 0 = Unreliable 1 = Local Input 2 = Network Sensor 3 = High Priority ... |  | FALSE | 9 |  | Effective Input Source 2 | 1732 | [5 empty] | Effective Input Source 2 | 1732 |  |  |  |  | 7013 | 25
York RTU.HVAC Zone | Indoor Air Quality Sensor Range | AV | 29529 | IAQRange | 1709 | 37 |  | 0 ... 5000 ppm |  | TRUE | 4 | 1s | ppm | 507:96 | 0 | 5000 |  |  | 1s | ppm | 507:96 | 0 | 5000 |  |  | 7015 | 25
York RTU.HVAC Zone | Network Override Indoor Air Quality | AV | 29530 | NetIAQ | 1709 | 38 |  | 0 ... 5000 ppm |  | TRUE | 4 | 10s | ppm | 507:96 | 0 | 5000 |  |  | 10s | ppm | 507:96 | 0 | 5000 |  |  | 7016 | 25
York RTU.HVAC Zone | Operational Space Humidity | AV | 29531 | OprSH | 1709 | 39 |  | %RH |  | FALSE | 4 | 10ths | %RH | 507:29 |  |  |  |  | 10ths | %RH | 507:29 |  |  |  |  | 7017 | 25
York RTU.HVAC Zone | Space Humidity Source | MV | 29532 | SHSrc | 1709 | 40 |  | 0 = Unreliable 1 = Local Input 2 = Network Sensor 3 = High Priority ... |  | FALSE | 9 |  | Effective Input Source 2 | 1732 | [5 empty] | Effective Input Source 2 | 1732 |  |  |  |  | 7018 | 25
York RTU.HVAC Zone | Network Override Zone Humidity | AV | 29533 | NetSH | 1709 | 42 |  | 0 ... 100 %RH |  | TRUE | 4 | 10ths | %RH | 507:29 | 0 | 100 |  |  | 10ths | %RH | 507:29 | 0 | 100 |  |  | 7020 | 25
York RTU.HVAC Zone | Operating Fan Request | MV | 29534 | OprFanReq | 1709 | 43 |  | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7021 | 25
York RTU.HVAC Zone | Fan Request Source | MV | 29535 | FanReqSrc | 1709 | 44 |  | 0 = Unreliable 1 = Local Input 2 = Network Sensor 3 = High Priority ... |  | FALSE | 9 |  | Effective Input Source 2 | 1732 | [5 empty] | Effective Input Source 2 | 1732 |  |  |  |  | 7022 | 25
York RTU.HVAC Zone | Network Override Fan Request | MV | 29536 | NetFanReq | 1709 | 45 |  | 0 = Off 1 = On |  | TRUE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7023 | 25
York RTU.HVAC Zone | Operational Space Temperature Setpoint Offset | AV | 29537 | OprSSO | 1709 | 46 |  | delta deg F (delta deg C) |  | FALSE | 4 | 10ths | delta deg F | 507:120 |  |  |  |  | 10ths | delta deg C | 507:359 |  |  |  |  | 7024 | 25
York RTU.HVAC Zone | Space Temperature Setpoint Offset Source | MV | 29538 | SSOSrc | 1709 | 47 |  | 0 = Unreliable 1 = Local Input 2 = Network Sensor 3 = High Priority ... |  | FALSE | 9 |  | Effective Input Source 2 | 1732 | [5 empty] | Effective Input Source 2 | 1732 |  |  |  |  | 7025 | 25
York RTU.HVAC Zone | Space Temp Setpoint Offset Input | AV | 29539 | SSO | 1709 | 48 |  | delta deg F (delta deg C) |  | FALSE | 4 | 10ths | delta deg F | 507:120 |  |  |  |  | 10ths | delta deg C | 507:359 |  |  |  |  | 7026 | 25
York RTU.HVAC Zone | Network Override Space Setpoint Offset | AV | 29540 | NetSSO | 1709 | 49 |  | -5 ... 5 delta deg F (-3 ... 3 delta deg C) |  | TRUE | 4 | 10ths | delta deg F | 507:120 | -5 | 5 |  |  | 10ths | delta deg C | 507:359 | -3 | 3 |  |  | 7027 | 25
York RTU.Weather Information | Operational Outdoor Air Temperature | AV | 29541 | OprOAT | 1709 | 52 |  | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7000 | 26
York RTU.Weather Information | Outdoor Air Temperature Source | MV | 29542 | OATSrc | 1709 | 53 |  | 0 = Unreliable 1 = Local Input 2 = Network Sensor 3 = High Priority ... |  | FALSE | 9 |  | Effective Input Source 2 | 1732 | [5 empty] | Effective Input Source 2 | 1732 |  |  |  |  | 7001 | 26
York RTU.Weather Information | Network Override Outdoor Air Temperature | AV | 29543 | NetOAT | 1709 | 55 |  | -50 ... 125 deg F (-18 ... 52 deg C) |  | TRUE | 4 | 10ths | deg F | 507:64 | -50 | 125 |  |  | 10ths | deg C | 507:62 | -18 | 52 |  |  | 7003 | 26
York RTU.Weather Information | Operational Outdoor Air Humidity | AV | 29544 | OprOAH | 1709 | 56 |  | %RH |  | FALSE | 4 | 1s | %RH | 507:29 |  |  |  |  | 1s | %RH | 507:29 |  |  |  |  | 7004 | 26
York RTU.Weather Information | Outdoor Air Enthalpy | AV | 29545 | OA-Enth | 1709 | 57 |  | Btu/lb (kJ/kg) |  | FALSE | 4 | 1s | Btu/lb | 507:117 |  |  |  |  | 1s | kJ/kg | 507:125 |  |  |  |  | 7005 | 26
York RTU.Weather Information | Network Override Outdoor Air Humidity | AV | 29546 | NetOAH | 1709 | 60 |  | 0 ... 100 %RH |  | TRUE | 4 | 10ths | %RH | 507:29 | 0 | 100 |  |  | 10ths | %RH | 507:29 | 0 | 100 |  |  | 7008 | 26
York RTU.Weather Information | Operational Outdoor Air Quality | AV | 29547 | OprOAQ | 1709 | 61 |  | ppm |  | FALSE | 4 | 10s | ppm | 507:96 |  |  |  |  | 10s | ppm | 507:96 |  |  |  |  | 7009 | 26
York RTU.Weather Information | Outdoor Air Quality Source | MV | 29548 | OAQSrc | 1709 | 62 |  | 0 = Unreliable 1 = Local Input 2 = Network Sensor 3 = High Priority ... |  | FALSE | 9 |  | Effective Input Source 2 | 1732 | [5 empty] | Effective Input Source 2 | 1732 |  |  |  |  | 7010 | 26
York RTU.Weather Information | Network Override Outdoor Air Quality | AV | 29549 | NetOAQ | 1709 | 65 |  | 0 ... 5000 ppm |  | TRUE | 4 | 10s | ppm | 507:96 | 0 | 5000 |  |  | 10s | ppm | 507:96 | 0 | 5000 |  |  | 7013 | 26
York RTU.Fan Control | Fan Status | MV | 29550 | Fan-S | 1709 | 66 |  | 0 = Off-Idle 1 = On-Purge 2 = On-Gas Valve or Limit Fault 3 = On-Defrost ... |  | FALSE | 9 |  | SE RTU Fan Status | 1739 | [5 empty] | SE RTU Fan Status | 1739 |  |  |  |  | 7000 | 3
York RTU.Fan Control | Fan % Command | AV | 29551 | FanVFD | 1709 | 67 |  | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7001 | 3
York RTU.Fan Control | Fan VFD Fault | MV | 29552 | FanVFDFlt | 1709 | 68 |  | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7002 | 3
York RTU.Fan Control | Fan Overload | MV | 29553 | FanOvrload | 1709 | 69 |  | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7003 | 3
York RTU.Fan Control | Fan Accumulated Runtime | AV | 29554 | Fan-RT | 1709 | 70 |  | 0 ... 10000 hours |  | TRUE | 4 | 1s | hours | 507:71 | 0 | 10000 |  |  | 1s | hours | 507:71 | 0 | 10000 |  |  | 7004 | 3
York RTU.Fan Control | Fan Control Type | MV | 29555 | FanCtl-Type | 1709 | 71 |  | 0 = Single Speed 1 = Not Used 2 = Fixed Variable 3 = Variable Speed |  | TRUE | 9 |  | SE RTU Fan Control Type | 1619 | [5 empty] | SE RTU Fan Control Type | 1619 |  |  |  |  | 7005 | 3
York RTU.Fan Control | Air Proving Switch Setup | MV | 29556 | APSSetup | 1709 | 72 |  | 0 = Constant Volume 1 = Variable Volume 2 = None |  | TRUE | 9 |  | Fan Setup | 1622 | [5 empty] | Fan Setup | 1622 |  |  |  |  | 7006 | 3
York RTU.Fan Control | Air Proving Switch | MV | 29557 | APS | 1709 | 73 |  | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7007 | 3
York RTU.Fan Control | Fan On Delay for Cool | AV | 29558 | FanOnDlyCool | 1709 | 74 |  | 0 ... 30 seconds |  | TRUE | 17 | 1s | seconds | 507:73 | 0 | 30 |  |  | 1s | seconds | 507:73 | 0 | 30 |  |  | 7008 | 3
York RTU.Fan Control | Fan Off Delay for Cool | AV | 29559 | FanOffDlyCool | 1709 | 75 |  | 0 ... 255 seconds |  | TRUE | 17 | 1s | seconds | 507:73 | 0 | 255 |  |  | 1s | seconds | 507:73 | 0 | 255 |  |  | 7009 | 3
York RTU.Fan Control | Fan On Delay for Heat | AV | 29560 | FanOnDlyHeat | 1709 | 76 |  | 0 ... 30 seconds |  | TRUE | 17 | 1s | seconds | 507:73 | 0 | 30 |  |  | 1s | seconds | 507:73 | 0 | 30 |  |  | 7010 | 3
York RTU.Fan Control | Fan Off Delay for Heat | AV | 29561 | FanOffDlyHeat | 1709 | 77 |  | 0 ... 255 seconds |  | TRUE | 17 | 1s | seconds | 507:73 | 0 | 255 |  |  | 1s | seconds | 507:73 | 0 | 255 |  |  | 7011 | 3
York RTU.Fan Control | Dirty Filter Switch | MV | 29562 | DFS | 1709 | 78 |  | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7012 | 3
York RTU.Fan Control | Fan Command | MV | 29563 | Fan | 1709 | 79 |  | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7013 | 3
York RTU.Fan Control | Supply Air Temperature | AV | 29564 | SAT | 1709 | 80 |  | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7014 | 3
York RTU.Fan Control | Duct Static Pressure | AV | 29565 | DctPrs | 1709 | 81 |  | in wc (kPa) |  | FALSE | 4 | 100ths | in wc | 507:58 |  |  |  |  | 100ths | kPa | 507:54 |  |  |  |  | 7015 | 3
York RTU.Fan Control | Duct Pressure Setpoint | AV | 29566 | DctPrs-Sp | 1709 | 82 |  | 0 ... 5 in wc (0 ... 1.25 kPa) |  | TRUE | 4 | 100ths | in wc | 507:58 | 0 | 5 |  |  | 100ths | kPa | 507:54 | 0 | 1.25 |  |  | 7016 | 3
York RTU.Fan Control | Duct Pressure Shutdown Setpoint | AV | 29567 | DctShutdownSp | 1709 | 83 |  | 0 ... 5 in wc (0 ... 1.25 kPa) |  | TRUE | 4 | 100ths | in wc | 507:58 | 0 | 5 |  |  | 100ths | kPa | 507:54 | 0 | 1.25 |  |  | 7017 | 3
York RTU.Fan Control | Continuous Fan Operation in Occupied Mode | MV | 29568 | FanOnOcc | 1709 | 84 |  | 0 = Yes 1 = No |  | TRUE | 9 |  | Yes/No | 1698 | [5 empty] | Yes/No | 1698 |  |  |  |  | 7018 | 3
York RTU.Fan Control | Turn Off Continuous Fan Operation When Starting Heat | MV | 29569 | FanOffStartHeat | 1709 | 85 |  | 0 = Yes 1 = No |  | TRUE | 9 |  | Yes/No | 1698 | [5 empty] | Yes/No | 1698 |  |  |  |  | 7019 | 3
York RTU.Fan Control | Occupied: No Heat or Cool % Command | AV | 29570 | FanOnly-%Cmd | 1709 | 86 |  | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7020 | 3
York RTU.Fan Control | Occupied: One Stage of Cool % Command | AV | 29571 | 1ClgStg-%Cmd | 1709 | 87 |  | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7021 | 3
York RTU.Fan Control | Occupied: Two Stage of Cool % Command | AV | 29572 | 2ClgStg-%Cmd | 1709 | 88 |  | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7022 | 3
York RTU.Fan Control | Occupied: One Stage of Heat % Command | AV | 29573 | 1HtgStg-%Cmd | 1709 | 89 |  | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7023 | 3
York RTU.Fan Control | Occupied: Two Stage of Heat % Command | AV | 29574 | 2HtgStg-%Cmd | 1709 | 90 |  | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7024 | 3
York RTU.Cooling Control | Cooling Mode Enabled For Operation | MV | 29575 | Clg-En | 1709 | 91 |  | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7000 | 4
York RTU.Cooling Control | Number of Cooling Stages Installed | AV | 29576 | #ClgStgs | 1709 | 92 |  | 1 ... 4 |  | TRUE | 16 | 1s |  | 507:95 | 1 | 4 |  |  | 1s |  | 507:95 | 1 | 4 |  |  | 7001 | 4
York RTU.Cooling Control | Cooling Status | MV | 29577 | Clg-S | 1709 | 93 |  | 0 = Off-Idle 1 = Thermostat Cooling 2 = Unoccupied Cooling 3 = Occupied Cooling ... |  | FALSE | 9 |  | SE RTU Cooling Control Status | 1740 | [5 empty] | SE RTU Cooling Control Status | 1740 |  |  |  |  | 7002 | 4
York RTU.Cooling Control | Minimum Runtime for a Cooling Stage | AV | 29578 | MinRtCoolStg | 1709 | 94 |  | 3 ... 10 minutes |  | TRUE | 16 | 1s | minutes | 507:72 | 3 | 10 |  |  | 1s | minutes | 507:72 | 3 | 10 |  |  | 7003 | 4
York RTU.Cooling Control | Lead/Lag Equalize Cooling Stage Runtime Enabled | MV | 29579 | LeadLag-En | 1709 | 95 |  | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7004 | 4
York RTU.Cooling Control | Low Ambient Fan Pre-run Time For Cooling | AV | 29580 | LowAmbFanPrerunCool | 1709 | 96 |  | 0 ... 255 seconds |  | TRUE | 17 | 1s | seconds | 507:73 | 0 | 255 |  |  | 1s | seconds | 507:73 | 0 | 255 |  |  | 7005 | 4
York RTU.Cooling Control | OAT Cooling Cutout Enabled | MV | 29581 | ClgOATCutout-En | 1709 | 97 |  | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7006 | 4
York RTU.Cooling Control | OAT Cooling Cutout | AV | 29582 | ClgOATCutout | 1709 | 98 |  | 0 ... 100 deg F (-18 ... 38 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 0 | 100 |  |  | 1s | deg C | 507:62 | -18 | 38 |  |  | 7007 | 4
York RTU.Cooling Control | Economizer Loading Enabled | MV | 29583 | EconLoad-En | 1709 | 99 |  | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7008 | 4
York RTU.Cooling Control | All Compressors Off in Free Cooling | MV | 29584 | AllCompOff-Econ | 1709 | 100 |  | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7009 | 4
York RTU.Cooling Control | Low Ambient Cooling Stages 10 on 5 off Setpoint | AV | 29585 | LowAmb10On5OffSp | 1709 | 101 |  | 0 ... 60 deg F (-18 ... 15 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 0 | 60 |  |  | 1s | deg C | 507:62 | -18 | 15 |  |  | 7010 | 4
York RTU.Cooling Control | Temperature/Humidity (Return) Control Enable | MV | 29586 | TempHumCtrl-En | 1709 | 102 |  | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7011 | 4
York RTU.Cooling Control | Temperature/Humidity Setpoint | AV | 29587 | TempHum-Sp | 1709 | 103 |  | 20 ... 80 %RH |  | TRUE | 4 | 1s | %RH | 507:29 | 20 | 80 |  |  | 1s | %RH | 507:29 | 20 | 80 |  |  | 7012 | 4
York RTU.Cooling Control | Maximum Temperature / Humidity Setpoint Offset | AV | 29588 | MaxTempHumSpOff | 1709 | 104 |  | 0 ... 5 delta deg F (0 ... 3 delta deg C) |  | TRUE | 4 | 10ths | delta deg F | 507:120 | 0 | 5 |  |  | 10ths | delta deg C | 507:359 | 0 | 3 |  |  | 7013 | 4
York RTU.Cooling Control | Temperature / Humidity Value per Degree Offset | AV | 29589 | TempHumValPerDegOff | 1709 | 105 |  | 1 ... 10 %RH |  | TRUE | 4 | 1s | %RH | 507:29 | 1 | 10 |  |  | 1s | %RH | 507:29 | 1 | 10 |  |  | 7014 | 4
York RTU.Cooling Control | SAT Limit for Cooling Enable | MV | 29590 | SATCoolLimit-En | 1709 | 106 |  | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7015 | 4
York RTU.Cooling Control | SAT Limit for Cooling Setpoint | AV | 29591 | SATCoolLimit-Sp | 1709 | 107 |  | 40 ... 65 deg F (4 ... 18 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 40 | 65 |  |  | 1s | deg C | 507:62 | 4 | 18 |  |  | 7016 | 4
York RTU.Cooling Control | Freeze Condition Setpoint | AV | 29592 | Freeze-Sp | 1709 | 108 |  | 20 ... 32 deg F (-7 ... 0 deg C) |  | TRUE | 4 | 10ths | deg F | 507:64 | 20 | 32 |  |  | 10ths | deg C | 507:62 | -7 | 0 |  |  | 7017 | 4
York RTU.Cooling Control | Condenser Fan 1 | MV | 29593 | CN-Fan | 1709 | 109 |  | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7018 | 4
York RTU.Cooling Control | Condenser Fan 2 | MV | 29594 | CF2 | 1709 | 110 |  | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7019 | 4
York RTU.Cooling Control | Unit Type | MV | 29595 | UnitType | 1709 | 111 |  | 0 = Not Used 1 = Package Cool 2 = Package HP 3 = Split Cool ... |  | TRUE | 9 |  | SE RTU Equipment Type | 1685 | [5 empty] | SE RTU Equipment Type | 1685 |  |  |  |  | 7020 | 4
York RTU.Cooling Control | EER | AV | 29596 | EER | 1709 | 112 |  | 0 ... 20 |  | TRUE | 4 | 1s |  | 507:95 | 0 | 20 |  |  | 1s |  | 507:95 | 0 | 20 |  |  | 7021 | 4
York RTU.Cooling Control | Subcooling Goal | AV | 29597 | SubcoolGoal | 1709 | 113 |  | -10 ... 20 deg F (-23 ... -6 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | -10 | 20 |  |  | 1s | deg C | 507:62 | -23 | -6 |  |  | 7022 | 4
York RTU.Cooling Control | Refrigerant Type | MV | 29598 | RefrigType | 1709 | 114 |  | 0 = R22 1 = R12 2 = R500 3 = R134A ... |  | TRUE | 9 |  | SE RTU Refrigerant Type | 1682 | [5 empty] | SE RTU Refrigerant Type | 1682 |  |  |  |  | 7023 | 4
York RTU.Cooling Control | High Side Port Location | MV | 29599 | HiSidePortLoc | 1709 | 115 |  | 0 = Liquid 1 = Discharge |  | TRUE | 9 |  | SE RTU High Side Port | 1681 | [5 empty] | SE RTU High Side Port | 1681 |  |  |  |  | 7024 | 4
York RTU.Cooling Control | Evaporator Coil Type | MV | 29600 | EvapCoil-Type | 1709 | 116 |  | 0 = MicroChannel 1 = Tube and Fin |  | TRUE | 9 |  | Cooling Coil Type | 1722 | [5 empty] | Cooling Coil Type | 1722 |  |  |  |  | 7025 | 4
York RTU.Cooling Control | Condenser Coil Type | MV | 29601 | CondCoil-Type | 1709 | 117 |  | 0 = MicroChannel 1 = Tube and Fin |  | TRUE | 9 |  | Cooling Coil Type | 1722 | [5 empty] | Cooling Coil Type | 1722 |  |  |  |  | 7026 | 4
York RTU.Cooling Control | Indoor Metering Device Type | MV | 29602 | InMeterDev-Type | 1709 | 118 |  | 0 = TxV 1 = FO 2 = TxV Or FO 3 = n |  | TRUE | 9 |  | SE RTU Expansion Device | 1684 | [5 empty] | SE RTU Expansion Device | 1684 |  |  |  |  | 7027 | 4
York RTU.Cooling Control | Outdoor Metering Device Type | MV | 29603 | OutMeterDev-Type | 1709 | 445 |  | 0 = TxV 1 = FO 2 = TxV Or FO 3 = n |  | TRUE | 9 |  | SE RTU Expansion Device | 1684 | [5 empty] | SE RTU Expansion Device | 1684 |  |  |  |  | 7028 | 4
York RTU.Cooling Control | VAV Cooling Supply Air Temp Upper Setpoint | AV | 29604 | SATUp-Sp | 1709 | 119 |  | 41 ... 70 deg F (5 ... 21 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 41 | 70 |  |  | 1s | deg C | 507:62 | 5 | 21 |  |  | 7029 | 4
York RTU.Cooling Control | VAV Cooling Supply Air Temp Lower Setpoint | AV | 29605 | SATLo-Sp | 1709 | 120 |  | 40 ... 69 deg F (4 ... 20 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 40 | 69 |  |  | 1s | deg C | 507:62 | 4 | 20 |  |  | 7030 | 4
York RTU.Cooling Control | VAV Supply Air Temp Reset Setpoint | AV | 29606 | SATRst-Sp | 1709 | 121 |  | 40 ... 85 deg F (4 ... 30 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 40 | 85 |  |  | 1s | deg C | 507:62 | 4 | 30 |  |  | 7031 | 4
York RTU.Cooling Control | VAV Operating Cooling Setpoint | AV | 29607 | OprVAVClg-Sp | 1709 | 122 |  | deg F (deg C) |  | FALSE | 4 | 100ths | deg F | 507:64 |  |  |  |  | 100ths | deg C | 507:62 |  |  |  |  | 7032 | 4
York RTU.Cooling Control | CV Occupied Cooling Setpoint | AV | 29608 | ClgOcc-Sp | 1709 | 123 |  | 45 ... 98 deg F (7 ... 36 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 45 | 98 |  |  | 1s | deg C | 507:62 | 7 | 36 |  |  | 7033 | 4
York RTU.Cooling Control | CV Unoccupied Cooling Setpoint | AV | 29609 | ClgUnocc-Sp | 1709 | 124 |  | 46 ... 99 deg F (8 ... 37 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 46 | 99 |  |  | 1s | deg C | 507:62 | 8 | 37 |  |  | 7034 | 4
York RTU.Cooling Control | CV Operating Cooling Setpoint | AV | 29610 | OprCVClg-Sp | 1709 | 125 |  | deg F (deg C) |  | FALSE | 4 | 100ths | deg F | 507:64 |  |  |  |  | 100ths | deg C | 507:62 |  |  |  |  | 7035 | 4
York RTU.Cooling Control.DX Cooling Circuit 1 | Compressor Stage Command | MV | 29611 | C1 | 1709 | 127 |  | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7001 | 5
York RTU.Cooling Control.DX Cooling Circuit 1 | Compressor Stage Status | MV | 29615 | C1-S | 1709 | 131 |  | 0 = Off-Idle 1 = On-Minimum On Time 2 = On-Normal Command 3 = Off-Cooling Is Disabled ... |  | FALSE | 9 |  | SE RTU DX Cooling Circuit 1 Status | 1741 | [5 empty] | SE RTU DX Cooling Circuit 1 Status | 1741 |  |  |  |  | 7002 | 5
York RTU.Cooling Control.DX Cooling Circuit 1 | Compressor Stage Enabled | MV | 29619 | C1-En | 1709 | 135 |  | 0 = Yes 1 = No |  | TRUE | 9 |  | Yes/No | 1698 | [5 empty] | Yes/No | 1698 |  |  |  |  | 7003 | 5
York RTU.Cooling Control.DX Cooling Circuit 1 | Hot Gas Bypass Present | MV | 29623 | HGP-Inst | 1709 | 139 |  | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7004 | 5
York RTU.Cooling Control.DX Cooling Circuit 1 | Compressor Stage Accumulated Runtime | AV | 29627 | C1RunTim | 1709 | 140 |  | 0 ... 10000 hours |  | TRUE | 4 | 1s | hours | 507:71 | 0 | 10000 |  |  | 1s | hours | 507:71 | 0 | 10000 |  |  | 7005 | 5
York RTU.Cooling Control.DX Cooling Circuit 1 | Min On Time Remaining | AV | 29631 | C1OnTmr | 1709 | 148 |  | seconds |  | FALSE | 17 | 1s | seconds | 507:73 |  |  |  |  | 1s | seconds | 507:73 |  |  |  |  | 7007 | 5
York RTU.Cooling Control.DX Cooling Circuit 1 | Anti-Short Cycle Delay Time Remaining | AV | 29635 | C1ASCDTmr | 1709 | 152 |  | seconds |  | FALSE | 17 | 1s | seconds | 507:73 |  |  |  |  | 1s | seconds | 507:73 |  |  |  |  | 7008 | 5
York RTU.Cooling Control.DX Cooling Circuit 1 | High Pressure Limit | MV | 29639 | HPS1 | 1709 | 156 |  | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7009 | 5
York RTU.Cooling Control.DX Cooling Circuit 1 | High Pressure Lockout | MV | 29643 | HPS1-LO | 1709 | 160 |  | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7010 | 5
York RTU.Cooling Control.DX Cooling Circuit 1 | Low Pressure Limit | MV | 29647 | LPS1 | 1709 | 164 |  | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7011 | 5
York RTU.Cooling Control.DX Cooling Circuit 1 | Low Pressure Lockout | MV | 29651 | LPS1-LO | 1709 | 168 |  | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7012 | 5
York RTU.Cooling Control.DX Cooling Circuit 1 | Freeze Condition | MV | 29655 | FS1 | 1709 | 172 |  | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7013 | 5
York RTU.Cooling Control.DX Cooling Circuit 1 | Freeze Condition Lockout | MV | 29659 | FS1-LO | 1709 | 176 |  | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7014 | 5
York RTU.Cooling Control.DX Cooling Circuit 1 | Evaporator Coil Temp | AV | 29663 | EC1 | 1709 | 180 |  | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7015 | 5
York RTU.Cooling Control.DX Cooling Circuit 1 | Condenser Coil Temp | AV | 29667 | CC1 | 1709 | 184 |  | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7016 | 5
York RTU.Cooling Control.DX Cooling Circuit 2 | Compressor Stage Command | MV | 29612 | C2 | 1709 | 128 |  | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7001 | 7
York RTU.Cooling Control.DX Cooling Circuit 2 | Compressor Stage Status | MV | 29616 | C2-S | 1709 | 132 |  | 0 = Off-Idle 1 = On-Minimum On Time 2 = On-Normal Command 3 = Off-Cooling Is Disabled ... |  | FALSE | 9 |  | SE RTU DX Cooling Circuit 1 Status | 1741 | [5 empty] | SE RTU DX Cooling Circuit 1 Status | 1741 |  |  |  |  | 7002 | 7
York RTU.Cooling Control.DX Cooling Circuit 2 | Compressor Stage Enabled | MV | 29620 | C2-En | 1709 | 136 |  | 0 = Yes 1 = No |  | TRUE | 9 |  | Yes/No | 1698 | [5 empty] | Yes/No | 1698 |  |  |  |  | 7003 | 7
York RTU.Cooling Control.DX Cooling Circuit 2 | Compressor Stage Accumulated Runtime | AV | 29628 | C2RunTim | 1709 | 141 |  | 0 ... 10000 hours |  | TRUE | 4 | 1s | hours | 507:71 | 0 | 10000 |  |  | 1s | hours | 507:71 | 0 | 10000 |  |  | 7005 | 7
York RTU.Cooling Control.DX Cooling Circuit 2 | Min On Time Remaining | AV | 29632 | C2OnTmr | 1709 | 149 |  | seconds |  | FALSE | 17 | 1s | seconds | 507:73 |  |  |  |  | 1s | seconds | 507:73 |  |  |  |  | 7007 | 7
York RTU.Cooling Control.DX Cooling Circuit 2 | Anti-Short Cycle Delay Time Remaining | AV | 29636 | C2ASCDTmr | 1709 | 153 |  | seconds |  | FALSE | 17 | 1s | seconds | 507:73 |  |  |  |  | 1s | seconds | 507:73 |  |  |  |  | 7008 | 7
York RTU.Cooling Control.DX Cooling Circuit 2 | High Pressure Limit | MV | 29640 | HPS2 | 1709 | 157 |  | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7009 | 7
York RTU.Cooling Control.DX Cooling Circuit 2 | High Pressure Lockout | MV | 29644 | HPS2-LO | 1709 | 161 |  | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7010 | 7
York RTU.Cooling Control.DX Cooling Circuit 2 | Low Pressure Limit | MV | 29648 | LPS2 | 1709 | 165 |  | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7011 | 7
York RTU.Cooling Control.DX Cooling Circuit 2 | Low Pressure Lockout | MV | 29652 | LPS2-LO | 1709 | 169 |  | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7012 | 7
York RTU.Cooling Control.DX Cooling Circuit 2 | Freeze Condition | MV | 29656 | FS2 | 1709 | 173 |  | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7013 | 7
York RTU.Cooling Control.DX Cooling Circuit 2 | Freeze Condition Lockout | MV | 29660 | FS2-LO | 1709 | 177 |  | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7014 | 7
York RTU.Cooling Control.DX Cooling Circuit 2 | Evaporator Coil Temp | AV | 29664 | EC2 | 1709 | 181 |  | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7015 | 7
York RTU.Cooling Control.DX Cooling Circuit 2 | Condenser Coil Temp | AV | 29668 | CC2 | 1709 | 185 |  | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7016 | 7
York RTU.Cooling Control.DX Cooling Circuit 3 | Compressor Stage Command | MV | 29613 | C3 | 1709 | 129 |  | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7001 | 9
York RTU.Cooling Control.DX Cooling Circuit 3 | Compressor Stage Status | MV | 29617 | C3-S | 1709 | 133 |  | 0 = Off-Idle 1 = On-Minimum On Time 2 = On-Normal Command 3 = Off-Cooling Is Disabled ... |  | FALSE | 9 |  | SE RTU DX Cooling Circuit 1 Status | 1741 | [5 empty] | SE RTU DX Cooling Circuit 1 Status | 1741 |  |  |  |  | 7002 | 9
York RTU.Cooling Control.DX Cooling Circuit 3 | Compressor Stage Enabled | MV | 29621 | C3-En | 1709 | 137 |  | 0 = Yes 1 = No |  | TRUE | 9 |  | Yes/No | 1698 | [5 empty] | Yes/No | 1698 |  |  |  |  | 7003 | 9
York RTU.Cooling Control.DX Cooling Circuit 3 | Compressor Stage Accumulated Runtime | AV | 29629 | C3RunTim | 1709 | 142 |  | 0 ... 10000 hours |  | TRUE | 4 | 1s | hours | 507:71 | 0 | 10000 |  |  | 1s | hours | 507:71 | 0 | 10000 |  |  | 7005 | 9
York RTU.Cooling Control.DX Cooling Circuit 3 | Min On Time Remaining | AV | 29633 | C3OnTmr | 1709 | 150 |  | seconds |  | FALSE | 17 | 1s | seconds | 507:73 |  |  |  |  | 1s | seconds | 507:73 |  |  |  |  | 7007 | 9
York RTU.Cooling Control.DX Cooling Circuit 3 | Anti-Short Cycle Delay Time Remaining | AV | 29637 | C3ASCDTmr | 1709 | 154 |  | seconds |  | FALSE | 17 | 1s | seconds | 507:73 |  |  |  |  | 1s | seconds | 507:73 |  |  |  |  | 7008 | 9
York RTU.Cooling Control.DX Cooling Circuit 3 | High Pressure Limit | MV | 29641 | HPS3 | 1709 | 158 |  | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7009 | 9
York RTU.Cooling Control.DX Cooling Circuit 3 | High Pressure Lockout | MV | 29645 | HPS3-LO | 1709 | 162 |  | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7010 | 9
York RTU.Cooling Control.DX Cooling Circuit 3 | Low Pressure Limit | MV | 29649 | LPS3 | 1709 | 166 |  | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7011 | 9
York RTU.Cooling Control.DX Cooling Circuit 3 | Low Pressure Lockout | MV | 29653 | LPS3-LO | 1709 | 170 |  | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7012 | 9
York RTU.Cooling Control.DX Cooling Circuit 3 | Freeze Condition | MV | 29657 | FS3 | 1709 | 174 |  | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7013 | 9
York RTU.Cooling Control.DX Cooling Circuit 3 | Freeze Condition Lockout | MV | 29661 | FS3-LO | 1709 | 178 |  | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7014 | 9
York RTU.Cooling Control.DX Cooling Circuit 3 | Evaporator Coil Temp | AV | 29665 | EC3 | 1709 | 182 |  | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7015 | 9
York RTU.Cooling Control.DX Cooling Circuit 3 | Condenser Coil Temp | AV | 29669 | CC3 | 1709 | 186 |  | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7016 | 9
York RTU.Cooling Control.DX Cooling Circuit 4 | Compressor Stage Command | MV | 29614 | C4 | 1709 | 130 |  | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7001 | 11
York RTU.Cooling Control.DX Cooling Circuit 4 | Compressor Stage Status | MV | 29618 | C4-S | 1709 | 134 |  | 0 = Off-Idle 1 = On-Minimum On Time 2 = On-Normal Command 3 = Off-Cooling Is Disabled ... |  | FALSE | 9 |  | SE RTU DX Cooling Circuit 1 Status | 1741 | [5 empty] | SE RTU DX Cooling Circuit 1 Status | 1741 |  |  |  |  | 7002 | 11
York RTU.Cooling Control.DX Cooling Circuit 4 | Compressor Stage Enabled | MV | 29622 | C4-En | 1709 | 138 |  | 0 = Yes 1 = No |  | TRUE | 9 |  | Yes/No | 1698 | [5 empty] | Yes/No | 1698 |  |  |  |  | 7003 | 11
York RTU.Cooling Control.DX Cooling Circuit 4 | Compressor Stage Accumulated Runtime | AV | 29630 | C4RunTim | 1709 | 143 |  | 0 ... 10000 hours |  | TRUE | 4 | 1s | hours | 507:71 | 0 | 10000 |  |  | 1s | hours | 507:71 | 0 | 10000 |  |  | 7005 | 11
York RTU.Cooling Control.DX Cooling Circuit 4 | Min On Time Remaining | AV | 29634 | C4OnTmr | 1709 | 151 |  | seconds |  | FALSE | 17 | 1s | seconds | 507:73 |  |  |  |  | 1s | seconds | 507:73 |  |  |  |  | 7007 | 11
York RTU.Cooling Control.DX Cooling Circuit 4 | Anti-Short Cycle Delay Time Remaining | AV | 29638 | C4ASCDTmr | 1709 | 155 |  | seconds |  | FALSE | 17 | 1s | seconds | 507:73 |  |  |  |  | 1s | seconds | 507:73 |  |  |  |  | 7008 | 11
York RTU.Cooling Control.DX Cooling Circuit 4 | High Pressure Limit | MV | 29642 | HPS4 | 1709 | 159 |  | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7009 | 11
York RTU.Cooling Control.DX Cooling Circuit 4 | High Pressure Lockout | MV | 29646 | HPS4-LO | 1709 | 163 |  | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7010 | 11
York RTU.Cooling Control.DX Cooling Circuit 4 | Low Pressure Limit | MV | 29650 | LPS4 | 1709 | 167 |  | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7011 | 11
York RTU.Cooling Control.DX Cooling Circuit 4 | Low Pressure Lockout | MV | 29654 | LPS4-LO | 1709 | 171 |  | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7012 | 11
York RTU.Cooling Control.DX Cooling Circuit 4 | Freeze Condition | MV | 29658 | FS4 | 1709 | 175 |  | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7013 | 11
York RTU.Cooling Control.DX Cooling Circuit 4 | Freeze Condition Lockout | MV | 29662 | FS4-LO | 1709 | 179 |  | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7014 | 11
York RTU.Cooling Control.DX Cooling Circuit 4 | Evaporator Coil Temp | AV | 29666 | EC4 | 1709 | 183 |  | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7015 | 11
York RTU.Cooling Control.DX Cooling Circuit 4 | Condenser Coil Temp | AV | 29670 | CC4 | 1709 | 187 |  | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7016 | 11
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Suction Pressure | AV | 29671 | SLP-1 | 1709 | 188 |  | psi (kPa) |  | FALSE | 4 | 10ths | psi | 507:56 |  |  |  |  | 1s | kPa | 507:54 |  |  |  |  | 7001 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Liquid Pressure | AV | 29675 | LLP-1 | 1709 | 192 |  | psi (kPa) |  | FALSE | 4 | 10ths | psi | 507:56 |  |  |  |  | 1s | kPa | 507:54 |  |  |  |  | 7002 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Suction Temperature | AV | 29679 | SLT-1 | 1709 | 196 |  | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7003 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Liquid Temperature | AV | 29683 | LLT-1 | 1709 | 200 |  | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7004 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Superheat | AV | 29687 | C1-SuperHeat | 1709 | 204 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7005 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Subcooling | AV | 29691 | C1-SubCool | 1709 | 208 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7006 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Condensing Temperature over Ambient | AV | 29695 | C1-CondTempOvrAmb | 1709 | 212 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7007 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Efficiency Index | AV | 29699 | C1-EI | 1709 | 216 |  | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7008 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Capacity Index | AV | 29703 | C1-CI | 1709 | 220 |  | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7009 | 6
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Suction Pressure | AV | 29672 | SLP-2 | 1709 | 189 |  | psi (kPa) |  | FALSE | 4 | 10ths | psi | 507:56 |  |  |  |  | 1s | kPa | 507:54 |  |  |  |  | 7001 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Liquid Pressure | AV | 29676 | LLP-2 | 1709 | 193 |  | psi (kPa) |  | FALSE | 4 | 10ths | psi | 507:56 |  |  |  |  | 1s | kPa | 507:54 |  |  |  |  | 7002 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Suction Temperature | AV | 29680 | SLT-2 | 1709 | 197 |  | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7003 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Liquid Temperature | AV | 29684 | LLT-2 | 1709 | 201 |  | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7004 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Superheat | AV | 29688 | C2-SuperHeat | 1709 | 205 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7005 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Subcooling | AV | 29692 | C2-SubCool | 1709 | 209 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7006 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Condensing Temperature over Ambient | AV | 29696 | C2-CondTempOvrAmb | 1709 | 213 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7007 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Efficiency Index | AV | 29700 | C2-EI | 1709 | 217 |  | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7008 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Capacity Index | AV | 29704 | C2-CI | 1709 | 221 |  | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7009 | 8
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Suction Pressure | AV | 29673 | SLP-3 | 1709 | 190 |  | psi (kPa) |  | FALSE | 4 | 10ths | psi | 507:56 |  |  |  |  | 1s | kPa | 507:54 |  |  |  |  | 7001 | 10
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Liquid Pressure | AV | 29677 | LLP-3 | 1709 | 194 |  | psi (kPa) |  | FALSE | 4 | 10ths | psi | 507:56 |  |  |  |  | 1s | kPa | 507:54 |  |  |  |  | 7002 | 10
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Suction Temperature | AV | 29681 | SLT-3 | 1709 | 198 |  | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7003 | 10
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Liquid Temperature | AV | 29685 | LLT-3 | 1709 | 202 |  | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7004 | 10
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Superheat | AV | 29689 | C3-SuperHeat | 1709 | 206 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7005 | 10
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Subcooling | AV | 29693 | C3-SubCool | 1709 | 210 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7006 | 10
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Condensing Temperature over Ambient | AV | 29697 | C3-CondTempOvrAmb | 1709 | 214 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7007 | 10
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Efficiency Index | AV | 29701 | C3-EI | 1709 | 218 |  | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7008 | 10
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Capacity Index | AV | 29705 | C3-CI | 1709 | 222 |  | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7009 | 10
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Suction Pressure | AV | 29674 | SLP-4 | 1709 | 191 |  | psi (kPa) |  | FALSE | 4 | 10ths | psi | 507:56 |  |  |  |  | 1s | kPa | 507:54 |  |  |  |  | 7001 | 12
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Liquid Pressure | AV | 29678 | LLP-4 | 1709 | 195 |  | psi (kPa) |  | FALSE | 4 | 10ths | psi | 507:56 |  |  |  |  | 1s | kPa | 507:54 |  |  |  |  | 7002 | 12
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Suction Temperature | AV | 29682 | SLT-4 | 1709 | 199 |  | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7003 | 12
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Liquid Temperature | AV | 29686 | LLT-4 | 1709 | 203 |  | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7004 | 12
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Superheat | AV | 29690 | C4-SuperHeat | 1709 | 207 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7005 | 12
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Subcooling | AV | 29694 | C4-SubCool | 1709 | 211 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7006 | 12
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Condensing Temperature over Ambient | AV | 29698 | C4-CondTempOvrAmb | 1709 | 215 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7007 | 12
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Efficiency Index | AV | 29702 | C4-EI | 1709 | 219 |  | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7008 | 12
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Capacity Index | AV | 29706 | C4-CI | 1709 | 223 |  | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7009 | 12
York RTU.Heating Control | Heating Mode Enabled For Operation | MV | 29707 | Htg-En | 1709 | 224 |  | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7000 | 13
York RTU.Heating Control | Heating Status | MV | 29708 | Htg-S | 1709 | 225 |  | 0 = Off-Idle 1 = On-Defrost 2 = SAT Tempering 3 = Morning Warmup ... |  | FALSE | 9 |  | SE RTU Heating Control Status | 1742 | [5 empty] | SE RTU Heating Control Status | 1742 |  |  |  |  | 7001 | 13
York RTU.Heating Control | SAT Air Temp Limit for Heating Enabled | MV | 29709 | SATHtgLimit-En | 1709 | 226 |  | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7002 | 13
York RTU.Heating Control | SAT Air Temp Limit For Heating Setpoint | AV | 29710 | SATHtgLimit-Sp | 1709 | 227 |  | 100 ... 180 deg F (38 ... 82 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 100 | 180 |  |  | 1s | deg C | 507:62 | 38 | 82 |  |  | 7003 | 13
York RTU.Heating Control | Outdoor Air Temp Heating Cutout Setpoint | AV | 29711 | HtgOATCutout-Sp | 1709 | 228 |  | 0 ... 100 deg F (-18 ... 38 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 0 | 100 |  |  | 1s | deg C | 507:62 | -18 | 38 |  |  | 7004 | 13
York RTU.Heating Control | Hot Water Freeze Stat | MV | 29712 | FSHW | 1709 | 229 |  | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7005 | 13
York RTU.Heating Control | Gas Valve1 Input | MV | 29713 | MV | 1709 | 230 |  | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7006 | 13
York RTU.Heating Control | Gas Valve2 Input | MV | 29714 | GV2 | 1709 | 231 |  | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7007 | 13
York RTU.Heating Control | Gas Valve3 Input | MV | 29715 | GV3 | 1709 | 232 |  | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7008 | 13
York RTU.Heating Control | Heat Limit1 Switch | MV | 29716 | Limit | 1709 | 233 |  | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7009 | 13
York RTU.Heating Control | Heat Limit1 Switch Lockout | MV | 29717 | LimitLO | 1709 | 234 |  | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7010 | 13
York RTU.Heating Control | Heat Limit2 Switch | MV | 29718 | Lim2 | 1709 | 235 |  | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7011 | 13
York RTU.Heating Control | Heat Limit2 Switch Lockout | MV | 29719 | Lim2LO | 1709 | 236 |  | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7012 | 13
York RTU.Heating Control | Heat Limit3 Switch | MV | 29720 | Lim3 | 1709 | 237 |  | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7013 | 13
York RTU.Heating Control | Heat Limit3 Switch Lockout | MV | 29721 | Lim3LO | 1709 | 238 |  | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7014 | 13
York RTU.Heating Control | VAV Occupied Heating Enabled | MV | 29722 | HtgOcc-En | 1709 | 239 |  | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7015 | 13
York RTU.Heating Control | VAV Occupied Heating Setpoint | AV | 29723 | VAVHtgOcc-SP | 1709 | 240 |  | 40 ... 85 deg F (4 ... 30 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 40 | 85 |  |  | 1s | deg C | 507:62 | 4 | 30 |  |  | 7016 | 13
York RTU.Heating Control | Unoccupied Heating Enabled | MV | 29724 | HtgUnocc-En | 1709 | 241 |  | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7017 | 13
York RTU.Heating Control | VAV Unoccupied Heating Setpoint | AV | 29725 | VAVHtgUnocc-Sp | 1709 | 242 |  | 45 ... 98 deg F (7 ... 36 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 45 | 98 |  |  | 1s | deg C | 507:62 | 7 | 36 |  |  | 7018 | 13
York RTU.Heating Control | VAV Operating Heating Setpoint | AV | 29726 | VAVOprHtg-Sp | 1709 | 243 |  | deg F (deg C) |  | FALSE | 4 | 100ths | deg F | 507:64 |  |  |  |  | 100ths | deg C | 507:62 |  |  |  |  | 7019 | 13
York RTU.Heating Control | VAV Box Heat Command | MV | 29727 | VAV Box | 1709 | 246 |  | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7022 | 13
York RTU.Heating Control | CV Occupied Heating Setpoint | AV | 29728 | CVHtgOcc-SP | 1709 | 461 |  | 46 ... 99 deg F (8 ... 37 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 46 | 99 |  |  | 1s | deg C | 507:62 | 8 | 37 |  |  | 7023 | 13
York RTU.Heating Control | CV Unoccupied Heating Setpoint | AV | 29729 | CVHtgUnocc-Sp | 1709 | 462 |  | 45 ... 98 deg F (7 ... 36 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 45 | 98 |  |  | 1s | deg C | 507:62 | 7 | 36 |  |  | 7024 | 13
York RTU.Heating Control | CV Operating Heating Setpoint | AV | 29730 | CVOprHtg-Sp | 1709 | 463 |  | deg F (deg C) |  | FALSE | 4 | 100ths | deg F | 507:64 |  |  |  |  | 100ths | deg C | 507:62 |  |  |  |  | 7025 | 13
York RTU.Heating Control.Staged Heat Control | Number of Heating Stages Installed | AV | 29731 | #HtgStgs | 1709 | 250 |  | 0 ... 3 |  | TRUE | 16 | 1s |  | 507:95 | 0 | 3 |  |  | 1s |  | 507:95 | 0 | 3 |  |  | 7000 | 14
York RTU.Heating Control.Staged Heat Control.Heating Stage 1 | Heat Stage Command | MV | 29732 | H1 | 1709 | 251 |  | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7000 | 15
York RTU.Heating Control.Staged Heat Control.Heating Stage 1 | Heat Stage Status | MV | 29735 | H1-S | 1709 | 254 |  | 0 = Off-Idle 1 = On-Minimum Runtime Timer 2 = On-Normal Command 3 = Off-Heating Is Disabled ... |  | FALSE | 9 |  | SE RTU Heating Stage 1 Status | 1743 | [5 empty] | SE RTU Heating Stage 1 Status | 1743 |  |  |  |  | 7001 | 15
York RTU.Heating Control.Staged Heat Control.Heating Stage 1 | Heat Stage Accumulated Runtime | AV | 29738 | H1RunTim | 1709 | 269 |  | 0 ... 10000 hours |  | TRUE | 4 | 1s | hours | 507:71 | 0 | 10000 |  |  | 1s | hours | 507:71 | 0 | 10000 |  |  | 7006 | 15
York RTU.Heating Control.Staged Heat Control.Heating Stage 2 | Heat Stage Command | MV | 29733 | H2 | 1709 | 252 |  | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7000 | 16
York RTU.Heating Control.Staged Heat Control.Heating Stage 2 | Heat Stage Status | MV | 29736 | H2-S | 1709 | 255 |  | 0 = Off-Idle 1 = On-Minimum Runtime Timer 2 = On-Normal Command 3 = Off-Heating Is Disabled ... |  | FALSE | 9 |  | SE RTU Heating Stage 1 Status | 1743 | [5 empty] | SE RTU Heating Stage 1 Status | 1743 |  |  |  |  | 7001 | 16
York RTU.Heating Control.Staged Heat Control.Heating Stage 2 | Heat Stage Accumulated Runtime | AV | 29739 | H2RunTim | 1709 | 270 |  | 0 ... 10000 hours |  | TRUE | 4 | 1s | hours | 507:71 | 0 | 10000 |  |  | 1s | hours | 507:71 | 0 | 10000 |  |  | 7006 | 16
York RTU.Heating Control.Staged Heat Control.Heating Stage 3 | Heat Stage Command | MV | 29734 | H3 | 1709 | 253 |  | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7000 | 17
York RTU.Heating Control.Staged Heat Control.Heating Stage 3 | Heat Stage Status | MV | 29737 | H3-S | 1709 | 256 |  | 0 = Off-Idle 1 = On-Minimum Runtime Timer 2 = On-Normal Command 3 = Off-Heating Is Disabled ... |  | FALSE | 9 |  | SE RTU Heating Stage 1 Status | 1743 | [5 empty] | SE RTU Heating Stage 1 Status | 1743 |  |  |  |  | 7001 | 17
York RTU.Heating Control.Staged Heat Control.Heating Stage 3 | Heat Stage Accumulated Runtime | AV | 29740 | H3RunTim | 1709 | 271 |  | 0 ... 10000 hours |  | TRUE | 4 | 1s | hours | 507:71 | 0 | 10000 |  |  | 1s | hours | 507:71 | 0 | 10000 |  |  | 7006 | 17
York RTU.Heating Control.Hydronic Heat Control | Hydronic Heat Valve % Command | AV | 29741 | HWV | 1709 | 275 |  | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7000 | 18
York RTU.Heating Control.Hydronic Heat Control | Hydronic Heat Valve Reverse Acting | MV | 29742 | HydReverse | 1709 | 276 |  | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7001 | 18
York RTU.Heating Control.Hydronic Heat Control | Hydronic Heating Stage #1 Supply Air Setpoint | AV | 29743 | HydH1SA-Sp | 1709 | 277 |  | 80 ... 180 deg F (27 ... 82 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 80 | 180 |  |  | 1s | deg C | 507:62 | 27 | 82 |  |  | 7002 | 18
York RTU.Heating Control.Hydronic Heat Control | Hydronic Heating Stage #2 Supply Air Setpoint | AV | 29744 | HydH2SA-Sp | 1709 | 278 |  | 80 ... 180 deg F (27 ... 82 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 80 | 180 |  |  | 1s | deg C | 507:62 | 27 | 82 |  |  | 7003 | 18
York RTU.Heating Control.Hydronic Heat Control | Hydronic Heat SAT Tempering Enabled | MV | 29745 | SATTempHydHt-En | 1709 | 279 |  | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7004 | 18
York RTU.Heating Control.Hydronic Heat Control | Hydronic Heat SAT Tempering Setpoint | AV | 29746 | SATTempHydHt-Sp | 1709 | 280 |  | 40 ... 60 deg F (4 ... 15 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 40 | 60 |  |  | 1s | deg C | 507:62 | 4 | 15 |  |  | 7005 | 18
York RTU.Economizer | Economizer Enabled For Operation | MV | 29747 | Econ-En | 1709 | 281 |  | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7000 | 19
York RTU.Economizer | Economizer Damper % Command | AV | 29748 | Economizer | 1675 | 1024 |  | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7001 | 19
York RTU.Economizer | Econ Free Cooling Available | MV | 29749 | Econ-Free | 1709 | 283 |  | 0 = No 1 = Yes |  | FALSE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7002 | 19
York RTU.Economizer | Economizer Status | MV | 29750 | Econ-S | 1709 | 284 |  | 0 = Disabled 1 = Damper Not Functional 2 = Purge 3 = Unavailable-Sensor Fault ... |  | FALSE | 9 |  | SE RTU Economizer Status | 1738 | [5 empty] | SE RTU Economizer Status | 1738 |  |  |  |  | 7003 | 19
York RTU.Economizer | Free Cooling Current Mode | MV | 29751 | FreeClg-Mode | 1709 | 285 |  | 0 = Dry Bulb Temperature 1 = Differential Dry Bulb 2 = Single Enthalpy 3 = Dual Enthalpy 4 = Unreliable |  | FALSE | 9 |  | Actual Economizer Type Advanced | 3338 | [5 empty] | Actual Economizer Type Advanced | 3338 |  |  |  |  | 7004 | 19
York RTU.Economizer | Free Cooling Selection | MV | 29752 | FreeClg-Sel | 1709 | 286 |  | 0 = Dry Bulb Temperature 1 = Single Enthalpy 2 = Dual Enthalpy 3 = Auto 4 = Differential Dry Bulb |  | TRUE | 9 |  | SE RTU Economizer Type | 3398 | [5 empty] | SE RTU Economizer Type | 3398 |  |  |  |  | 7005 | 19
York RTU.Economizer | Economizer Outdoor Air Temp Enable Setpoint | AV | 29753 | EconOAT-SpEn | 1709 | 287 |  | 0 ... 80 deg F (-17.8 ... 27 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 0 | 80 |  |  | 1s | deg C | 507:62 | -17.8 | 27 |  |  | 7006 | 19
York RTU.Economizer | Economizer Outdoor Air Enthalpy Setpoint | AV | 29754 | EconOAEnth-Sp | 1709 | 288 |  | 10 ... 50 Btu/lb dry air (23 ... 116 kJ/kg) |  | TRUE | 4 | 1s | Btu/lb dry air | 507:24 | 10 | 50 |  |  | 1s | kJ/kg | 507:125 | 23 | 116 |  |  | 7007 | 19
York RTU.Economizer | Low Ambient Economizer Setpoint | AV | 29755 | LowAmb-Sp | 1709 | 289 |  | -20 ... 60 deg F (-29 ... 15 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | -20 | 60 |  |  | 1s | deg C | 507:62 | -29 | 15 |  |  | 7008 | 19
York RTU.Economizer | Low Ambient Economizer Minimum Position | AV | 29756 | LowAmb-MinPos | 1709 | 290 |  | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7009 | 19
York RTU.Economizer | Economizer Minimum Position Setpoint | AV | 29759 | Econ-MinPos | 1709 | 381 |  | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7017 | 19
York RTU.Economizer | Mixed Air Temperature | AV | 29760 | MAT | 1709 | 293 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7012 | 19
York RTU.Economizer | Supply Air Humidity | AV | 29762 | SAH | 1709 | 295 |  | %RH |  | FALSE | 4 | 1s | %RH | 507:29 |  |  |  |  | 1s | %RH | 507:29 |  |  |  |  | 7014 | 19
York RTU.Economizer | Return Air Enthalpy | AV | 29763 | RA-Enth | 1709 | 296 |  | Btu/lb (kJ/kg) |  | FALSE | 4 | 1s | Btu/lb | 507:117 |  |  |  |  | 1s | kJ/kg | 507:125 |  |  |  |  | 7015 | 19
York RTU.HVAC Zone | Return Air Temperature | AV | 29764 | RAT | 1709 | 297 |  | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7038 | 25
York RTU.Demand Ventilation Control | Demand Ventilation Mode of Operation | MV | 29765 | DVent-Mode | 1709 | 298 |  | 0 = Disabled 1 = Controlled by IAQ 2 = Diff between IAQ and OAQ |  | TRUE | 9 |  | SE RTU DCV Mode | 1729 | [5 empty] | SE RTU DCV Mode | 1729 |  |  |  |  | 7000 | 23
York RTU.Demand Ventilation Control | Demand Ventilation Maximum Economizer Position | AV | 29766 | DVentMaxEconPos | 1709 | 299 |  | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7001 | 23
York RTU.Demand Ventilation Control | Demand Ventilation Indoor Air Quality Setpoint | AV | 29767 | DVentIAQ-Sp | 1709 | 300 |  | 0 ... 5000 ppm |  | TRUE | 4 | 1s | ppm | 507:96 | 0 | 5000 |  |  | 1s | ppm | 507:96 | 0 | 5000 |  |  | 7002 | 23
York RTU.Demand Ventilation Control | Demand Ventilation Differential Setpoint | AV | 29768 | DVentDiff-Sp | 1709 | 301 |  | 0 ... 5000 ppm |  | TRUE | 4 | 1s | ppm | 507:96 | 0 | 5000 |  |  | 1s | ppm | 507:96 | 0 | 5000 |  |  | 7003 | 23
York RTU.Exhaust Fan Control | Exhaust Fan Command | MV | 29775 | ExFan | 1709 | 309 |  | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7001 | 21
York RTU.Exhaust Fan Control | Exhaust Fan VFD % Command | AV | 29776 | ExFanVFD | 1709 | 310 |  | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7002 | 21
York RTU.Exhaust Fan Control | Exhaust Fan Status | MV | 29777 | ExF-S | 1709 | 311 |  | 0 = Off-Idle 1 = On-Normal Command 2 = Off-Disabled 3 = Off-VFD Fault ... |  | FALSE | 9 |  | SE RTU Exhaust Fan | 1745 | [5 empty] | SE RTU Exhaust Fan | 1745 |  |  |  |  | 7003 | 21
York RTU.Exhaust Fan Control | Exhaust Fan VFD Fault | MV | 29778 | ExFanVFDFlt | 1709 | 312 |  | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7004 | 21
York RTU.Exhaust Fan Control | Exhaust Fan Accumulated Runtime | AV | 29779 | ExF-RunTim | 1709 | 313 |  | hours |  | FALSE | 4 | 1s | hours | 507:71 |  |  |  |  | 1s | hours | 507:71 |  |  |  |  | 7005 | 21
York RTU.Exhaust Fan Control | Building Pressure Setpoint | AV | 29780 | Bldg-Sp | 1709 | 314 |  | -0.25 ... 0.25 in wc (-0.07 ... 0.07 kPa) |  | TRUE | 4 | 1000ths | in wc | 507:58 | -0.25 | 0.25 |  |  | 1000ths | kPa | 507:54 | -0.07 | 0.07 |  |  | 7006 | 21
York RTU.Exhaust Fan Control | Building Static Pressure | AV | 29781 | BldgPres | 1709 | 315 |  | in wc (kPa) |  | FALSE | 4 | 1000ths | in wc | 507:58 |  |  |  |  | 1000ths | kPa | 507:54 |  |  |  |  | 7007 | 21
York RTU.Exhaust Fan Control | Exhaust Damper % Command | AV | 29782 | EAD-O | 1709 | 316 |  | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7008 | 21
York RTU.Exhaust Fan Control | Exhaust Damper Position for Exhaust Fan to Turn On | AV | 29783 | ExDmpPosFanOn | 1709 | 317 |  | 20 ... 99 % |  | TRUE | 4 | 1s | % | 507:98 | 20 | 99 |  |  | 1s | % | 507:98 | 20 | 99 |  |  | 7009 | 21
York RTU.Exhaust Fan Control | Exhaust Damper Position for Exhaust Fan to Turn Off | AV | 29784 | ExDmpPosFanOff | 1709 | 318 |  | 10 ... 89 % |  | TRUE | 4 | 1s | % | 507:98 | 10 | 89 |  |  | 1s | % | 507:98 | 10 | 89 |  |  | 7010 | 21
York RTU.Exhaust Fan Control | Economizer Damper Position for Exhaust Fan to Turn On | AV | 29785 | EconDmpPosFanOn | 1709 | 319 |  | 20 ... 99 % |  | TRUE | 4 | 1s | % | 507:98 | 20 | 99 |  |  | 1s | % | 507:98 | 20 | 99 |  |  | 7011 | 21
York RTU.Exhaust Fan Control | Economizer Damper Position for Exhaust Fan to Turn Off | AV | 29786 | EconDmpPosFanOff | 1709 | 320 |  | 10 ... 89 % |  | TRUE | 4 | 1s | % | 507:98 | 10 | 89 |  |  | 1s | % | 507:98 | 10 | 89 |  |  | 7012 | 21
York RTU.Exhaust Fan Control | ERV Enabled | MV | 29787 | ERV-En | 1709 | 321 |  | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7013 | 21
York RTU.Exhaust Fan Control | ERV Unoccupied Fan Enabled | MV | 29788 | ERVUnoccFan-En | 1709 | 322 |  | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7014 | 21
York RTU.Hot Gas Reheat | Hot Gas Reheat Enabled For Operation | MV | 29789 | HGR-En | 1709 | 323 |  | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7000 | 20
York RTU.Hot Gas Reheat | Hot Gas Reheat Command | MV | 29790 | HGR | 1709 | 324 |  | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7001 | 20
York RTU.Hot Gas Reheat | Hot Gas Reheat Status | MV | 29791 | HGR-S | 1709 | 325 |  | 0 = Off-Idle 1 = On-Normal Command 2 = On-Alternate Operation Command 3 = Off-Disabled |  | FALSE | 9 |  | SE RTU Hot Gas Reheat | 1744 | [5 empty] | SE RTU Hot Gas Reheat | 1744 |  |  |  |  | 7002 | 20
York RTU.Hot Gas Reheat | Hot Gas Reheat Humidity Setpoint | AV | 29792 | HGRHum-Sp | 1709 | 326 |  | 0 ... 100 %RH |  | TRUE | 4 | 1s | %RH | 507:29 | 0 | 100 |  |  | 1s | %RH | 507:29 | 0 | 100 |  |  | 7003 | 20
York RTU.Hot Gas Reheat | Hot Gas Reheat Alternate Operation Enabled | MV | 29793 | HGRAlt-En | 1709 | 327 |  | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7004 | 20
York RTU.Hot Gas Reheat | Hot Gas Reheat Alternate Operation Writeable | MV | 29794 | HGRAltWrite | 1709 | 328 |  | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7005 | 20
York RTU.Air Monitor Station | Fresh Air Intake Setpoint | AV | 29795 | MOAFlow-Sp | 1709 | 329 |  | 0 ... 50000 cfm (0 ... 25000 L/s) |  | TRUE | 4 | 10s | cfm | 507:84 | 0 | 50000 |  |  | 10s | L/s | 507:87 | 0 | 25000 |  |  | 7000 | 24
York RTU.Air Monitor Station | Fresh Air Intake Value | AV | 29796 | Fr Air | 1709 | 330 |  | cfm (L/s) |  | FALSE | 4 | 1s | cfm | 507:84 |  |  |  |  | 1s | L/s | 507:87 |  |  |  |  | 7001 | 24
York RTU.Air Monitor Station | Fresh Air Intake Max Sensor Range | AV | 29797 | MOA-Range | 1709 | 331 |  | 0 ... 50000 cfm (0 ... 25000 L/s) |  | TRUE | 4 | 10s | cfm | 507:84 | 0 | 50000 |  |  | 10s | L/s | 507:87 | 0 | 25000 |  |  | 7002 | 24
York RTU.Shutdown Input | Operating Purge Command | MV | 29798 | OprPurgeCmd | 1709 | 332 |  | 0 = False 1 = True |  | FALSE | 9 |  | False/True | 1701 | [5 empty] | False/True | 1701 |  |  |  |  | 7000 | 27
York RTU.Shutdown Input | Purge Command Source | MV | 29799 | PurgeCmdSrc | 1709 | 333 |  | 0 = Unreliable 1 = Local Input 2 = Network Sensor 3 = High Priority ... |  | FALSE | 9 |  | Effective Input Source 2 | 1732 | [5 empty] | Effective Input Source 2 | 1732 |  |  |  |  | 7001 | 27
York RTU.Shutdown Input | Local Purge Command Input | MV | 29800 | Purge | 1709 | 334 |  | 0 = False 1 = True |  | FALSE | 9 |  | False/True | 1701 | [5 empty] | False/True | 1701 |  |  |  |  | 7002 | 27
York RTU.Shutdown Input | Network Override Purge Command | MV | 29801 | NetPurge | 1709 | 335 |  | 0 = False 1 = True |  | TRUE | 9 |  | False/True | 1701 | [5 empty] | False/True | 1701 |  |  |  |  | 7003 | 27
York RTU.Shutdown Input | Shutdown Input/Smoke Detector | MV | 29802 | SD | 1709 | 336 |  | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7004 | 27
York RTU | Unit Status | MV | 29803 | Unit-S | 1709 | 0 |  | 0 = Idle 1 = SD Alarm 2 = Purge Command 3 = Self Test ... |  | FALSE | 9 |  | SE RTU Unit Status | 1737 | [5 empty] | SE RTU Unit Status | 1737 |  |  |  |  | 7000 | 1
York RTU | Unit Name | CSV | 29804 | Name | 1709 | 1 |  |  |  | TRUE | 7 | [14 empty] | 7001 | 1
York RTU | Unit Model Number | CSV | 29805 | Model# | 1709 | 2 |  |  |  | TRUE | 7 | [14 empty] | 7002 | 1
York RTU | Unit Serial Number | CSV | 29806 | Serial# | 1709 | 3 |  |  |  | TRUE | 7 | [14 empty] | 7003 | 1
York RTU | Firmware Version | CSV | 29807 | FirmVer | 1709 | 4 |  |  |  | FALSE | 7 | [14 empty] | 7004 | 1
York RTU.Economizer | Economizer Damper Minimum Position Low Speed Fan | AV | 29808 | LowSpeedFan-MinPos | 1709 | 447 |  | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7025 | 19
York RTU.Economizer | Excess Outdoor Air | MV | 29809 | ExcessOutAirFlt | 1709 | 450 |  | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7018 | 19
York RTU.Economizer | Not Economizing When Should | MV | 29810 | NotEconFlt | 1709 | 451 |  | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7019 | 19
York RTU.Economizer | Damper Not Modulating | MV | 29811 | EconDampFlt | 1709 | 452 |  | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7020 | 19
York RTU.Economizer | Economizing When Should Not | MV | 29812 | EconWhenShouldNotFlt | 1709 | 453 |  | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7021 | 19
York RTU.System Controllers | Econ Controller | MV | 29813 | EconCntlr | 1709 | 437 |  | 0 = Not Present 1 = Offline 2 = Online |  | FALSE | 9 |  | EIO Connection Status | 1662 | [5 empty] | EIO Connection Status | 1662 |  |  |  |  | 7004 | 29
York RTU.System Controllers | 4 Stage Controller | MV | 29814 | 4StgCntlr | 1709 | 438 |  | 0 = Not Present 1 = Offline 2 = Online |  | FALSE | 9 |  | EIO Connection Status | 1662 | [5 empty] | EIO Connection Status | 1662 |  |  |  |  | 7005 | 29
York RTU.System Controllers | FDD Manager Controller | MV | 29815 | FDDMCntlr | 1709 | 439 |  | 0 = Not Present 1 = Offline 2 = Online |  | FALSE | 9 |  | EIO Connection Status | 1662 | [5 empty] | EIO Connection Status | 1662 |  |  |  |  | 7006 | 29
York RTU.System Controllers | FDD Subordinate Controller | MV | 29816 | FDDSCntlr | 1709 | 440 |  | 0 = Not Present 1 = Offline 2 = Online |  | FALSE | 9 |  | EIO Connection Status | 1662 | [5 empty] | EIO Connection Status | 1662 |  |  |  |  | 7007 | 29
York RTU.System Controllers | Device Name | CSV | 29818 | DevName | 1709 | 446 |  |  |  | TRUE | 7 | [14 empty] | 7009 | 29
York RTU.Fan Control | Occupied: Three Stage of Cool % Command | AV | 29819 | 3ClgStg-%Cmd | 1709 | 442 |  | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7027 | 3
York RTU.Fan Control | Occupied: Four Stage of Cool % Command | AV | 29820 | 4ClgStg-%Cmd | 1709 | 443 |  | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7028 | 3
York RTU.Fan Control | Occupied: Three Stage of Heat % Command | AV | 29821 | 3HtgStg-%Cmd | 1709 | 444 |  | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7029 | 3
York RTU.Heating Control | Morning Warmup Enabled | MV | 29822 | MornW-En | 1709 | 244 |  | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7020 | 13
York RTU.Heating Control | Morning Warmup/Return Air Temp Setpoint | AV | 29823 | MornWRAT-Sp | 1709 | 245 |  | 50 ... 85 deg F (10 ... 30 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 50 | 85 |  |  | 1s | deg C | 507:62 | 10 | 30 |  |  | 7021 | 13
York RTU.Economizer | Economizer Damper Position | AV | 29824 | EconDampPos | 1709 | 449 |  | % open |  | FALSE | 4 | 1s | % open | 507:264 |  |  |  |  | 1s | % open | 507:264 |  |  |  |  | 7011 | 19
York RTU.HVAC Zone | Temporary Occupancy Input | MV | 29825 | TempOCC | 1709 | 448 |  | 0 = Disable 1 = Enable |  | TRUE | 9 |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 |  |  |  |  | 7040 | 25
York RTU | Reset Lockouts | MV | 29826 | ResetLO | 1709 | 464 |  | 0 = Off 1 = On |  | TRUE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7011 | 1
York RTU.HVAC Zone | Space Humidity RAH Input | AV | 29828 | RAH | 1709 | 41 |  | %RH |  | FALSE | 4 | 10ths | %RH | 507:29 |  |  |  |  | 10ths | %RH | 507:29 |  |  |  |  | 7019 | 25
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Cooling Circuit Test Status | MV | 29829 | ClgCktTestS-1 | 1709 | 478 |  | 0 = Unknown Status 1 = Basic Data Not Available Manual Entry 2 = Basic Data Not Available 3 = Return Wet Bulb Temp Not Available ... |  | FALSE | 9 |  | SE FDD Codes | 1694 | [5 empty] | SE FDD Codes | 1694 |  |  |  |  | 7000 | 6
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Cooling Circuit Test Status | MV | 29830 | ClgCktTestS-2 | 1709 | 479 |  | 0 = Unknown Status 1 = Basic Data Not Available Manual Entry 2 = Basic Data Not Available 3 = Return Wet Bulb Temp Not Available ... |  | FALSE | 9 |  | SE FDD Codes | 1694 | [5 empty] | SE FDD Codes | 1694 |  |  |  |  | 7000 | 8
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Cooling Circuit Test Status | MV | 29831 | ClgCktTestS-3 | 1709 | 480 |  | 0 = Unknown Status 1 = Basic Data Not Available Manual Entry 2 = Basic Data Not Available 3 = Return Wet Bulb Temp Not Available ... |  | FALSE | 9 |  | SE FDD Codes | 1694 | [5 empty] | SE FDD Codes | 1694 |  |  |  |  | 7000 | 10
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Cooling Circuit Test Status | MV | 29832 | ClgCktTestS-4 | 1709 | 481 |  | 0 = Unknown Status 1 = Basic Data Not Available Manual Entry 2 = Basic Data Not Available 3 = Return Wet Bulb Temp Not Available ... |  | FALSE | 9 |  | SE FDD Codes | 1694 | [5 empty] | SE FDD Codes | 1694 |  |  |  |  | 7000 | 12
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Evaporating Temp Value | AV | 29833 | C1-EvapTempValue | 1709 | 534 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7014 | 6
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Evaporating Temp Value | AV | 29834 | C2-EvapTempValue | 1709 | 535 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7014 | 8
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Evaporating Temp Value | AV | 29835 | C3-EvapTempValue | 1709 | 536 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7014 | 10
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Evaporating Temp Value | AV | 29836 | C4-EvapTempValue | 1709 | 537 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7014 | 12
York RTU.HVAC Zone | Time to Next Occupancy Period | AV | 29837 | TimeToNextOcc | 1709 | 538 |  | minutes |  | FALSE | 4 | 10ths | minutes | 507:72 |  |  |  |  | 10ths | minutes | 507:72 |  |  |  |  | 7046 | 25
York RTU.HVAC Zone | Operating Mode | MV | 29838 | OprMode | 1709 | 539 |  | 0 = Normal 1 = Warmup 2 = Cooldown 3 = Coast |  | FALSE | 9 |  | OST Warmup Cooldown | 366 | [5 empty] | OST Warmup Cooldown | 366 |  |  |  |  | 7047 | 25
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Condenser Temperature Over Ambient High | AV | 29849 | C1-CondTempOAHigh | 1709 | 551 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7015 | 6
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Condenser Temperature Over Ambient High | AV | 29850 | C2-CondTempOAHigh | 1709 | 552 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7015 | 8
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Condenser Temperature Over Ambient High | AV | 29851 | C3-CondTempOAHigh | 1709 | 553 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7015 | 10
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Condenser Temperature Over Ambient High | AV | 29852 | C4-CondTempOAHigh | 1709 | 554 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7015 | 12
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Condenser Temperature Over Ambient Low | AV | 29853 | C1-CondTempOALow | 1709 | 555 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7016 | 6
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Condenser Temperature Over Ambient Low | AV | 29854 | C2-CondTempOALow | 1709 | 556 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7016 | 8
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Condenser Temperature Over Ambient Low | AV | 29855 | C3-CondTempOALow | 1709 | 557 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7016 | 10
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Condenser Temperature Over Ambient Low | AV | 29856 | C4-CondTempOALow | 1709 | 558 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7016 | 12
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Superheat High | AV | 29857 | C1-SuperheatHigh | 1709 | 559 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7017 | 6
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Superheat High | AV | 29858 | C2-SuperheatHigh | 1709 | 560 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7017 | 8
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Superheat High | AV | 29859 | C3-SuperheatHigh | 1709 | 561 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7017 | 10
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Superheat High | AV | 29860 | C4-SuperheatHigh | 1709 | 562 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7017 | 12
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Superheat Low | AV | 29861 | C1-SuperheatLow | 1709 | 563 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7018 | 6
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Superheat Low | AV | 29862 | C2-SuperheatLow | 1709 | 564 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7018 | 8
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Superheat Low | AV | 29863 | C3-SuperheatLow | 1709 | 565 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7018 | 10
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Superheat Low | AV | 29864 | C4-SuperheatLow | 1709 | 566 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7018 | 12
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Subcool High | AV | 29865 | C1-SubcoolHigh | 1709 | 567 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7019 | 6
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Subcool High | AV | 29866 | C2-SubcoolHigh | 1709 | 568 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7019 | 8
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Subcool High | AV | 29867 | C3-SubcoolHigh | 1709 | 569 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7019 | 10
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Subcool High | AV | 29868 | C4-SubcoolHigh | 1709 | 570 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7019 | 12
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Subcool Low | AV | 29869 | C1-SubcoolLow | 1709 | 571 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7020 | 6
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Subcool Low | AV | 29870 | C2-SubcoolLow | 1709 | 572 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7020 | 8
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Subcool Low | AV | 29871 | C3-SubcoolLow | 1709 | 573 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7020 | 10
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Subcool Low | AV | 29872 | C4-SubcoolLow | 1709 | 574 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7020 | 12
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Evaporating Temperature High | AV | 29873 | C1-EvapTempHigh | 1709 | 575 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7021 | 6
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Evaporating Temperature High | AV | 29874 | C2-EvapTempHigh | 1709 | 576 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7021 | 8
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Evaporating Temperature High | AV | 29875 | C3-EvapTempHigh | 1709 | 577 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7021 | 10
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Evaporating Temperature High | AV | 29876 | C4-EvapTempHigh | 1709 | 578 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7021 | 12
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Evaporating Temperature Low | AV | 29877 | C1-EvapTempLow | 1709 | 579 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7022 | 6
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Evaporating Temperature Low | AV | 29878 | C2-EvapTempLow | 1709 | 580 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7022 | 8
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Evaporating Temperature Low | AV | 29879 | C3-EvapTempLow | 1709 | 581 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7022 | 10
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Evaporating Temperature Low | AV | 29880 | C4-EvapTempLow | 1709 | 582 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7022 | 12
York RTU.Heating Control | Heating Adaptive Tuning Enable | MV | 29881 | HtgAdapTunEn | 1709 | 616 |  | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7041 | 13
York RTU.Cooling Control | Cooling Adaptive Tuning Enable | MV | 29882 | ClgAdapTunEn | 1709 | 617 |  | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7043 | 4
York RTU.HVAC Zone | Load Shed Active | MV | 29883 | LoadShedEnable | 1709 | 528 |  | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7043 | 25
York RTU.HVAC Zone | Load Shed Rate Limit | AV | 29884 | LoadShedRateLim | 1709 | 529 |  | 0 ... 1 deg F/min (0 ... 1 deg C/min) |  | TRUE | 4 | 1000ths | deg F/min | 507:94 | 0 | 1 |  |  | 1000ths | deg C/min | 507:92 | 0 | 1 |  |  | 7044 | 25
York RTU.HVAC Zone | Load Shed Adjust | AV | 29885 | LoadShedAdjust | 1709 | 530 |  | 0 ... 8 delta deg F (0 ... 4.4 delta deg C) |  | TRUE | 4 | 10ths | delta deg F | 507:120 | 0 | 8 |  |  | 10ths | delta deg C | 507:359 | 0 | 4.4 |  |  | 7045 | 25
York RTU.Cooling Control | Unit Capacity | AV | 29886 | UnitCap | 1709 | 482 |  | 0 ... 130 tons refr (0 ... 460 kW) |  | TRUE | 4 | 10ths | tons refr | 507:52 | 0 | 130 |  |  | 10ths | kW | 507:48 | 0 | 460 |  |  | 7038 | 4
York RTU.Cooling Control | Fan Power | AV | 29887 | FanPower | 1709 | 483 |  | 0 ... 19 kW |  | TRUE | 4 | 10ths | kW | 507:48 | 0 | 19 |  |  | 10ths | kW | 507:48 | 0 | 19 |  |  | 7039 | 4
York RTU.Cooling Control | Super Heat Goal | AV | 29888 | SuperHeatGoal | 1709 | 484 |  | 10 ... 30 deg F (-12.2 ... -1.1 deg C) |  | TRUE | 4 | 10ths | deg F | 507:64 | 10 | 30 |  |  | 10ths | deg C | 507:62 | -12.2 | -1.1 |  |  | 7040 | 4
York RTU.Cooling Control | Altitude | AV | 29889 | Altitude | 1709 | 485 |  | -1500 ... 30000 ft (-457.2 ... 9144 m) |  | TRUE | 4 | 10ths | ft | 507:33 | -1500 | 30000 |  |  | 10ths | m | 507:31 | -457.2 | 9144 |  |  | 7041 | 4
York RTU.Cooling Control | Number of Refrig Systems Installed | AV | 29890 | #RefrigSys | 1709 | 627 |  | 0 ... 4 |  | TRUE | 4 | 1s |  | 507:95 | 0 | 4 |  |  | 1s |  | 507:95 | 0 | 4 |  |  | 7044 | 4
York RTU.Heating Control | Morning Cooldown Enabled | MV | 29891 | MornC-En | 1709 | 486 |  | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7034 | 13
York RTU.Heating Control | Morning Cooldown/Return Air Temp Setpoint | AV | 29892 | MornCRAT-Sp | 1709 | 487 |  | 50 ... 85 deg F (10 ... 30 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 50 | 85 |  |  | 1s | deg C | 507:62 | 10 | 30 |  |  | 7035 | 13
York RTU.Heating Control | Optimal Start Enabled | MV | 29893 | OptStrt-En | 1709 | 488 |  | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7036 | 13
York RTU.Heating Control | Occupancy BI Enabled | MV | 29894 | OccBI-En | 1709 | 489 |  | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7037 | 13
York RTU.Heating Control | Early Start Period | AV | 29895 | EarlyStrtPeriod | 1709 | 490 |  | 0 ... 120 minutes |  | TRUE | 4 | 1s | minutes | 507:72 | 0 | 120 |  |  | 1s | minutes | 507:72 | 0 | 120 |  |  | 7038 | 13
York RTU.Heat Pump Control | Number of Heat Pump Stages Installed | AV | 29898 | #HtPumpStgs | 1709 | 491 |  | 0 ... 2 |  | TRUE | 4 | 1s |  | 507:95 | 0 | 2 |  |  | 1s |  | 507:95 | 0 | 2 |  |  | 7000 | 38
York RTU.Heat Pump Control | Defrost Curve Selection | MV | 29899 | DefrostCurveSel | 1709 | 495 |  | 0 = Curve 1 1 = Curve 2 2 = Curve 3 3 = Curve 4 ... |  | TRUE | 9 |  | SE RTU Defrost Curves | 1665 | [5 empty] | SE RTU Defrost Curves | 1665 |  |  |  |  | 7004 | 38
York RTU.Heat Pump Control | Defrost State | MV | 29920 | DefrostState | 1709 | 496 |  | 0 = Defrost Off 1 = Normal Defrost 2 = Test Defrost 3 = Comp Delay Exit Defrost ... |  | FALSE | 9 |  | Defrost State | 1645 | [5 empty] | Defrost State | 1645 |  |  |  |  | 7005 | 38
York RTU.Heat Pump Control | Reversing Valve | MV | 29900 | RevVlv | 1709 | 613 |  | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7011 | 38
York RTU.Heat Pump Control | Auxiliary Heat | MV | 29901 | AuxHtg | 1709 | 614 |  | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7012 | 38
York RTU.Heat Pump Control | Mode | MV | 29902 | Mode | 1709 | 615 |  | 0 = Heating 1 = Cooling |  | FALSE | 9 |  | Heating/Cooling | 350 | [5 empty] | Heating/Cooling | 350 |  |  |  |  | 7013 | 38
York RTU.Hot Gas Reheat | HGR Unoccupied Humidity Setpoint | AV | 29903 | HGRUnoccHum-SP | 1709 | 642 |  | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7006 | 20
York RTU.Hot Gas Reheat | HGR Enabled for Unoccupied Operation | MV | 29904 | HGRUnocc-En | 1709 | 643 |  | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7007 | 20
York RTU.Heating Control | DAT Max Heating SP | AV | 29905 | DATMaxHtgSP | 1709 | 624 |  | 80 ... 110 deg F (26.6 ... 43.4 deg C) |  | TRUE | 4 | 10ths | deg F | 507:64 | 80 | 110 |  |  | 10ths | deg C | 507:62 | 26.6 | 43.4 |  |  | 7043 | 13
York RTU.Heating Control | DAT Satisfied SP | AV | 29906 | DATSatSP | 1709 | 625 |  | 65 ... 75 deg F (18.3 ... 23.9 deg C) |  | TRUE | 4 | 10ths | deg F | 507:64 | 65 | 75 |  |  | 10ths | deg C | 507:62 | 18.3 | 23.9 |  |  | 7044 | 13
York RTU.Cooling Control | DAT Cooling Min SP | AV | 29907 | DATClgMinSP | 1709 | 626 |  | 50 ... 60 deg F (9.5 ... 15.6 deg C) |  | TRUE | 4 | 10ths | deg F | 507:64 | 50 | 60 |  |  | 10ths | deg C | 507:62 | 9.5 | 15.6 |  |  | 7045 | 4
York RTU | SZ VAV Enabled | MV | 29908 | SZVAVEn | 1709 | 623 |  | 0 = Off 1 = On |  | TRUE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7020 | 1
York RTU | Hardware Reset | MV | 29909 | HdwrReset | 1709 | 631 |  | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7021 | 1
York RTU.HVAC Zone | Direct Loadshed | MV | 29910 | DirLoadshd | 1709 | 629 |  | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7061 | 25
York RTU.HVAC Zone | Redline | MV | 29911 | Redline | 1709 | 632 |  | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7062 | 25
York RTU.Economizer | EconMech Setup | MV | 29912 | EconMechStp | 1709 | 630 |  | 0 = Option A 1 = Option B |  | TRUE | 9 |  | SE RTU EconMech Setup | 1752 | [5 empty] | SE RTU EconMech Setup | 1752 |  |  |  |  | 7027 | 19
York RTU.Fan Control | SZ VAV Minimum Fan Speed | AV | 29913 | SZVAVMinFanSpd | 1709 | 647 |  | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7037 | 3
York RTU.HVAC Zone | Off During Unoccupied | MV | 29914 | OffDurUnocc | 1709 | 633 |  | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7059 | 25
York RTU.Economizer | Economizer Fault Detection Enable | MV | 29915 | EconFltDetectEn | 1709 | 646 |  | 0 = Disable 1 = Enable |  | TRUE | 9 |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 |  |  |  |  | 7028 | 19
York RTU.Economizer | FDD Economizer Alarm Delay | AV | 29916 | EconAlrmDly | 1709 | 653 |  | 0 ... 3600 seconds |  | TRUE | 4 | 10s | seconds | 507:73 | 0 | 3600 |  |  | 10s | seconds | 507:73 | 0 | 3600 |  |  | 7029 | 19
York RTU.Economizer | FDD Economizer Damper Allowed Error | AV | 29917 | EconPosErr | 1709 | 654 |  | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7030 | 19
York RTU.Economizer | FDD Damper Min Position Tolerance | AV | 29918 | EconMinErr | 1709 | 655 |  | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7031 | 19
York RTU.HVAC Zone | PID Tuning Reset | MV | 29919 | PIDTunRst | 1709 | 651 |  | 0 = False 1 = True |  | TRUE | 9 |  | False/True | 1701 | [5 empty] | False/True | 1701 |  |  |  |  | 7063 | 25
York RTU.Cooling Control | Pump Out Enable | MV | 29921 | PmpOut-En | 1709 | 644 |  | 0 = Disable 1 = Enable |  | TRUE | 9 |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 |  |  |  |  | 7046 | 4
York RTU.Cooling Control | Staged Cooling Command | AV | 29922 | StgClgCmd | 1709 | 648 |  | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7047 | 4
York RTU.Heating Control | Staged Heating Command | AV | 29923 | StgHtgCmd | 1709 | 649 |  | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7045 | 13
York RTU.Heating Control | Proportional Heating Command | AV | 29924 | PropHtgCmd | 1709 | 650 |  | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7046 | 13
York RTU.Cooling Control | SZ VAV Occupied Cooling Setpoint | AV | 29925 | SZVAVClgOcc-Sp | 1709 | 656 |  | 45 ... 98 deg F (7 ... 36 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 45 | 98 |  |  | 1s | deg C | 507:62 | 7 | 36 |  |  | 7048 | 4
York RTU.Cooling Control | SZ VAV Unoccupied Cooling Setpoint | AV | 29926 | SZVAVClgUnocc-Sp | 1709 | 657 |  | 45 ... 98 deg F (7 ... 36 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 45 | 98 |  |  | 1s | deg C | 507:62 | 7 | 36 |  |  | 7049 | 4
York RTU.Cooling Control | SZ VAV Operating Cooling Setpoint | AV | 29927 | OprSZVAVClg-Sp | 1709 | 660 |  | deg F (deg C) |  | FALSE | 4 | 100ths | deg F | 507:64 |  |  |  |  | 100ths | deg C | 507:62 |  |  |  |  | 7061 | 4
York RTU.Cooling Control | Low Ambient Enabled | MV | 29928 | LowAmb-En | 1709 | 662 |  | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7051 | 4
York RTU.Heating Control | SZ VAV Occupied Heating Setpoint | AV | 29929 | SZVAVHtgOcc-Sp | 1709 | 658 |  | 46 ... 99 deg F (8 ... 37 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 46 | 99 |  |  | 1s | deg C | 507:62 | 8 | 37 |  |  | 7047 | 13
York RTU.Heating Control | SZ VAV Unoccupied Heating Setpoint | AV | 29930 | SZVAVHtgUnocc-Sp | 1709 | 659 |  | 45 ... 98 deg F (7 ... 36 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 45 | 98 |  |  | 1s | deg C | 507:62 | 7 | 36 |  |  | 7048 | 13
York RTU.Cooling Control | VAV Unoccupied Cooling Setpoint | AV | 29932 | VAVClgUnocc-Sp | 1709 | 663 |  | 46 ... 99 deg F (8 ... 37 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 46 | 99 |  |  | 1s | deg C | 507:62 | 8 | 37 |  |  | 7052 | 4
York RTU.Air Monitor Station | Fresh Air Intake Enable | MV | 29933 | FrAir-En | 1709 | 664 |  | 0 = Disable 1 = Enable |  | TRUE | 9 |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 |  |  |  |  | 7004 | 24
York RTU.System Controllers.Network | BACnet Encoding Type | MV | 29934 | EncodeType | 1709 | 668 |  | 0 = ISO 10646 (UCS-2) 1 = ANSI X3.4 (US-ASCII) 2 = Microsoft DBCS code page 932 (Japanese Shift JIS) 3 = ISO 10646 (UTF-8) |  | TRUE | 9 |  | BACnet Encoding | 575 | [5 empty] | BACnet Encoding | 575 |  |  |  |  | 7008 | 31
York RTU.Cooling Control | SZ VAV Cooling Load | AV | 29935 | SZVAVClgLd | 1709 | 665 |  | % |  | FALSE | 4 | 10ths | % | 507:98 |  |  |  |  | 10ths | % | 507:98 |  |  |  |  | 7053 | 4
York RTU.Heating Control | SZ VAV Heating Load | AV | 29936 | SZVAVHtgLd | 1709 | 666 |  | % |  | FALSE | 4 | 10ths | % | 507:98 |  |  |  |  | 10ths | % | 507:98 |  |  |  |  | 7050 | 13
York RTU.Hot Gas Reheat | HGR Humidity Setpoint Differential | AV | 29937 | HGR-Diff | 1709 | 669 |  | 1 ... 10 % |  | TRUE | 4 | 1s | % | 507:98 | 1 | 10 |  |  | 1s | % | 507:98 | 1 | 10 |  |  | 7008 | 20
York RTU | Unit Enable | MV | 29896 | UnitEn | 1709 | 641 |  | 0 = Shutdown 1 = Enable |  | TRUE | 9 |  | Shutdown/Enable | 349 | [5 empty] | Shutdown/Enable | 349 |  |  |  |  | 7019 | 1
York RTU.System Controllers.Network | Device OID | AV | 29897 | DeviceId | 1709 | 353 |  | 0 ... 4194302 |  | TRUE | 2 | 1s |  | 507:95 | 0 | 4194302 |  |  | 1s |  | 507:95 | 0 | 4194302 |  |  | 7002 | 31
York RTU | Event 1 Value | AV | 29938 | Event1Value | 1709 | 710 |  |  |  | FALSE | 18 | 1s |  | 507:95 |  |  |  |  | 1s |  | 507:95 |  |  |  |  | 7023 | 1
York RTU | Event 2 Value | AV | 29940 | Event2Value | 1709 | 711 |  |  |  | FALSE | 18 | 1s |  | 507:95 |  |  |  |  | 1s |  | 507:95 |  |  |  |  | 7024 | 1
York RTU | Event 3 Value | AV | 29942 | Event3Value | 1709 | 712 |  |  |  | FALSE | 18 | 1s |  | 507:95 |  |  |  |  | 1s |  | 507:95 |  |  |  |  | 7025 | 1
York RTU | Event 4 Value | AV | 29944 | Event4Value | 1709 | 713 |  |  |  | FALSE | 18 | 1s |  | 507:95 |  |  |  |  | 1s |  | 507:95 |  |  |  |  | 7026 | 1
York RTU | Event 5 Value | AV | 29946 | Event5Value | 1709 | 714 |  |  |  | FALSE | 18 | 1s |  | 507:95 |  |  |  |  | 1s |  | 507:95 |  |  |  |  | 7027 | 1
York RTU | Event 1 Set | AV | 29939 | Event1Set | 1709 | 715 |  |  |  | FALSE | 18 | 1s |  | 507:95 |  |  |  |  | 1s |  | 507:95 |  |  |  |  | 7028 | 1
York RTU | Event 2 Set | AV | 29941 | Event2Set | 1709 | 716 |  |  |  | FALSE | 18 | 1s |  | 507:95 |  |  |  |  | 1s |  | 507:95 |  |  |  |  | 7029 | 1
York RTU | Event 3 Set | AV | 29943 | Event3Set | 1709 | 717 |  |  |  | FALSE | 18 | 1s |  | 507:95 |  |  |  |  | 1s |  | 507:95 |  |  |  |  | 7030 | 1
York RTU | Event 4 Set | AV | 29945 | Event4Set | 1709 | 718 |  |  |  | FALSE | 18 | 1s |  | 507:95 |  |  |  |  | 1s |  | 507:95 |  |  |  |  | 7031 | 1
York RTU | Event 5 Set | AV | 29947 | Event5Set | 1709 | 719 |  |  |  | FALSE | 18 | 1s |  | 507:95 |  |  |  |  | 1s |  | 507:95 |  |  |  |  | 7032 | 1
York RTU.HVAC Zone | Heat Cool Setpoint Mode | MV | 30066 | HtgClgSP-Mode | 1709 | 701 |  | 0 = Common Setpoint 1 = Individual Setpoints |  | TRUE | 9 |  | Heat Cool Setpoint Mode | 2596 | [5 empty] | Heat Cool Setpoint Mode | 2596 |  |  |  |  | 7075 | 25
York RTU.HVAC Zone | Common Setpoint | AV | 30065 | Common-SP | 1709 | 702 |  | 45 ... 98 deg F (8 ... 36 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 45 | 98 |  |  | 1s | deg C | 507:62 | 8 | 36 |  |  | 7074 | 25
York RTU.Fan Control | Dehumidification % Command | AV | 29948 | Dehum%Cmd | 1709 | 731 |  | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7042 | 3
York RTU.Hot Gas Reheat | Hot Gas Reheat Command | AV | 29949 | ModHGR | 1709 | 737 |  | % |  | FALSE | 4 | 10ths | % | 507:98 |  |  |  |  | 10ths | % | 507:98 |  |  |  |  | 7027 | 20
York RTU.Economizer | Calibration Fault Detect Enable | MV | 30067 | CalFaultDetectEn | 1709 | 723 |  | 0 = Disable 1 = Enable |  | TRUE | 9 |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 |  |  |  |  | 7032 | 19
York RTU.Shutdown Input | Pressurize Instead Of Purge | MV | 30068 | PressurizeNotPurge | 1709 | 709 |  | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7005 | 27
York RTU.Cooling Control | Cooling Allowed During Heat Limit | MV | 30071 | CoolDuringHeatLimit | 1709 | 727 |  | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7060 | 4
York RTU.Fan Control | Low Pressure Limit 1 | AV | 30072 | DAP-Min | 2645 | 244 |  | 0.01 ... 1 in wc (2.5 ... 250 Pa) |  | TRUE | 4 | 100ths | in wc | 507:58 | 0.01 | 1 |  |  | 100ths | Pa | 507:53 | 2.5 | 250 |  |  | 7038 | 3
York RTU.Fan Control | Time | AV | 30073 | DAP-AlmDly | 2645 | 245 |  | 0 ... 600 seconds |  | TRUE | 18 | 1s | seconds | 507:73 | 0 | 600 |  |  | 1s | seconds | 507:73 | 0 | 600 |  |  | 7040 | 3
York RTU.Hot Gas Reheat | Evaporator Coil Temp | AV | 30074 | EVAP-T | 2645 | 110 |  | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7026 | 20
York RTU.Hot Gas Reheat | Hot Gas Reheat Bleed Valve Command | MV | 30075 | HGRB-C | 2645 | 369 |  | 0 = Close 1 = Open |  | FALSE | 9 |  | Close/Open | 939 | [5 empty] | Close/Open | 939 |  |  |  |  | 7029 | 20
York RTU.Cooling Control | FDD Alarm Enable | MV | 30076 | FDDAlarmEn | 1709 | 733 |  | 0 = Disable 1 = Enable |  | TRUE | 9 |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 |  |  |  |  | 7062 | 4
York RTU.Cooling Control | SZ VAV Operating Cooling Setpoint | AV | 30077 | OprClgDAT-SP | 2645 | 358 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7050 | 4
York RTU.Economizer | Econ Sensor Fault Indications | MV | 30078 | EconSensorFaults | 1709 | 736 |  | 0 = Disable 1 = Enable |  | TRUE | 9 |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 |  |  |  |  | 7033 | 19
York RTU.Cooling Control | Modulating Condenser Fan 1 Output | AV | 30079 | ModCondFan1Out | 2645 | 312 |  | 0 ... 100 % |  | FALSE | 4 | 10ths | % | 507:98 | 0 | 100 |  |  | 10ths | % | 507:98 | 0 | 100 |  |  | 7065 | 4
York RTU.Cooling Control | Modulating Condenser Fan 2 Output | AV | 30080 | ModCondFan2Out | 2645 | 313 |  | 0 ... 100 % |  | FALSE | 4 | 10ths | % | 507:98 | 0 | 100 |  |  | 10ths | % | 507:98 | 0 | 100 |  |  | 7066 | 4
York RTU.Cooling Control | Modulating Compressor Output | AV | 30081 | ModCompOut | 2645 | 311 |  | 0 ... 100 % |  | FALSE | 4 | 10ths | % | 507:98 | 0 | 100 |  |  | 10ths | % | 507:98 | 0 | 100 |  |  | 7067 | 4
York RTU.Cooling Control | Circuit 1 OAT Cooling Cutout | AV | 30082 | Circ1ClgOATCutout | 2645 | 425 |  | ... 100 deg F ( ... 38 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 |  | 100 | 7070 |  | 1s | deg C | 507:62 |  | 38 | 7070 |  | 7068 | 4
York RTU.Cooling Control | Circuit 2 OAT Cooling Cutout | AV | 30083 | Circ2ClgOATCutout | 2645 | 426 |  | ... 100 deg F ( ... 38 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 |  | 100 | 7071 |  | 1s | deg C | 507:62 |  | 38 | 7071 |  | 7069 | 4
York RTU.Cooling Control | Compressor VFD Alarm | MV | 30084 | CompVFD-Alarm | 2645 | 445 |  | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7075 | 4
York RTU.Cooling Control | Saturated Suction Temperature 1 | AV | 30085 | SatSucTemp1 | 2645 | 382 |  | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7078 | 4
York RTU.Cooling Control | Saturated Discharge Temperature 1 | AV | 30086 | SatDischTemp1 | 2645 | 378 |  | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7079 | 4
York RTU.Cooling Control | Saturated Discharge Temperature 2 | AV | 30087 | SatDischTemp2 | 2645 | 379 |  | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7080 | 4
York RTU.Cooling Control | Saturated Suction Temperature 2 | AV | 30088 | SatSucTemp2 | 2645 | 383 |  | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7081 | 4
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Discharge Line Pressure | AV | 30089 | DLP1 | 2645 | 386 |  | 0 ... 750 psi (0 ... 5172 kPa) |  | FALSE | 4 | 10ths | psi | 507:56 | 0 | 750 |  |  | 1s | kPa | 507:54 | 0 | 5172 |  |  | 7024 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Discharge Line Temperature | AV | 30090 | DLT1 | 2645 | 388 |  | -50 ... 250 deg F (-45.6 ... 121.1 deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 | -50 | 250 |  |  | 10ths | deg C | 507:62 | -45.6 | 121.1 |  |  | 7025 | 6
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Discharge Line Pressure | AV | 30091 | DLP2 | 2645 | 387 |  | 0 ... 750 psi (0 ... 5172 kPa) |  | FALSE | 4 | 10ths | psi | 507:56 | 0 | 750 |  |  | 1s | kPa | 507:54 | 0 | 5172 |  |  | 7024 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Discharge Line Temperature | AV | 30092 | DLT2 | 2645 | 389 |  | -50 ... 250 deg F (-45.6 ... 121.1 deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 | -50 | 250 |  |  | 10ths | deg C | 507:62 | -45.6 | 121.1 |  |  | 7025 | 8
York RTU.Cooling Control | Suction Superheat 1 | AV | 30093 | SucSuperheat1 | 2645 | 374 |  | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7082 | 4
York RTU.HVAC Zone | Space Temperature Setpoint Offset Range | AV | 30094 | SSORange | 1709 | 50 |  | 0 ... 5 delta deg F (0 ... 3 delta deg C) |  | TRUE | 4 | 10ths | delta deg F | 507:120 | 0 | 5 |  |  | 10ths | delta deg C | 507:359 | 0 | 3 |  |  | 7028 | 25
York RTU.Hot Gas Reheat | Operational Evap Temperature Sp | AV | 30095 | OprEvapTempSp | 1709 | 729 |  | 0 ... 100 deg F (0 ... 100 deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 | 0 | 100 |  |  | 10ths | deg C | 507:62 | 0 | 100 |  |  | 7015 | 20
York RTU.Hot Gas Reheat | Operational HGR Temperature Sp | AV | 30096 | OprHGRTempSp | 1709 | 730 |  | 0 ... 100 deg F (0 ... 100 deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 | 0 | 100 |  |  | 10ths | deg C | 507:62 | 0 | 100 |  |  | 7016 | 20
York RTU.Hot Gas Reheat | Dehum Evap Low Setpoint | AV | 30097 | DehumEvapLowSp | 1709 | 725 |  | 40 ... deg F (4 ... deg C) |  | TRUE | 4 | 10ths | deg F | 507:64 | 40 |  |  | 7017 | 10ths | deg C | 507:62 | 4 |  |  | 7017 | 7018 | 20
York RTU.Hot Gas Reheat | Dehumidify In Satisfied | MV | 30099 | SatisfiedDehum | 1709 | 726 |  | 0 = False 1 = True |  | TRUE | 9 |  | False/True | 1701 | [5 empty] | False/True | 1701 |  |  |  |  | 7012 | 20
York RTU.Hot Gas Reheat | Modulating HGR Valve Full Open Allowed | MV | 30100 | ModHGRFullOpenAllowed | 1709 | 728 |  | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7024 | 20
York RTU.Hot Gas Reheat | Condenser Fan 2 OAT Cutout Setpoint | AV | 30101 | CondFan2OATCutoutSP | 1709 | 732 |  | 50 ... 80 deg F (10 ... 27 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 50 | 80 |  |  | 1s | deg C | 507:62 | 10 | 27 |  |  | 7023 | 20
York RTU.Cooling Control | Cooling Rapid Start Enable | MV | 30103 | ClgRapidStartEn | 1709 | 767 |  | 0 = Disable 1 = Enable |  | TRUE | 9 |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 |  |  |  |  | 7101 | 4
York RTU.Heating Control | Heating Rapid Start Enable | MV | 30107 | HtgRapidStartEn | 1709 | 768 |  | 0 = Disable 1 = Enable |  | TRUE | 9 |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 |  |  |  |  | 7056 | 13
York RTU.Heating Control | SZ VAV Operating Heating Setpoint | AV | 30108 | OprHtgDAT-SP | 2645 | 359 |  | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7049 | 13
York RTU.Economizer | Mixed Air Temperature Cooling Limit | MV | 30111 | MATClgLim | 2645 | 293 |  | 0 = Disable 1 = Enable |  | TRUE | 9 |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 |  |  |  |  | 7034 | 19
York RTU.Heat Pump Control | OAT Heat Pump Cutout | AV | 30132 | OATHPCutout | 1709 | 780 |  | -20 ... 50 deg F (-29 ... 10 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | -20 | 50 |  |  | 1s | deg C | 507:62 | -29 | 10 |  |  | 7017 | 38
York RTU.Hot Gas Reheat | Use OprST for HGR | MV | 30133 | UseOprSTforHGR | 1709 | 777 |  | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7031 | 20
York RTU.Hot Gas Reheat | Min Heating Setpoint | AV | 30136 | HGRModVlvMinSP | 1709 | 783 |  | 0 ... 100 % |  | TRUE | 4 | 10ths | % | 507:98 | 0 | 100 |  |  | 10ths | % | 507:98 | 0 | 100 |  |  | 7014 | 20
York RTU.Hot Gas Reheat | Max Heating Setpoint | AV | 30137 | HGRModVlvMaxSP | 1709 | 782 |  | 0 ... 100 % |  | TRUE | 4 | 10ths | % | 507:98 | 0 | 100 |  |  | 10ths | % | 507:98 | 0 | 100 |  |  | 7013 | 20
York RTU.Hot Gas Reheat | Use DFS For Dehum | MV | 30138 | UseDFSforDehum | 1709 | 721 |  | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7010 | 20
York RTU.Hot Gas Reheat | Aux Mode | MV | 30139 | HybridMode | 1709 | 781 |  | 0 = Off 1 = On |  | TRUE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7009 | 20
York RTU.Cooling Control | Cooling Rapid Start Time | AV | 30140 | ClgRapidStartTime | 1709 | 769 |  | 2 ... 30 minutes |  | TRUE | 4 | 1s | minutes | 507:72 | 2 | 30 |  |  | 1s | minutes | 507:72 | 2 | 30 |  |  | 7102 | 4
York RTU.Heating Control | Heating Rapid Start Time | AV | 30141 | HtgRapidStartTime | 1709 | 770 |  | 2 ... 30 minutes |  | TRUE | 4 | 1s | minutes | 507:72 | 2 | 30 |  |  | 1s | minutes | 507:72 | 2 | 30 |  |  | 7057 | 13
York RTU.Cooling Control | A2L Leak Detector Alarm | MV | 30134 | A2LLeakAlarm | 1709 | 787 |  | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7103 | 4
York RTU.Cooling Control | A2L Leak Detector Alarm-Lockout | MV | 30135 | A2LLeakAlarm-LO | 1709 | 791 |  | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7106 | 4
York RTU.Cooling Control | Condensate Overflow Switch | MV | 30136 | COS | 1709 | 788 |  | 0 = Alarm 1 = Normal |  | FALSE | 9 |  | Alarm/Normal | 1696 | [5 empty] | Alarm/Normal | 1696 |  |  |  |  | 7108 | 4
York RTU.Hot Gas Reheat | Neutral Air ModHGR Enable | MV | 30143 | NeuAirModHGR-En | 1709 | 792 |  | 0 = Disable 1 = Enable |  | TRUE | 9 |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 |  |  |  |  | 7032 | 20
York RTU.Hot Gas Reheat | Neutral Air ModHGR Offset | AV | 30145 | NeuAirModHGR-Off | 1709 | 793 |  | -10 ... 10 delta deg F (-6 ... 6 delta deg C) |  | TRUE | 4 | 1s | delta deg F | 507:120 | -10 | 10 |  |  | 1s | delta deg C | 507:359 | -6 | 6 |  |  | 7033 | 20
York RTU.Heat Pump Control | Dual Fuel OAT HP Cutout | AV | 30151 | DualFuelOATHPCutout | 1709 | 796 |  | 0 ... 65 deg F (-18 ... 18 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 0 | 65 |  |  | 1s | deg C | 507:62 | -18 | 18 |  |  | 7019 | 38
York RTU.Cooling Control | Condensate Alarm Enable | MV | 30156 | COS-En | 1709 | 797 |  | 0 = Disable 1 = Enable |  | TRUE | 9 |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 |  |  |  |  | 7107 | 4

## FC-Bus Modbus
Model Fullname | Attribute | Name (free) | Name (Dict) | Name SetId | Name EnumId | Object Type | Object Address | Is Signed | Offset | Factor | Factor Id | Enum Set / Range | Remarks | Write-able | Data Type Id | Display Prec. (IP) | Unit (IP) | Unit Id (IP) | Min Value (IP) | Max Value (IP) | Min Prop. (IP) | Max Prop. (IP) | Display Prec. (SI) | Unit (SI) | Unit Id (SI) | Min Value (SI) | Max Value (SI) | Min Prop. (SI) | Max Prop. (SI) | Prop. Id | EM Object Id
York RTU | Unit Status | Unit-S | Not Set | 344 | 2 | InputRegister | 280 | FALSE | 0 | 1 | 4 | 0 = Idle 1 = SD Alarm 2 = Purge Command 3 = Self Test ... |  | FALSE | 9 |  | SE RTU Unit Status | 1737 | [5 empty] | SE RTU Unit Status | 1737 |  |  |  |  | 7000 | 1
York RTU | Exhaust Type | ExFType | Not Set | 344 | 2 | HoldingRegister | 412 | FALSE | 0 | 1 | 4 | 0 = None 1 = Non-Modulating 2 = Modulating Damper 3 = Variable Frequency Fan |  | TRUE | 9 |  | SE RTU Exhaust Setup | 1639 | [5 empty] | SE RTU Exhaust Setup | 1639 |  |  |  |  | 7008 | 1
York RTU | Reset Lockouts | ResetLO | Not Set | 344 | 2 | HoldingRegister | 80 | FALSE | 0 | 1 | 4 | 0 = Off 1 = On |  | TRUE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7011 | 1
York RTU | SZ VAV Enabled | SZVAVEN | Not Set | 344 | 2 | InputRegister | 399 | FALSE | 0 | 1 | 4 | 0 = Off 1 = On |  | TRUE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7020 | 1
York RTU | Hardware Reset | HdwrReset | Not Set | 344 | 2 | HoldingRegister | 126 | FALSE | 0 | 1 | 4 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7021 | 1
York RTU.Thermostat Control | Y1 - Thermostat | Y1-Tstat | Not Set | 344 | 2 | InputRegister | 281 | FALSE | 0 | 1 | 4 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7000 | 2
York RTU.Thermostat Control | Y2 - Thermostat | Y2-Tstat | Not Set | 344 | 2 | InputRegister | 282 | FALSE | 0 | 1 | 4 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7001 | 2
York RTU.Thermostat Control | Y3 - Thermostat | Y3-Tstat | Not Set | 344 | 2 | InputRegister | 283 | FALSE | 0 | 1 | 4 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7002 | 2
York RTU.Thermostat Control | Y4 - Thermostat | Y4-Tstat | Not Set | 344 | 2 | InputRegister | 284 | FALSE | 0 | 1 | 4 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7003 | 2
York RTU.Thermostat Control | W1 - Thermostat | W1-Tstat | Not Set | 344 | 2 | InputRegister | 285 | FALSE | 0 | 1 | 4 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7004 | 2
York RTU.Thermostat Control | W2 - Thermostat | W2-Tstat | Not Set | 344 | 2 | InputRegister | 286 | FALSE | 0 | 1 | 4 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7005 | 2
York RTU.Thermostat Control | W3 - Thermostat | W3-Tstat | Not Set | 344 | 2 | InputRegister | 287 | FALSE | 0 | 1 | 4 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7006 | 2
York RTU.Thermostat Control | G - Thermostat | G-Tstat | Not Set | 344 | 2 | InputRegister | 288 | FALSE | 0 | 1 | 4 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7007 | 2
York RTU.Thermostat Control | X-OUT | X-Out | Not Set | 344 | 2 | InputRegister | 289 | FALSE | 0 | 1 | 4 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7009 | 2
York RTU.Thermostat Control | Thermostat Only Control Enabled | Tstat-Only | Not Set | 344 | 2 | HoldingRegister | 413 | FALSE | 0 | 1 | 4 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7010 | 2
York RTU.Fan Control | Fan Status | Fan-S | Not Set | 344 | 2 | InputRegister | 302 | FALSE | 0 | 1 | 4 | 0 = Off-Idle 1 = On-Purge 2 = On-Gas Valve or Limit Fault 3 = On-Defrost ... |  | FALSE | 9 |  | SE RTU Fan Status | 1739 | [5 empty] | SE RTU Fan Status | 1739 |  |  |  |  | 7000 | 3
York RTU.Fan Control | Fan % Command | FanVFD | Not Set | 344 | 2 | InputRegister | 157 | TRUE | 0 | 10 | 5 | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7001 | 3
York RTU.Fan Control | Fan VFD Fault | FanVFDFlt | Not Set | 344 | 2 | InputRegister | 303 | FALSE | 0 | 1 | 4 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7002 | 3
York RTU.Fan Control | Fan Overload | FanOvrload | Not Set | 344 | 2 | InputRegister | 304 | FALSE | 0 | 1 | 4 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7003 | 3
York RTU.Fan Control | Fan Accumulated Runtime | Fan-RT | Not Set | 344 | 2 | InputRegister | 9 | FALSE | 0 | 10 | 5 | 0 ... 10000 hours |  | TRUE | 4 | 1s | hours | 507:71 | 0 | 10000 |  |  | 1s | hours | 507:71 | 0 | 10000 |  |  | 7004 | 3
York RTU.Fan Control | Fan Control Type | FANCTLTYPE | Not Set | 344 | 2 | HoldingRegister | 400 | FALSE | 0 | 1 | 4 | 0 = Single Speed 1 = Not Used 2 = Fixed Variable 3 = Variable Speed |  | TRUE | 9 |  | SE RTU Fan Control Type | 1619 | [5 empty] | SE RTU Fan Control Type | 1619 |  |  |  |  | 7005 | 3
York RTU.Fan Control | Air Proving Switch Setup | APSSetup | Not Set | 344 | 2 | HoldingRegister | 414 | FALSE | 0 | 1 | 4 | 0 = Constant Volume 1 = Variable Volume 2 = None |  | TRUE | 9 |  | Fan Setup | 1622 | [5 empty] | Fan Setup | 1622 |  |  |  |  | 7006 | 3
York RTU.Fan Control | Air Proving Switch | APS | Not Set | 344 | 2 | InputRegister | 305 | FALSE | 0 | 1 | 4 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7007 | 3
York RTU.Fan Control | Fan On Delay for Cool | FanOnDlyCool | Not Set | 344 | 2 | HoldingRegister | 90 | FALSE | 0 | 1 | 4 | 0 ... 30 seconds |  | TRUE | 17 | 1s | seconds | 507:73 | 0 | 30 |  |  | 1s | seconds | 507:73 | 0 | 30 |  |  | 7008 | 3
York RTU.Fan Control | Fan Off Delay for Cool | FanOffDlyCool | Not Set | 344 | 2 | HoldingRegister | 415 | FALSE | 0 | 1 | 4 | 0 ... 255 seconds |  | TRUE | 17 | 1s | seconds | 507:73 | 0 | 255 |  |  | 1s | seconds | 507:73 | 0 | 255 |  |  | 7009 | 3
York RTU.Fan Control | Fan On Delay for Heat | FanOnDlyHeat | Not Set | 344 | 2 | HoldingRegister | 416 | FALSE | 0 | 1 | 4 | 0 ... 30 seconds |  | TRUE | 17 | 1s | seconds | 507:73 | 0 | 30 |  |  | 1s | seconds | 507:73 | 0 | 30 |  |  | 7010 | 3
York RTU.Fan Control | Fan Off Delay for Heat | FanOffDlyHeat | Not Set | 344 | 2 | HoldingRegister | 417 | FALSE | 0 | 1 | 4 | 0 ... 255 seconds |  | TRUE | 17 | 1s | seconds | 507:73 | 0 | 255 |  |  | 1s | seconds | 507:73 | 0 | 255 |  |  | 7011 | 3
York RTU.Fan Control | Dirty Filter Switch | DFS | Not Set | 344 | 2 | InputRegister | 306 | FALSE | 0 | 1 | 4 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7012 | 3
York RTU.Fan Control | Fan Command | Fan | Not Set | 344 | 2 | InputRegister | 307 | FALSE | 0 | 1 | 4 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7013 | 3
York RTU.Fan Control | Supply Air Temperature | SAT | Not Set | 344 | 2 | InputRegister | 158 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7014 | 3
York RTU.Fan Control | Duct Static Pressure | DctPrs | Not Set | 344 | 2 | InputRegister | 159 | TRUE | 0 | 100 | 6 | in wc (kPa) |  | FALSE | 4 | 100ths | in wc | 507:58 |  |  |  |  | 100ths | kPa | 507:54 |  |  |  |  | 7015 | 3
York RTU.Fan Control | Duct Pressure Setpoint | DctPrs-Sp | Not Set | 344 | 2 | HoldingRegister | 10 | TRUE | 0 | 100 | 6 | 0 ... 5 in wc (0 ... 1.25 kPa) |  | TRUE | 4 | 100ths | in wc | 507:58 | 0 | 5 |  |  | 100ths | kPa | 507:54 | 0 | 1.25 |  |  | 7016 | 3
York RTU.Fan Control | Duct Pressure Shutdown Setpoint | DctShutdownSp | Not Set | 344 | 2 | HoldingRegister | 11 | TRUE | 0 | 100 | 6 | 0 ... 5 in wc (0 ... 1.25 kPa) |  | TRUE | 4 | 100ths | in wc | 507:58 | 0 | 5 |  |  | 100ths | kPa | 507:54 | 0 | 1.25 |  |  | 7017 | 3
York RTU.Fan Control | Continuous Fan Operation in Occupied Mode | FanOnOcc | Not Set | 344 | 2 | HoldingRegister | 91 | FALSE | 0 | 1 | 4 | 0 = Yes 1 = No |  | TRUE | 9 |  | Yes/No | 1698 | [5 empty] | Yes/No | 1698 |  |  |  |  | 7018 | 3
York RTU.Fan Control | Turn Off Continuous Fan Operation When Starting Heat | FanOffStartHeat | Not Set | 344 | 2 | HoldingRegister | 92 | FALSE | 0 | 1 | 4 | 0 = Yes 1 = No |  | TRUE | 9 |  | Yes/No | 1698 | [5 empty] | Yes/No | 1698 |  |  |  |  | 7019 | 3
York RTU.Fan Control | Occupied: No Heat or Cool % Command | FanOnly-%Cmd | Not Set | 344 | 2 | HoldingRegister | 12 | TRUE | 0 | 10 | 5 | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7020 | 3
York RTU.Fan Control | Occupied: One Stage of Cool % Command | 1ClgStg-%Cmd | Not Set | 344 | 2 | HoldingRegister | 13 | TRUE | 0 | 10 | 5 | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7021 | 3
York RTU.Fan Control | Occupied: Two Stage of Cool % Command | 2ClgStg-%Cmd | Not Set | 344 | 2 | HoldingRegister | 14 | TRUE | 0 | 10 | 5 | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7022 | 3
York RTU.Fan Control | Occupied: One Stage of Heat % Command | 1HtgStg-%Cmd | Not Set | 344 | 2 | HoldingRegister | 17 | TRUE | 0 | 10 | 5 | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7023 | 3
York RTU.Fan Control | Occupied: Two Stage of Heat % Command | 2HtgStg-%Cmd | Not Set | 344 | 2 | HoldingRegister | 18 | TRUE | 0 | 10 | 5 | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7024 | 3
York RTU.Fan Control | Occupied: Three Stage of Cool % Command | 3ClgStg-%Cmd | Not Set | 344 | 2 | HoldingRegister | 15 | TRUE | 0 | 10 | 5 | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7027 | 3
York RTU.Fan Control | Occupied: Four Stage of Cool % Command | 4ClgStg-%Cmd | Not Set | 344 | 2 | HoldingRegister | 16 | TRUE | 0 | 10 | 5 | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7028 | 3
York RTU.Fan Control | Occupied: Three Stage of Heat % Command | 3HtgStg-%Cmd | Not Set | 344 | 2 | HoldingRegister | 19 | TRUE | 0 | 10 | 5 | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7029 | 3
York RTU.Fan Control | SZ VAV Minimum Fan Speed | SZVAVMinFanSpd | Not Set | 344 | 2 | HoldingRegister | 73 | TRUE | 0 | 10 | 5 | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7037 | 3
York RTU.Cooling Control | Cooling Mode Enabled For Operation | Clg-En | Not Set | 344 | 2 | HoldingRegister | 93 | FALSE | 0 | 1 | 4 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7000 | 4
York RTU.Cooling Control | Number of Cooling Stages Installed | #ClgStgs | Not Set | 344 | 2 | HoldingRegister | 401 | FALSE | 0 | 1 | 4 | 1 ... 4 |  | TRUE | 16 | 1s |  | 507:95 | 1 | 4 |  |  | 1s |  | 507:95 | 1 | 4 |  |  | 7001 | 4
York RTU.Cooling Control | Cooling Status | Clg-S | Not Set | 344 | 2 | InputRegister | 308 | FALSE | 0 | 1 | 4 | 0 = Off-Idle 1 = Thermostat Cooling 2 = Unoccupied Cooling 3 = Occupied Cooling ... |  | FALSE | 9 |  | SE RTU Cooling Control Status | 1740 | [5 empty] | SE RTU Cooling Control Status | 1740 |  |  |  |  | 7002 | 4
York RTU.Cooling Control | Minimum Runtime for a Cooling Stage | MinRtCoolStg | Not Set | 344 | 2 | InputRegister | 20 | FALSE | 0 | 10 | 5 | 3 ... 10 minutes |  | TRUE | 16 | 1s | minutes | 507:72 | 3 | 10 |  |  | 1s | minutes | 507:72 | 3 | 10 |  |  | 7003 | 4
York RTU.Cooling Control | Lead/Lag Equalize Cooling Stage Runtime Enabled | LeadLag-En | Not Set | 344 | 2 | HoldingRegister | 402 | FALSE | 0 | 1 | 4 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7004 | 4
York RTU.Cooling Control | Low Ambient Fan Pre-run Time For Cooling | LowAmbFanPrerunCool | Not Set | 344 | 2 | HoldingRegister | 418 | FALSE | 0 | 1 | 4 | 0 ... 255 seconds |  | TRUE | 17 | 1s | seconds | 507:73 | 0 | 255 |  |  | 1s | seconds | 507:73 | 0 | 255 |  |  | 7005 | 4
York RTU.Cooling Control | OAT Cooling Cutout Enabled | ClgOATCutout-En | Not Set | 344 | 2 | HoldingRegister | 94 | FALSE | 0 | 1 | 4 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7006 | 4
York RTU.Cooling Control | OAT Cooling Cutout | ClgOATCutout | Not Set | 344 | 2 | HoldingRegister | 21 | TRUE | 0 | 10 | 5 | 0 ... 100 deg F (-18 ... 38 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 0 | 100 |  |  | 1s | deg C | 507:62 | -18 | 38 |  |  | 7007 | 4
York RTU.Cooling Control | Economizer Loading Enabled | EconLoad-En | Not Set | 344 | 2 | HoldingRegister | 95 | FALSE | 0 | 1 | 4 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7008 | 4
York RTU.Cooling Control | All Compressors Off in Free Cooling | AllCompOff-Econ | Not Set | 344 | 2 | HoldingRegister | 96 | FALSE | 0 | 1 | 4 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7009 | 4
York RTU.Cooling Control | Low Ambient Cooling Stages 10 on 5 off Setpoint | LowAmb10On5OffSp | Not Set | 344 | 2 | HoldingRegister | 419 | FALSE | 0 | 1 | 4 | 0 ... 60 deg F (-18 ... 15 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 0 | 60 |  |  | 1s | deg C | 507:62 | -18 | 15 |  |  | 7010 | 4
York RTU.Cooling Control | Temperature/Humidity (Return) Control Enable | TempHumCtrl-En | Not Set | 344 | 2 | HoldingRegister | 97 | FALSE | 0 | 1 | 4 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7011 | 4
York RTU.Cooling Control | Temperature/Humidity Setpoint | TempHum-Sp | Not Set | 344 | 2 | HoldingRegister | 22 | TRUE | 0 | 10 | 5 | 20 ... 80 %RH |  | TRUE | 4 | 1s | %RH | 507:29 | 20 | 80 |  |  | 1s | %RH | 507:29 | 20 | 80 |  |  | 7012 | 4
York RTU.Cooling Control | Maximum Temperature / Humidity Setpoint Offset | MaxTempHumSpOff | Not Set | 344 | 2 | HoldingRegister | 23 | TRUE | 0 | 10 | 5 | 0 ... 5 delta deg F (0 ... 3 delta deg C) |  | TRUE | 4 | 10ths | delta deg F | 507:120 | 0 | 5 |  |  | 10ths | delta deg C | 507:359 | 0 | 3 |  |  | 7013 | 4
York RTU.Cooling Control | Temperature / Humidity Value per Degree Offset | TempHumValPerDegOff | Not Set | 344 | 2 | HoldingRegister | 24 | TRUE | 0 | 10 | 5 | 1 ... 10 %RH |  | TRUE | 4 | 1s | %RH | 507:29 | 1 | 10 |  |  | 1s | %RH | 507:29 | 1 | 10 |  |  | 7014 | 4
York RTU.Cooling Control | SAT Limit for Cooling Enable | SATCoolLimit-En | Not Set | 344 | 2 | HoldingRegister | 98 | FALSE | 0 | 1 | 4 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7015 | 4
York RTU.Cooling Control | SAT Limit for Cooling Setpoint | SATCoolLimit-Sp | Not Set | 344 | 2 | HoldingRegister | 25 | TRUE | 0 | 10 | 5 | 40 ... 65 deg F (4 ... 18 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 40 | 65 |  |  | 1s | deg C | 507:62 | 4 | 18 |  |  | 7016 | 4
York RTU.Cooling Control | Freeze Condition Setpoint | Freeze-Sp | Not Set | 344 | 2 | HoldingRegister | 420 | FALSE | 0 | 10 | 5 | 20 ... 32 deg F (-7 ... 0 deg C) |  | TRUE | 4 | 10ths | deg F | 507:64 | 20 | 32 |  |  | 10ths | deg C | 507:62 | -7 | 0 |  |  | 7017 | 4
York RTU.Cooling Control | Condenser Fan 1 | CN-Fan | Not Set | 344 | 2 | InputRegister | 309 | FALSE | 0 | 1 | 4 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7018 | 4
York RTU.Cooling Control | Condenser Fan 2 | CF2 | Not Set | 344 | 2 | InputRegister | 310 | FALSE | 0 | 1 | 4 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7019 | 4
York RTU.Cooling Control | Unit Type | UnitType | Not Set | 344 | 2 | HoldingRegister | 403 | FALSE | 0 | 1 | 4 | 0 = Not Used 1 = Package Cool 2 = Package HP 3 = Split Cool ... |  | TRUE | 9 |  | SE RTU Equipment Type | 1685 | [5 empty] | SE RTU Equipment Type | 1685 |  |  |  |  | 7020 | 4
York RTU.Cooling Control | EER | EER | Not Set | 344 | 2 | HoldingRegister | 404 | TRUE | 0 | 10 | 5 | 0 ... 20 |  | TRUE | 4 | 1s |  | 507:95 | 0 | 20 |  |  | 1s |  | 507:95 | 0 | 20 |  |  | 7021 | 4
York RTU.Cooling Control | Subcooling Goal | SubcoolGoal | Not Set | 344 | 2 | HoldingRegister | 421 | FALSE | 0 | 1 | 4 | -10 ... 20 deg F (-23 ... -6 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | -10 | 20 |  |  | 1s | deg C | 507:62 | -23 | -6 |  |  | 7022 | 4
York RTU.Cooling Control | Refrigerant Type | RefrigType | Not Set | 344 | 2 | InputRegister | 405 | FALSE | 0 | 1 | 4 | 0 = R22 1 = R12 2 = R500 3 = R134A ... |  | TRUE | 9 |  | SE RTU Refrigerant Type | 1682 | [5 empty] | SE RTU Refrigerant Type | 1682 |  |  |  |  | 7023 | 4
York RTU.Cooling Control | High Side Port Location | HiSidePortLoc | Not Set | 344 | 2 | HoldingRegister | 422 | FALSE | 0 | 1 | 4 | 0 = Liquid 1 = Discharge |  | TRUE | 9 |  | SE RTU High Side Port | 1681 | [5 empty] | SE RTU High Side Port | 1681 |  |  |  |  | 7024 | 4
York RTU.Cooling Control | Evaporator Coil Type | EvapCoil-Type | Not Set | 344 | 2 | HoldingRegister | 406 | FALSE | 0 | 1 | 4 | 0 = MicroChannel 1 = Tube and Fin |  | TRUE | 9 |  | Cooling Coil Type | 1722 | [5 empty] | Cooling Coil Type | 1722 |  |  |  |  | 7025 | 4
York RTU.Cooling Control | Condenser Coil Type | CondCoil-Type | Not Set | 344 | 2 | HoldingRegister | 423 | FALSE | 0 | 1 | 4 | 0 = MicroChannel 1 = Tube and Fin |  | TRUE | 9 |  | Cooling Coil Type | 1722 | [5 empty] | Cooling Coil Type | 1722 |  |  |  |  | 7026 | 4
York RTU.Cooling Control | Indoor Metering Device Type | InMeterDev-Type | Not Set | 344 | 2 | HoldingRegister | 424 | FALSE | 0 | 1 | 4 | 0 = TxV 1 = FO 2 = TxV Or FO 3 = n |  | TRUE | 9 |  | SE RTU Expansion Device | 1684 | [5 empty] | SE RTU Expansion Device | 1684 |  |  |  |  | 7027 | 4
York RTU.Cooling Control | Outdoor Metering Device Type | OutMeterDev-Type | Not Set | 344 | 2 | HoldingRegister | 425 | FALSE | 0 | 1 | 4 | 0 = TxV 1 = FO 2 = TxV Or FO 3 = n |  | TRUE | 9 |  | SE RTU Expansion Device | 1684 | [5 empty] | SE RTU Expansion Device | 1684 |  |  |  |  | 7028 | 4
York RTU.Cooling Control | VAV Cooling Supply Air Temp Upper Setpoint | SATUp-Sp | Not Set | 344 | 2 | HoldingRegister | 26 | TRUE | 0 | 10 | 5 | 41 ... 70 deg F (5 ... 21 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 41 | 70 |  |  | 1s | deg C | 507:62 | 5 | 21 |  |  | 7029 | 4
York RTU.Cooling Control | VAV Cooling Supply Air Temp Lower Setpoint | SATLo-Sp | Not Set | 344 | 2 | HoldingRegister | 27 | TRUE | 0 | 10 | 5 | 40 ... 69 deg F (4 ... 20 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 40 | 69 |  |  | 1s | deg C | 507:62 | 4 | 20 |  |  | 7030 | 4
York RTU.Cooling Control | VAV Supply Air Temp Reset Setpoint | SATRst-Sp | Not Set | 344 | 2 | HoldingRegister | 28 | TRUE | 0 | 10 | 5 | 40 ... 85 deg F (4 ... 30 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 40 | 85 |  |  | 1s | deg C | 507:62 | 4 | 30 |  |  | 7031 | 4
York RTU.Cooling Control | VAV Operating Cooling Setpoint | OprVAVClg-Sp | Not Set | 344 | 2 | InputRegister | 160 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 100ths | deg F | 507:64 |  |  |  |  | 100ths | deg C | 507:62 |  |  |  |  | 7032 | 4
York RTU.Cooling Control | CV Occupied Cooling Setpoint | ClgOcc-Sp | Not Set | 344 | 2 | HoldingRegister | 29 | TRUE | 0 | 10 | 5 | 45 ... 98 deg F (7 ... 36 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 45 | 98 |  |  | 1s | deg C | 507:62 | 7 | 36 |  |  | 7033 | 4
York RTU.Cooling Control | CV Unoccupied Cooling Setpoint | ClgUnocc-Sp | Not Set | 344 | 2 | HoldingRegister | 30 | TRUE | 0 | 10 | 5 | 46 ... 99 deg F (8 ... 37 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 46 | 99 |  |  | 1s | deg C | 507:62 | 8 | 37 |  |  | 7034 | 4
York RTU.Cooling Control | CV Operating Cooling Setpoint | OprCVClg-Sp | Not Set | 344 | 2 | InputRegister | 161 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 100ths | deg F | 507:64 |  |  |  |  | 100ths | deg C | 507:62 |  |  |  |  | 7035 | 4
York RTU.Cooling Control | Unit Capacity | UnitCap | Not Set | 344 | 2 | HoldingRegister | 407 | FALSE | 0 | 10 | 5 | 0 ... 130 tons refr (0 ... 460 kW) |  | TRUE | 4 | 10ths | tons refr | 507:52 | 0 | 130 |  |  | 10ths | kW | 507:48 | 0 | 460 |  |  | 7038 | 4
York RTU.Cooling Control | Fan Power | FanPower | Not Set | 344 | 2 | HoldingRegister | 426 | FALSE | 0 | 10 | 5 | 0 ... 19 kW |  | TRUE | 4 | 10ths | kW | 507:48 | 0 | 19 |  |  | 10ths | kW | 507:48 | 0 | 19 |  |  | 7039 | 4
York RTU.Cooling Control | Super Heat Goal | SuperHeatGoal | Not Set | 344 | 2 | HoldingRegister | 427 | FALSE | 0 | 10 | 5 | 10 ... 30 deg F (-12.2 ... -1.1 deg C) |  | TRUE | 4 | 10ths | deg F | 507:64 | 10 | 30 |  |  | 10ths | deg C | 507:62 | -12.2 | -1.1 |  |  | 7040 | 4
York RTU.Cooling Control | Altitude | Altitude | Not Set | 344 | 2 | HoldingRegister | 31 | TRUE | 0 | 10 | 5 | -1500 ... 30000 ft (-457.2 ... 9144 m) |  | TRUE | 4 | 10ths | ft | 507:33 | -1500 | 30000 |  |  | 10ths | m | 507:31 | -457.2 | 9144 |  |  | 7041 | 4
York RTU.Cooling Control | Cooling Adaptive Tuning Enable | ClgAdapTunEn | Not Set | 344 | 2 | HoldingRegister | 100 | FALSE | 0 | 1 | 4 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7043 | 4
York RTU.Cooling Control | Number of Refrig Systems Installed | #RefrigSys | Not Set | 344 | 2 | HoldingRegister | 32 | FALSE | 0 | 10 | 5 | 0 ... 4 |  | TRUE | 4 | 1s |  | 507:95 | 0 | 4 |  |  | 1s |  | 507:95 | 0 | 4 |  |  | 7044 | 4
York RTU.Cooling Control | DAT Cooling Min SP | DATClgMinSP | Not Set | 344 | 2 | HoldingRegister | 74 | TRUE | 0 | 10 | 5 | 50 ... 60 deg F (9.5 ... 15.6 deg C) |  | TRUE | 4 | 10ths | deg F | 507:64 | 50 | 60 |  |  | 10ths | deg C | 507:62 | 9.5 | 15.6 |  |  | 7045 | 4
York RTU.Cooling Control | Pump Out Enable | PmpOut-En | Not Set | 344 | 2 | HoldingRegister | 428 | FALSE | 0 | 1 | 4 | 0 = Disable 1 = Enable |  | TRUE | 9 |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 |  |  |  |  | 7046 | 4
York RTU.Cooling Control | Staged Cooling Command | StgClgCmd | Not Set | 344 | 2 | InputRegister | 263 | TRUE | 0 | 10 | 5 | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7047 | 4
York RTU.Cooling Control | Low Ambient Enabled | LowAmb-En | Not Set | 344 | 2 | HoldingRegister | 429 | FALSE | 0 | 1 | 4 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7051 | 4
York RTU.Cooling Control.DX Cooling Circuit 1 | Compressor Stage Command | C1 | Not Set | 344 | 2 | InputRegister | 311 | FALSE | 0 | 1 | 4 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7001 | 5
York RTU.Cooling Control.DX Cooling Circuit 1 | Compressor Stage Status | C1-S | Not Set | 344 | 2 | InputRegister | 312 | FALSE | 0 | 1 | 4 | 0 = Off-Idle 1 = On-Minimum On Time 2 = On-Normal Command 3 = Off-Cooling Is Disabled ... |  | FALSE | 9 |  | SE RTU DX Cooling Circuit 1 Status | 1741 | [5 empty] | SE RTU DX Cooling Circuit 1 Status | 1741 |  |  |  |  | 7002 | 5
York RTU.Cooling Control.DX Cooling Circuit 1 | Compressor Stage Enabled | C1-En | Not Set | 344 | 2 | HoldingRegister | 101 | FALSE | 0 | 1 | 4 | 0 = Yes 1 = No |  | TRUE | 9 |  | Yes/No | 1698 | [5 empty] | Yes/No | 1698 |  |  |  |  | 7003 | 5
York RTU.Cooling Control.DX Cooling Circuit 1 | Hot Gas Bypass Present | HGP-Inst | Not Set | 344 | 2 | HoldingRegister | 408 | FALSE | 0 | 1 | 4 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7004 | 5
York RTU.Cooling Control.DX Cooling Circuit 1 | Compressor Stage Accumulated Runtime | C1RunTim | Not Set | 344 | 2 | InputRegister | 33 | FALSE | 0 | 10 | 5 | 0 ... 10000 hours |  | TRUE | 4 | 1s | hours | 507:71 | 0 | 10000 |  |  | 1s | hours | 507:71 | 0 | 10000 |  |  | 7005 | 5
York RTU.Cooling Control.DX Cooling Circuit 1 | Min On Time Remaining | C1OnTmr | Not Set | 344 | 2 | InputRegister | 162 | FALSE | 0 | 1 | 4 | seconds |  | FALSE | 17 | 1s | seconds | 507:73 |  |  |  |  | 1s | seconds | 507:73 |  |  |  |  | 7007 | 5
York RTU.Cooling Control.DX Cooling Circuit 1 | Anti-Short Cycle Delay Time Remaining | C1ASCDTmr | Not Set | 344 | 2 | InputRegister | 163 | FALSE | 0 | 1 | 4 | seconds |  | FALSE | 17 | 1s | seconds | 507:73 |  |  |  |  | 1s | seconds | 507:73 |  |  |  |  | 7008 | 5
York RTU.Cooling Control.DX Cooling Circuit 1 | High Pressure Limit | HPS1 | Not Set | 344 | 2 | InputRegister | 313 | FALSE | 0 | 1 | 4 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7009 | 5
York RTU.Cooling Control.DX Cooling Circuit 1 | High Pressure Lockout | HPS1-LO | Not Set | 344 | 2 | InputRegister | 314 | FALSE | 0 | 1 | 4 | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7010 | 5
York RTU.Cooling Control.DX Cooling Circuit 1 | Low Pressure Limit | LPS1 | Not Set | 344 | 2 | InputRegister | 315 | FALSE | 0 | 1 | 4 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7011 | 5
York RTU.Cooling Control.DX Cooling Circuit 1 | Low Pressure Lockout | LPS1-LO | Not Set | 344 | 2 | InputRegister | 316 | FALSE | 0 | 1 | 4 | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7012 | 5
York RTU.Cooling Control.DX Cooling Circuit 1 | Freeze Condition | FS1 | Not Set | 344 | 2 | InputRegister | 317 | FALSE | 0 | 1 | 4 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7013 | 5
York RTU.Cooling Control.DX Cooling Circuit 1 | Freeze Condition Lockout | FS1-LO | Not Set | 344 | 2 | InputRegister | 318 | FALSE | 0 | 1 | 4 | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7014 | 5
York RTU.Cooling Control.DX Cooling Circuit 1 | Evaporator Coil Temp | EC1 | Not Set | 344 | 2 | InputRegister | 164 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7015 | 5
York RTU.Cooling Control.DX Cooling Circuit 1 | Condenser Coil Temp | CC1 | Not Set | 344 | 2 | InputRegister | 165 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7016 | 5
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Cooling Circuit Test Status | ClgCktTestS-1 | Not Set | 344 | 2 | InputRegister | 343 | FALSE | 0 | 1 | 4 | 0 = Unknown Status 1 = Basic Data Not Available Manual Entry 2 = Basic Data Not Available 3 = Return Wet Bulb Temp Not Available ... |  | FALSE | 9 |  | SE FDD Codes | 1694 | [5 empty] | SE FDD Codes | 1694 |  |  |  |  | 7000 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Suction Pressure | SLP-1 | Not Set | 344 | 2 | InputRegister | 178 | TRUE | 0 | 10 | 5 | psi (kPa) |  | FALSE | 4 | 10ths | psi | 507:56 |  |  |  |  | 1s | kPa | 507:54 |  |  |  |  | 7001 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Liquid Pressure | LLP-1 | Not Set | 344 | 2 | InputRegister | 179 | TRUE | 0 | 10 | 5 | psi (kPa) |  | FALSE | 4 | 10ths | psi | 507:56 |  |  |  |  | 1s | kPa | 507:54 |  |  |  |  | 7002 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Suction Temperature | SLT-1 | Not Set | 344 | 2 | InputRegister | 180 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7003 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Liquid Temperature | LLT-1 | Not Set | 344 | 2 | InputRegister | 181 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7004 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Superheat | C1-SuperHeat | Not Set | 344 | 2 | InputRegister | 182 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7005 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Subcooling | C1-SubCool | Not Set | 344 | 2 | InputRegister | 183 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7006 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Condensing Temperature over Ambient | C1-CondTempOvrAmb | Not Set | 344 | 2 | InputRegister | 184 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7007 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Efficiency Index | C1-EI | Not Set | 344 | 2 | InputRegister | 185 | TRUE | 0 | 10 | 5 | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7008 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Capacity Index | C1-CI | Not Set | 344 | 2 | InputRegister | 186 | TRUE | 0 | 10 | 5 | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7009 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Evaporating Temp Value | C1-EvapTempValue | Not Set | 344 | 2 | InputRegister | 187 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7014 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Condenser Temperature Over Ambient High | C1-CondTempOAHigh | Not Set | 344 | 2 | InputRegister | 188 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7015 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Condenser Temperature Over Ambient Low | C1-CondTempOALow | Not Set | 344 | 2 | InputRegister | 189 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7016 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Superheat High | C1-SuperheatHigh | Not Set | 344 | 2 | InputRegister | 190 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7017 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Superheat Low | C1-SuperheatLow | Not Set | 344 | 2 | InputRegister | 191 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7018 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Subcool High | C1-SubcoolHigh | Not Set | 344 | 2 | InputRegister | 192 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7019 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Subcool Low | C1-SubcoolLow | Not Set | 344 | 2 | InputRegister | 193 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7020 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Evaporating Temperature High | C1-EvapTempHigh | Not Set | 344 | 2 | InputRegister | 194 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7021 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Evaporating Temperature Low | C1-EvapTempLow | Not Set | 344 | 2 | InputRegister | 195 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7022 | 6
York RTU.Cooling Control.DX Cooling Circuit 2 | Compressor Stage Command | C2 | Not Set | 344 | 2 | InputRegister | 319 | FALSE | 0 | 1 | 4 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7001 | 7
York RTU.Cooling Control.DX Cooling Circuit 2 | Compressor Stage Status | C2-S | Not Set | 344 | 2 | InputRegister | 320 | FALSE | 0 | 1 | 4 | 0 = Off-Idle 1 = On-Minimum On Time 2 = On-Normal Command 3 = Off-Cooling Is Disabled ... |  | FALSE | 9 |  | SE RTU DX Cooling Circuit 1 Status | 1741 | [5 empty] | SE RTU DX Cooling Circuit 1 Status | 1741 |  |  |  |  | 7002 | 7
York RTU.Cooling Control.DX Cooling Circuit 2 | Compressor Stage Enabled | C2-En | Not Set | 344 | 2 | HoldingRegister | 102 | FALSE | 0 | 1 | 4 | 0 = Yes 1 = No |  | TRUE | 9 |  | Yes/No | 1698 | [5 empty] | Yes/No | 1698 |  |  |  |  | 7003 | 7
York RTU.Cooling Control.DX Cooling Circuit 2 | Compressor Stage Accumulated Runtime | C2RunTim | Not Set | 344 | 2 | InputRegister | 34 | FALSE | 0 | 10 | 5 | 0 ... 10000 hours |  | TRUE | 4 | 1s | hours | 507:71 | 0 | 10000 |  |  | 1s | hours | 507:71 | 0 | 10000 |  |  | 7005 | 7
York RTU.Cooling Control.DX Cooling Circuit 2 | Min On Time Remaining | C2OnTmr | Not Set | 344 | 2 | InputRegister | 166 | FALSE | 0 | 1 | 4 | seconds |  | FALSE | 17 | 1s | seconds | 507:73 |  |  |  |  | 1s | seconds | 507:73 |  |  |  |  | 7007 | 7
York RTU.Cooling Control.DX Cooling Circuit 2 | Anti-Short Cycle Delay Time Remaining | C2ASCDTmr | Not Set | 344 | 2 | InputRegister | 167 | FALSE | 0 | 1 | 4 | seconds |  | FALSE | 17 | 1s | seconds | 507:73 |  |  |  |  | 1s | seconds | 507:73 |  |  |  |  | 7008 | 7
York RTU.Cooling Control.DX Cooling Circuit 2 | High Pressure Limit | HPS2 | Not Set | 344 | 2 | InputRegister | 321 | FALSE | 0 | 1 | 4 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7009 | 7
York RTU.Cooling Control.DX Cooling Circuit 2 | High Pressure Lockout | HPS2-LO | Not Set | 344 | 2 | InputRegister | 322 | FALSE | 0 | 1 | 4 | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7010 | 7
York RTU.Cooling Control.DX Cooling Circuit 2 | Low Pressure Limit | LPS2 | Not Set | 344 | 2 | InputRegister | 323 | FALSE | 0 | 1 | 4 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7011 | 7
York RTU.Cooling Control.DX Cooling Circuit 2 | Low Pressure Lockout | LPS2-LO | Not Set | 344 | 2 | InputRegister | 324 | FALSE | 0 | 1 | 4 | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7012 | 7
York RTU.Cooling Control.DX Cooling Circuit 2 | Freeze Condition | FS2 | Not Set | 344 | 2 | InputRegister | 325 | FALSE | 0 | 1 | 4 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7013 | 7
York RTU.Cooling Control.DX Cooling Circuit 2 | Freeze Condition Lockout | FS2-LO | Not Set | 344 | 2 | InputRegister | 326 | FALSE | 0 | 1 | 4 | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7014 | 7
York RTU.Cooling Control.DX Cooling Circuit 2 | Evaporator Coil Temp | EC2 | Not Set | 344 | 2 | InputRegister | 168 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7015 | 7
York RTU.Cooling Control.DX Cooling Circuit 2 | Condenser Coil Temp | CC2 | Not Set | 344 | 2 | InputRegister | 169 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7016 | 7
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Cooling Circuit Test Status | ClgCktTestS-2 | Not Set | 344 | 2 | InputRegister | 344 | FALSE | 0 | 1 | 4 | 0 = Unknown Status 1 = Basic Data Not Available Manual Entry 2 = Basic Data Not Available 3 = Return Wet Bulb Temp Not Available ... |  | FALSE | 9 |  | SE FDD Codes | 1694 | [5 empty] | SE FDD Codes | 1694 |  |  |  |  | 7000 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Suction Pressure | SLP-2 | Not Set | 344 | 2 | InputRegister | 196 | TRUE | 0 | 10 | 5 | psi (kPa) |  | FALSE | 4 | 10ths | psi | 507:56 |  |  |  |  | 1s | kPa | 507:54 |  |  |  |  | 7001 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Liquid Pressure | LLP-2 | Not Set | 344 | 2 | InputRegister | 197 | TRUE | 0 | 10 | 5 | psi (kPa) |  | FALSE | 4 | 10ths | psi | 507:56 |  |  |  |  | 1s | kPa | 507:54 |  |  |  |  | 7002 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Suction Temperature | SLT-2 | Not Set | 344 | 2 | InputRegister | 198 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7003 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Liquid Temperature | LLT-2 | Not Set | 344 | 2 | InputRegister | 199 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7004 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Superheat | C2-SuperHeat | Not Set | 344 | 2 | InputRegister | 200 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7005 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Subcooling | C2-SubCool | Not Set | 344 | 2 | InputRegister | 201 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7006 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Condensing Temperature over Ambient | C2-CondTempOvrAmb | Not Set | 344 | 2 | InputRegister | 202 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7007 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Efficiency Index | C2-EI | Not Set | 344 | 2 | InputRegister | 203 | TRUE | 0 | 10 | 5 | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7008 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Capacity Index | C2-CI | Not Set | 344 | 2 | InputRegister | 204 | TRUE | 0 | 10 | 5 | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7009 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Evaporating Temp Value | C2-EvapTempValue | Not Set | 344 | 2 | InputRegister | 205 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7014 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Condenser Temperature Over Ambient High | C2-CondTempOAHigh | Not Set | 344 | 2 | InputRegister | 206 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7015 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Condenser Temperature Over Ambient Low | C2-CondTempOALow | Not Set | 344 | 2 | InputRegister | 207 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7016 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Superheat High | C2-SuperheatHigh | Not Set | 344 | 2 | InputRegister | 208 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7017 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Superheat Low | C2-SuperheatLow | Not Set | 344 | 2 | InputRegister | 209 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7018 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Subcool High | C2-SubcoolHigh | Not Set | 344 | 2 | InputRegister | 210 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7019 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Subcool Low | C2-SubcoolLow | Not Set | 344 | 2 | InputRegister | 211 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7020 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Evaporating Temperature High | C2-EvapTempHigh | Not Set | 344 | 2 | InputRegister | 212 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7021 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Evaporating Temperature Low | C2-EvapTempLow | Not Set | 344 | 2 | InputRegister | 213 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7022 | 8
York RTU.Cooling Control.DX Cooling Circuit 3 | Compressor Stage Command | C3 | Not Set | 344 | 2 | InputRegister | 327 | FALSE | 0 | 1 | 4 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7001 | 9
York RTU.Cooling Control.DX Cooling Circuit 3 | Compressor Stage Status | C3-S | Not Set | 344 | 2 | InputRegister | 328 | FALSE | 0 | 1 | 4 | 0 = Off-Idle 1 = On-Minimum On Time 2 = On-Normal Command 3 = Off-Cooling Is Disabled ... |  | FALSE | 9 |  | SE RTU DX Cooling Circuit 1 Status | 1741 | [5 empty] | SE RTU DX Cooling Circuit 1 Status | 1741 |  |  |  |  | 7002 | 9
York RTU.Cooling Control.DX Cooling Circuit 3 | Compressor Stage Enabled | C3-En | Not Set | 344 | 2 | HoldingRegister | 103 | FALSE | 0 | 1 | 4 | 0 = Yes 1 = No |  | TRUE | 9 |  | Yes/No | 1698 | [5 empty] | Yes/No | 1698 |  |  |  |  | 7003 | 9
York RTU.Cooling Control.DX Cooling Circuit 3 | Compressor Stage Accumulated Runtime | C3RunTim | Not Set | 344 | 2 | InputRegister | 35 | FALSE | 0 | 10 | 5 | 0 ... 10000 hours |  | TRUE | 4 | 1s | hours | 507:71 | 0 | 10000 |  |  | 1s | hours | 507:71 | 0 | 10000 |  |  | 7005 | 9
York RTU.Cooling Control.DX Cooling Circuit 3 | Min On Time Remaining | C3OnTmr | Not Set | 344 | 2 | InputRegister | 170 | FALSE | 0 | 1 | 4 | seconds |  | FALSE | 17 | 1s | seconds | 507:73 |  |  |  |  | 1s | seconds | 507:73 |  |  |  |  | 7007 | 9
York RTU.Cooling Control.DX Cooling Circuit 3 | Anti-Short Cycle Delay Time Remaining | C3ASCDTmr | Not Set | 344 | 2 | InputRegister | 171 | FALSE | 0 | 1 | 4 | seconds |  | FALSE | 17 | 1s | seconds | 507:73 |  |  |  |  | 1s | seconds | 507:73 |  |  |  |  | 7008 | 9
York RTU.Cooling Control.DX Cooling Circuit 3 | High Pressure Limit | HPS3 | Not Set | 344 | 2 | InputRegister | 329 | FALSE | 0 | 1 | 4 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7009 | 9
York RTU.Cooling Control.DX Cooling Circuit 3 | High Pressure Lockout | HPS3-LO | Not Set | 344 | 2 | InputRegister | 330 | FALSE | 0 | 1 | 4 | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7010 | 9
York RTU.Cooling Control.DX Cooling Circuit 3 | Low Pressure Limit | LPS3 | Not Set | 344 | 2 | InputRegister | 331 | FALSE | 0 | 1 | 4 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7011 | 9
York RTU.Cooling Control.DX Cooling Circuit 3 | Low Pressure Lockout | LPS3-LO | Not Set | 344 | 2 | InputRegister | 332 | FALSE | 0 | 1 | 4 | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7012 | 9
York RTU.Cooling Control.DX Cooling Circuit 3 | Freeze Condition | FS3 | Not Set | 344 | 2 | InputRegister | 333 | FALSE | 0 | 1 | 4 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7013 | 9
York RTU.Cooling Control.DX Cooling Circuit 3 | Freeze Condition Lockout | FS3-LO | Not Set | 344 | 2 | InputRegister | 334 | FALSE | 0 | 1 | 4 | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7014 | 9
York RTU.Cooling Control.DX Cooling Circuit 3 | Evaporator Coil Temp | EC3 | Not Set | 344 | 2 | InputRegister | 172 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7015 | 9
York RTU.Cooling Control.DX Cooling Circuit 3 | Condenser Coil Temp | CC3 | Not Set | 344 | 2 | InputRegister | 173 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7016 | 9
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Cooling Circuit Test Status | ClgCktTestS-3 | Not Set | 344 | 2 | InputRegister | 345 | FALSE | 0 | 1 | 4 | 0 = Unknown Status 1 = Basic Data Not Available Manual Entry 2 = Basic Data Not Available 3 = Return Wet Bulb Temp Not Available ... |  | FALSE | 9 |  | SE FDD Codes | 1694 | [5 empty] | SE FDD Codes | 1694 |  |  |  |  | 7000 | 10
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Suction Pressure | SLP-3 | Not Set | 344 | 2 | InputRegister | 214 | TRUE | 0 | 10 | 5 | psi (kPa) |  | FALSE | 4 | 10ths | psi | 507:56 |  |  |  |  | 1s | kPa | 507:54 |  |  |  |  | 7001 | 10
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Liquid Pressure | LLP-3 | Not Set | 344 | 2 | InputRegister | 215 | TRUE | 0 | 10 | 5 | psi (kPa) |  | FALSE | 4 | 10ths | psi | 507:56 |  |  |  |  | 1s | kPa | 507:54 |  |  |  |  | 7002 | 10
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Suction Temperature | SLT-3 | Not Set | 344 | 2 | InputRegister | 216 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7003 | 10
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Liquid Temperature | LLT-3 | Not Set | 344 | 2 | InputRegister | 217 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7004 | 10
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Superheat | C3-SuperHeat | Not Set | 344 | 2 | InputRegister | 218 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7005 | 10
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Subcooling | C3-SubCool | Not Set | 344 | 2 | InputRegister | 219 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7006 | 10
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Condensing Temperature over Ambient | C3-CondTempOvrAmb | Not Set | 344 | 2 | InputRegister | 220 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7007 | 10
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Efficiency Index | C3-EI | Not Set | 344 | 2 | InputRegister | 221 | TRUE | 0 | 10 | 5 | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7008 | 10
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Capacity Index | C3-CI | Not Set | 344 | 2 | InputRegister | 222 | TRUE | 0 | 10 | 5 | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7009 | 10
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Evaporating Temp Value | C3-EvapTempValue | Not Set | 344 | 2 | InputRegister | 223 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7014 | 10
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Condenser Temperature Over Ambient High | C3-CondTempOAHigh | Not Set | 344 | 2 | InputRegister | 224 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7015 | 10
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Condenser Temperature Over Ambient Low | C3-CondTempOALow | Not Set | 344 | 2 | InputRegister | 225 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7016 | 10
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Superheat High | C3-SuperheatHigh | Not Set | 344 | 2 | InputRegister | 226 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7017 | 10
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Superheat Low | C3-SuperheatLow | Not Set | 344 | 2 | InputRegister | 227 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7018 | 10
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Subcool High | C3-SubcoolHigh | Not Set | 344 | 2 | InputRegister | 228 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7019 | 10
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Subcool Low | C3-SubcoolLow | Not Set | 344 | 2 | InputRegister | 229 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7020 | 10
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Evaporating Temperature High | C3-EvapTempHigh | Not Set | 344 | 2 | InputRegister | 230 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7021 | 10
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Evaporating Temperature Low | C3-EvapTempLow | Not Set | 344 | 2 | InputRegister | 231 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7022 | 10
York RTU.Cooling Control.DX Cooling Circuit 4 | Compressor Stage Command | C4 | Not Set | 344 | 2 | InputRegister | 335 | FALSE | 0 | 1 | 4 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7001 | 11
York RTU.Cooling Control.DX Cooling Circuit 4 | Compressor Stage Status | C4-S | Not Set | 344 | 2 | InputRegister | 336 | FALSE | 0 | 1 | 4 | 0 = Off-Idle 1 = On-Minimum On Time 2 = On-Normal Command 3 = Off-Cooling Is Disabled ... |  | FALSE | 9 |  | SE RTU DX Cooling Circuit 1 Status | 1741 | [5 empty] | SE RTU DX Cooling Circuit 1 Status | 1741 |  |  |  |  | 7002 | 11
York RTU.Cooling Control.DX Cooling Circuit 4 | Compressor Stage Enabled | C4-En | Not Set | 344 | 2 | HoldingRegister | 104 | FALSE | 0 | 1 | 4 | 0 = Yes 1 = No |  | TRUE | 9 |  | Yes/No | 1698 | [5 empty] | Yes/No | 1698 |  |  |  |  | 7003 | 11
York RTU.Cooling Control.DX Cooling Circuit 4 | Compressor Stage Accumulated Runtime | C4RunTim | Not Set | 344 | 2 | InputRegister | 36 | FALSE | 0 | 10 | 5 | 0 ... 10000 hours |  | TRUE | 4 | 1s | hours | 507:71 | 0 | 10000 |  |  | 1s | hours | 507:71 | 0 | 10000 |  |  | 7005 | 11
York RTU.Cooling Control.DX Cooling Circuit 4 | Min On Time Remaining | C4OnTmr | Not Set | 344 | 2 | InputRegister | 174 | FALSE | 0 | 1 | 4 | seconds |  | FALSE | 17 | 1s | seconds | 507:73 |  |  |  |  | 1s | seconds | 507:73 |  |  |  |  | 7007 | 11
York RTU.Cooling Control.DX Cooling Circuit 4 | Anti-Short Cycle Delay Time Remaining | C4ASCDTmr | Not Set | 344 | 2 | InputRegister | 175 | FALSE | 0 | 1 | 4 | seconds |  | FALSE | 17 | 1s | seconds | 507:73 |  |  |  |  | 1s | seconds | 507:73 |  |  |  |  | 7008 | 11
York RTU.Cooling Control.DX Cooling Circuit 4 | High Pressure Limit | HPS4 | Not Set | 344 | 2 | InputRegister | 337 | FALSE | 0 | 1 | 4 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7009 | 11
York RTU.Cooling Control.DX Cooling Circuit 4 | High Pressure Lockout | HPS4-LO | Not Set | 344 | 2 | InputRegister | 338 | FALSE | 0 | 1 | 4 | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7010 | 11
York RTU.Cooling Control.DX Cooling Circuit 4 | Low Pressure Limit | LPS4 | Not Set | 344 | 2 | InputRegister | 339 | FALSE | 0 | 1 | 4 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7011 | 11
York RTU.Cooling Control.DX Cooling Circuit 4 | Low Pressure Lockout | LPS4-LO | Not Set | 344 | 2 | InputRegister | 340 | FALSE | 0 | 1 | 4 | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7012 | 11
York RTU.Cooling Control.DX Cooling Circuit 4 | Freeze Condition | FS4 | Not Set | 344 | 2 | InputRegister | 341 | FALSE | 0 | 1 | 4 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7013 | 11
York RTU.Cooling Control.DX Cooling Circuit 4 | Freeze Condition Lockout | FS4-LO | Not Set | 344 | 2 | InputRegister | 342 | FALSE | 0 | 1 | 4 | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7014 | 11
York RTU.Cooling Control.DX Cooling Circuit 4 | Evaporator Coil Temp | EC4 | Not Set | 344 | 2 | InputRegister | 176 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7015 | 11
York RTU.Cooling Control.DX Cooling Circuit 4 | Condenser Coil Temp | CC4 | Not Set | 344 | 2 | InputRegister | 177 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7016 | 11
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Cooling Circuit Test Status | ClgCktTestS-4 | Not Set | 344 | 2 | InputRegister | 346 | FALSE | 0 | 1 | 4 | 0 = Unknown Status 1 = Basic Data Not Available Manual Entry 2 = Basic Data Not Available 3 = Return Wet Bulb Temp Not Available ... |  | FALSE | 9 |  | SE FDD Codes | 1694 | [5 empty] | SE FDD Codes | 1694 |  |  |  |  | 7000 | 12
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Suction Pressure | SLP-4 | Not Set | 344 | 2 | InputRegister | 232 | TRUE | 0 | 10 | 5 | psi (kPa) |  | FALSE | 4 | 10ths | psi | 507:56 |  |  |  |  | 1s | kPa | 507:54 |  |  |  |  | 7001 | 12
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Liquid Pressure | LLP-4 | Not Set | 344 | 2 | InputRegister | 233 | TRUE | 0 | 10 | 5 | psi (kPa) |  | FALSE | 4 | 10ths | psi | 507:56 |  |  |  |  | 1s | kPa | 507:54 |  |  |  |  | 7002 | 12
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Suction Temperature | SLT-4 | Not Set | 344 | 2 | InputRegister | 234 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7003 | 12
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Liquid Temperature | LLT-4 | Not Set | 344 | 2 | InputRegister | 235 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7004 | 12
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Superheat | C4-SuperHeat | Not Set | 344 | 2 | InputRegister | 236 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7005 | 12
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Subcooling | C4-SubCool | Not Set | 344 | 2 | InputRegister | 237 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7006 | 12
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Condensing Temperature over Ambient | C4-CondTempOvrAmb | Not Set | 344 | 2 | InputRegister | 238 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7007 | 12
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Efficiency Index | C4-EI | Not Set | 344 | 2 | InputRegister | 239 | TRUE | 0 | 10 | 5 | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7008 | 12
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Capacity Index | C4-CI | Not Set | 344 | 2 | InputRegister | 240 | TRUE | 0 | 10 | 5 | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7009 | 12
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Evaporating Temp Value | C4-EvapTempValue | Not Set | 344 | 2 | InputRegister | 241 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7014 | 12
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Condenser Temperature Over Ambient High | C4-CondTempOAHigh | Not Set | 344 | 2 | InputRegister | 242 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7015 | 12
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Condenser Temperature Over Ambient Low | C4-CondTempOALow | Not Set | 344 | 2 | InputRegister | 243 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7016 | 12
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Superheat High | C4-SuperheatHigh | Not Set | 344 | 2 | InputRegister | 244 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7017 | 12
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Superheat Low | C4-SuperheatLow | Not Set | 344 | 2 | InputRegister | 245 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7018 | 12
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Subcool High | C4-SubcoolHigh | Not Set | 344 | 2 | InputRegister | 246 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7019 | 12
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Subcool Low | C4-SubcoolLow | Not Set | 344 | 2 | InputRegister | 247 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7020 | 12
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Evaporating Temperature High | C4-EvapTempHigh | Not Set | 344 | 2 | InputRegister | 248 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7021 | 12
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Evaporating Temperature Low | C4-EvapTempLow | Not Set | 344 | 2 | InputRegister | 249 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7022 | 12
York RTU.Heating Control | Heating Mode Enabled For Operation | Htg-En | Not Set | 344 | 2 | HoldingRegister | 105 | FALSE | 0 | 1 | 4 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7000 | 13
York RTU.Heating Control | Heating Status | Htg-S | Not Set | 344 | 2 | InputRegister | 347 | FALSE | 0 | 1 | 4 | 0 = Off-Idle 1 = On-Defrost 2 = SAT Tempering 3 = Morning Warmup ... |  | FALSE | 9 |  | SE RTU Heating Control Status | 1742 | [5 empty] | SE RTU Heating Control Status | 1742 |  |  |  |  | 7001 | 13
York RTU.Heating Control | SAT Air Temp Limit for Heating Enabled | SATHtgLimit-En | Not Set | 344 | 2 | HoldingRegister | 106 | FALSE | 0 | 1 | 4 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7002 | 13
York RTU.Heating Control | SAT Air Temp Limit For Heating Setpoint | SATHtgLimit-Sp | Not Set | 344 | 2 | HoldingRegister | 37 | TRUE | 0 | 10 | 5 | 100 ... 180 deg F (38 ... 82 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 100 | 180 |  |  | 1s | deg C | 507:62 | 38 | 82 |  |  | 7003 | 13
York RTU.Heating Control | Outdoor Air Temp Heating Cutout Setpoint | HtgOATCutout-Sp | Not Set | 344 | 2 | HoldingRegister | 38 | TRUE | 0 | 10 | 5 | 0 ... 100 deg F (-18 ... 38 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 0 | 100 |  |  | 1s | deg C | 507:62 | -18 | 38 |  |  | 7004 | 13
York RTU.Heating Control | Hot Water Freeze Stat | FSHW | Not Set | 344 | 2 | InputRegister | 348 | FALSE | 0 | 1 | 4 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7005 | 13
York RTU.Heating Control | Gas Valve1 Input | MV | Not Set | 344 | 2 | InputRegister | 349 | FALSE | 0 | 1 | 4 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7006 | 13
York RTU.Heating Control | Gas Valve2 Input | GV2 | Not Set | 344 | 2 | InputRegister | 350 | FALSE | 0 | 1 | 4 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7007 | 13
York RTU.Heating Control | Gas Valve3 Input | GV3 | Not Set | 344 | 2 | InputRegister | 351 | FALSE | 0 | 1 | 4 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7008 | 13
York RTU.Heating Control | Heat Limit1 Switch | Limit | Not Set | 344 | 2 | InputRegister | 352 | FALSE | 0 | 1 | 4 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7009 | 13
York RTU.Heating Control | Heat Limit1 Switch Lockout | LimitLO | Not Set | 344 | 2 | InputRegister | 353 | FALSE | 0 | 1 | 4 | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7010 | 13
York RTU.Heating Control | Heat Limit2 Switch | Lim2 | Not Set | 344 | 2 | InputRegister | 354 | FALSE | 0 | 1 | 4 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7011 | 13
York RTU.Heating Control | Heat Limit2 Switch Lockout | Lim2LO | Not Set | 344 | 2 | InputRegister | 355 | FALSE | 0 | 1 | 4 | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7012 | 13
York RTU.Heating Control | Heat Limit3 Switch | Lim3 | Not Set | 344 | 2 | InputRegister | 356 | FALSE | 0 | 1 | 4 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7013 | 13
York RTU.Heating Control | Heat Limit3 Switch Lockout | Lim3LO | Not Set | 344 | 2 | InputRegister | 357 | FALSE | 0 | 1 | 4 | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7014 | 13
York RTU.Heating Control | VAV Occupied Heating Enabled | HtgOcc-En | Not Set | 344 | 2 | HoldingRegister | 107 | FALSE | 0 | 1 | 4 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7015 | 13
York RTU.Heating Control | VAV Occupied Heating Setpoint | VAVHtgOcc-SP | Not Set | 344 | 2 | HoldingRegister | 39 | TRUE | 0 | 10 | 5 | 40 ... 85 deg F (4 ... 30 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 40 | 85 |  |  | 1s | deg C | 507:62 | 4 | 30 |  |  | 7016 | 13
York RTU.Heating Control | Unoccupied Heating Enabled | HtgUnocc-En | Not Set | 344 | 2 | HoldingRegister | 108 | FALSE | 0 | 1 | 4 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7017 | 13
York RTU.Heating Control | VAV Unoccupied Heating Setpoint | VAVHtgUnocc-Sp | Not Set | 344 | 2 | HoldingRegister | 40 | TRUE | 0 | 10 | 5 | 45 ... 98 deg F (7 ... 36 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 45 | 98 |  |  | 1s | deg C | 507:62 | 7 | 36 |  |  | 7018 | 13
York RTU.Heating Control | VAV Operating Heating Setpoint | VAVOprHtg-Sp | Not Set | 344 | 2 | InputRegister | 250 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 100ths | deg F | 507:64 |  |  |  |  | 100ths | deg C | 507:62 |  |  |  |  | 7019 | 13
York RTU.Heating Control | Morning Warmup Enabled | MornW-En | Not Set | 344 | 2 | HoldingRegister | 109 | FALSE | 0 | 1 | 4 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7020 | 13
York RTU.Heating Control | Morning Warmup/Return Air Temp Setpoint | MornWRAT-Sp | Not Set | 344 | 2 | HoldingRegister | 41 | TRUE | 0 | 10 | 5 | 50 ... 85 deg F (10 ... 30 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 50 | 85 |  |  | 1s | deg C | 507:62 | 10 | 30 |  |  | 7021 | 13
York RTU.Heating Control | VAV Box Heat Command | VAV Box | Not Set | 344 | 2 | InputRegister | 358 | FALSE | 0 | 1 | 4 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7022 | 13
York RTU.Heating Control | CV Occupied Heating Setpoint | CVHtgOcc-SP | Not Set | 344 | 2 | HoldingRegister | 42 | TRUE | 0 | 10 | 5 | 46 ... 99 deg F (8 ... 37 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 46 | 99 |  |  | 1s | deg C | 507:62 | 8 | 37 |  |  | 7023 | 13
York RTU.Heating Control | CV Unoccupied Heating Setpoint | CVHtgUnocc-Sp | Not Set | 344 | 2 | HoldingRegister | 43 | TRUE | 0 | 10 | 5 | 45 ... 98 deg F (7 ... 36 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 45 | 98 |  |  | 1s | deg C | 507:62 | 7 | 36 |  |  | 7024 | 13
York RTU.Heating Control | CV Operating Heating Setpoint | CVOprHtg-Sp | Not Set | 344 | 2 | InputRegister | 251 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 100ths | deg F | 507:64 |  |  |  |  | 100ths | deg C | 507:62 |  |  |  |  | 7025 | 13
York RTU.Heating Control | Morning Cooldown Enabled | MornC-En | Not Set | 344 | 2 | HoldingRegister | 110 | FALSE | 0 | 1 | 4 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7034 | 13
York RTU.Heating Control | Morning Cooldown/Return Air Temp Setpoint | MornCRAT-Sp | Not Set | 344 | 2 | HoldingRegister | 44 | TRUE | 0 | 10 | 5 | 50 ... 85 deg F (10 ... 30 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 50 | 85 |  |  | 1s | deg C | 507:62 | 10 | 30 |  |  | 7035 | 13
York RTU.Heating Control | Optimal Start Enabled | OptStrt-En | Not Set | 344 | 2 | HoldingRegister | 111 | FALSE | 0 | 1 | 4 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7036 | 13
York RTU.Heating Control | Occupancy BI Enabled | OccBI-En | Not Set | 344 | 2 | HoldingRegister | 112 | FALSE | 0 | 1 | 4 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7037 | 13
York RTU.Heating Control | Early Start Period | EarlyStrtPeriod | Not Set | 344 | 2 | HoldingRegister | 45 | FALSE | 0 | 10 | 5 | 0 ... 120 minutes |  | TRUE | 4 | 1s | minutes | 507:72 | 0 | 120 |  |  | 1s | minutes | 507:72 | 0 | 120 |  |  | 7038 | 13
York RTU.Heating Control | Heating Adaptive Tuning Enable | HtgAdapTunEn | Not Set | 344 | 2 | HoldingRegister | 114 | FALSE | 0 | 1 | 4 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7041 | 13
York RTU.Heating Control | DAT Max Heating SP | DATMaxHtgSP | Not Set | 344 | 2 | InputRegister | 75 | TRUE | 0 | 10 | 5 | 80 ... 110 deg F (26.6 ... 43.4 deg C) |  | TRUE | 4 | 10ths | deg F | 507:64 | 80 | 110 |  |  | 10ths | deg C | 507:62 | 26.6 | 43.4 |  |  | 7043 | 13
York RTU.Heating Control | DAT Satisfied SP | DATSatSP | Not Set | 344 | 2 | InputRegister | 76 | TRUE | 0 | 10 | 5 | 65 ... 75 deg F (18.3 ... 23.9 deg C) |  | TRUE | 4 | 10ths | deg F | 507:64 | 65 | 75 |  |  | 10ths | deg C | 507:62 | 18.3 | 23.9 |  |  | 7044 | 13
York RTU.Heating Control | Staged Heating Command | StgHtgCmd | Not Set | 344 | 2 | InputRegister | 264 | TRUE | 0 | 10 | 5 | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7045 | 13
York RTU.Heating Control.Staged Heat Control | Number of Heating Stages Installed | #HtgStgs | Not Set | 344 | 2 | HoldingRegister | 430 | FALSE | 0 | 1 | 4 | 0 ... 3 |  | TRUE | 16 | 1s |  | 507:95 | 0 | 3 |  |  | 1s |  | 507:95 | 0 | 3 |  |  | 7000 | 14
York RTU.Heating Control.Staged Heat Control.Heating Stage 1 | Heat Stage Command | H1 | Not Set | 344 | 2 | InputRegister | 359 | FALSE | 0 | 1 | 4 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7000 | 15
York RTU.Heating Control.Staged Heat Control.Heating Stage 1 | Heat Stage Status | H1-S | Not Set | 344 | 2 | InputRegister | 360 | FALSE | 0 | 1 | 4 | 0 = Off-Idle 1 = On-Minimum Runtime Timer 2 = On-Normal Command 3 = Off-Heating Is Disabled ... |  | FALSE | 9 |  | SE RTU Heating Stage 1 Status | 1743 | [5 empty] | SE RTU Heating Stage 1 Status | 1743 |  |  |  |  | 7001 | 15
York RTU.Heating Control.Staged Heat Control.Heating Stage 1 | Heat Stage Accumulated Runtime | H1RunTim | Not Set | 344 | 2 | InputRegister | 48 | FALSE | 0 | 10 | 5 | 0 ... 10000 hours |  | TRUE | 4 | 1s | hours | 507:71 | 0 | 10000 |  |  | 1s | hours | 507:71 | 0 | 10000 |  |  | 7006 | 15
York RTU.Heating Control.Staged Heat Control.Heating Stage 2 | Heat Stage Command | H2 | Not Set | 344 | 2 | InputRegister | 361 | FALSE | 0 | 1 | 4 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7000 | 16
York RTU.Heating Control.Staged Heat Control.Heating Stage 2 | Heat Stage Status | H2-S | Not Set | 344 | 2 | InputRegister | 362 | FALSE | 0 | 1 | 4 | 0 = Off-Idle 1 = On-Minimum Runtime Timer 2 = On-Normal Command 3 = Off-Heating Is Disabled ... |  | FALSE | 9 |  | SE RTU Heating Stage 1 Status | 1743 | [5 empty] | SE RTU Heating Stage 1 Status | 1743 |  |  |  |  | 7001 | 16
York RTU.Heating Control.Staged Heat Control.Heating Stage 2 | Heat Stage Accumulated Runtime | H2RunTim | Not Set | 344 | 2 | InputRegister | 49 | FALSE | 0 | 10 | 5 | 0 ... 10000 hours |  | TRUE | 4 | 1s | hours | 507:71 | 0 | 10000 |  |  | 1s | hours | 507:71 | 0 | 10000 |  |  | 7006 | 16
York RTU.Heating Control.Staged Heat Control.Heating Stage 3 | Heat Stage Command | H3 | Not Set | 344 | 2 | InputRegister | 363 | FALSE | 0 | 1 | 4 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7000 | 17
York RTU.Heating Control.Staged Heat Control.Heating Stage 3 | Heat Stage Status | H3-S | Not Set | 344 | 2 | InputRegister | 364 | FALSE | 0 | 1 | 4 | 0 = Off-Idle 1 = On-Minimum Runtime Timer 2 = On-Normal Command 3 = Off-Heating Is Disabled ... |  | FALSE | 9 |  | SE RTU Heating Stage 1 Status | 1743 | [5 empty] | SE RTU Heating Stage 1 Status | 1743 |  |  |  |  | 7001 | 17
York RTU.Heating Control.Staged Heat Control.Heating Stage 3 | Heat Stage Accumulated Runtime | H3RunTim | Not Set | 344 | 2 | InputRegister | 50 | FALSE | 0 | 10 | 5 | 0 ... 10000 hours |  | TRUE | 4 | 1s | hours | 507:71 | 0 | 10000 |  |  | 1s | hours | 507:71 | 0 | 10000 |  |  | 7006 | 17
York RTU.Heating Control.Hydronic Heat Control | Hydronic Heat Valve % Command | HWV | Not Set | 344 | 2 | InputRegister | 252 | TRUE | 0 | 10 | 5 | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7000 | 18
York RTU.Heating Control.Hydronic Heat Control | Hydronic Heat Valve Reverse Acting | HydReverse | Not Set | 344 | 2 | HoldingRegister | 115 | FALSE | 0 | 1 | 4 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7001 | 18
York RTU.Heating Control.Hydronic Heat Control | Hydronic Heating Stage #1 Supply Air Setpoint | HydH1SA-Sp | Not Set | 344 | 2 | HoldingRegister | 51 | TRUE | 0 | 10 | 5 | 80 ... 180 deg F (27 ... 82 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 80 | 180 |  |  | 1s | deg C | 507:62 | 27 | 82 |  |  | 7002 | 18
York RTU.Heating Control.Hydronic Heat Control | Hydronic Heating Stage #2 Supply Air Setpoint | HydH2SA-Sp | Not Set | 344 | 2 | HoldingRegister | 52 | TRUE | 0 | 10 | 5 | 80 ... 180 deg F (27 ... 82 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 80 | 180 |  |  | 1s | deg C | 507:62 | 27 | 82 |  |  | 7003 | 18
York RTU.Heating Control.Hydronic Heat Control | Hydronic Heat SAT Tempering Enabled | SATTempHydHt-En | Not Set | 344 | 2 | HoldingRegister | 116 | FALSE | 0 | 1 | 4 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7004 | 18
York RTU.Heating Control.Hydronic Heat Control | Hydronic Heat SAT Tempering Setpoint | SATTempHydHt-Sp | Not Set | 344 | 2 | HoldingRegister | 53 | TRUE | 0 | 10 | 5 | 40 ... 60 deg F (4 ... 15 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 40 | 60 |  |  | 1s | deg C | 507:62 | 4 | 15 |  |  | 7005 | 18
York RTU.Economizer | Economizer Enabled For Operation | Econ-En | Not Set | 344 | 2 | HoldingRegister | 118 | FALSE | 0 | 1 | 4 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7000 | 19
York RTU.Economizer | Economizer Damper % Command | Economizer | Not Set | 344 | 2 | InputRegister | 253 | TRUE | 0 | 10 | 5 | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7001 | 19
York RTU.Economizer | Econ Free Cooling Available | Econ-Free | Not Set | 344 | 2 | InputRegister | 369 | FALSE | 0 | 1 | 4 | 0 = No 1 = Yes |  | FALSE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7002 | 19
York RTU.Economizer | Economizer Status | Econ-S | Not Set | 344 | 2 | InputRegister | 370 | FALSE | 0 | 1 | 4 | 0 = Disabled 1 = Damper Not Functional 2 = Purge 3 = Unavailable-Sensor Fault ... |  | FALSE | 9 |  | SE RTU Economizer Status | 1738 | [5 empty] | SE RTU Economizer Status | 1738 |  |  |  |  | 7003 | 19
York RTU.Economizer | Free Cooling Current Mode | FreeClg-Mode | Not Set | 344 | 2 | InputRegister | 371 | FALSE | 0 | 1 | 4 | 0 = Dry Bulb Temperature 1 = Differential Dry Bulb 2 = Single Enthalpy 3 = Dual Enthalpy 4 = Unreliable |  | FALSE | 9 |  | Actual Economizer Type Advanced | 3338 | [5 empty] | Actual Economizer Type Advanced | 3338 |  |  |  |  | 7004 | 19
York RTU.Economizer | Free Cooling Selection | FreeClg-Sel | Not Set | 344 | 2 | HoldingRegister | 119 | FALSE | 0 | 1 | 4 | 0 = Dry Bulb Temperature 1 = Single Enthalpy 2 = Dual Enthalpy 3 = Auto 4 = Differential Dry Bulb |  | TRUE | 9 |  | SE RTU Economizer Type | 3398 | [5 empty] | SE RTU Economizer Type | 3398 |  |  |  |  | 7005 | 19
York RTU.Economizer | Economizer Outdoor Air Temp Enable Setpoint | EconOAT-SpEn | Not Set | 344 | 2 | HoldingRegister | 55 | TRUE | 0 | 10 | 5 | 0 ... 80 deg F (-17.8 ... 27 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 0 | 80 |  |  | 1s | deg C | 507:62 | -17.8 | 27 |  |  | 7006 | 19
York RTU.Economizer | Economizer Outdoor Air Enthalpy Setpoint | EconOAEnth-Sp | Not Set | 344 | 2 | HoldingRegister | 56 | TRUE | 0 | 10 | 5 | 10 ... 50 Btu/lb dry air (23 ... 116 kJ/kg) |  | TRUE | 4 | 1s | Btu/lb dry air | 507:24 | 10 | 50 |  |  | 1s | kJ/kg | 507:125 | 23 | 116 |  |  | 7007 | 19
York RTU.Economizer | Low Ambient Economizer Setpoint | LowAmb-Sp | Not Set | 344 | 2 | HoldingRegister | 57 | TRUE | 0 | 10 | 5 | -20 ... 60 deg F (-29 ... 15 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | -20 | 60 |  |  | 1s | deg C | 507:62 | -29 | 15 |  |  | 7008 | 19
York RTU.Economizer | Low Ambient Economizer Minimum Position | LowAmb-MinPos | Not Set | 344 | 2 | HoldingRegister | 58 | TRUE | 0 | 10 | 5 | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7009 | 19
York RTU.Economizer | Economizer Damper Position | EconDampPos | Not Set | 344 | 2 | InputRegister | 254 | TRUE | 0 | 10 | 5 | % open |  | FALSE | 4 | 1s | % open | 507:264 |  |  |  |  | 1s | % open | 507:264 |  |  |  |  | 7011 | 19
York RTU.Economizer | Mixed Air Temperature | MAT | Not Set | 344 | 2 | InputRegister | 255 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7012 | 19
York RTU.Economizer | Supply Air Humidity | SAH | Not Set | 344 | 2 | InputRegister | 256 | TRUE | 0 | 10 | 5 | %RH |  | FALSE | 4 | 1s | %RH | 507:29 |  |  |  |  | 1s | %RH | 507:29 |  |  |  |  | 7014 | 19
York RTU.Economizer | Return Air Enthalpy | RA-Enth | Not Set | 344 | 2 | InputRegister | 257 | TRUE | 0 | 10 | 5 | Btu/lb (kJ/kg) |  | FALSE | 4 | 1s | Btu/lb | 507:117 |  |  |  |  | 1s | kJ/kg | 507:125 |  |  |  |  | 7015 | 19
York RTU.Economizer | Economizer Minimum Position Setpoint | Econ-MinPos | Not Set | 344 | 2 | HoldingRegister | 77 | TRUE | 0 | 10 | 5 | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7017 | 19
York RTU.Economizer | Excess Outdoor Air | ExcessOutAirFlt | Not Set | 344 | 2 | InputRegister | 372 | FALSE | 0 | 1 | 4 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7018 | 19
York RTU.Economizer | Not Economizing When Should | NotEconFlt | Not Set | 344 | 2 | InputRegister | 373 | FALSE | 0 | 1 | 4 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7019 | 19
York RTU.Economizer | Damper Not Modulating | EconDampFlt | Not Set | 344 | 2 | InputRegister | 374 | FALSE | 0 | 1 | 4 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7020 | 19
York RTU.Economizer | Economizing When Should Not | EconWhenShouldNotFlt | Not Set | 344 | 2 | InputRegister | 375 | FALSE | 0 | 1 | 4 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7021 | 19
York RTU.Economizer | Economizer Damper Minimum Position Low Speed Fan | LowSpeedFan-MinPos | Not Set | 344 | 2 | HoldingRegister | 54 | TRUE | 0 | 10 | 5 | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7025 | 19
York RTU.Economizer | EconMech Setup | EconMechStp | Not Set | 344 | 2 | HoldingRegister | 409 | FALSE | 0 | 1 | 4 | 0 = Option A 1 = Option B |  | TRUE | 9 |  | SE RTU EconMech Setup | 1752 | [5 empty] | SE RTU EconMech Setup | 1752 |  |  |  |  | 7027 | 19
York RTU.Economizer | Economizer Fault Detection Enable | EconFltDetectEn | Not Set | 344 | 2 | HoldingRegister | 132 | FALSE | 0 | 1 | 4 | 0 = Disable 1 = Enable |  | TRUE | 9 |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 |  |  |  |  | 7028 | 19
York RTU.Economizer | FDD Economizer Alarm Delay | EconAlrmDly | Not Set | 344 | 2 | HoldingRegister | 431 | FALSE | 0 | 1 | 4 | 0 ... 3600 seconds |  | TRUE | 4 | 10s | seconds | 507:73 | 0 | 3600 |  |  | 10s | seconds | 507:73 | 0 | 3600 |  |  | 7029 | 19
York RTU.Economizer | FDD Economizer Damper Allowed Error | EconPosErr | Not Set | 344 | 2 | HoldingRegister | 432 | FALSE | 0 | 1 | 4 | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7030 | 19
York RTU.Economizer | FDD Damper Min Position Tolerance | EconMinErr | Not Set | 344 | 2 | HoldingRegister | 433 | FALSE | 0 | 1 | 4 | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7031 | 19
York RTU.Hot Gas Reheat | Hot Gas Reheat Enabled For Operation | HGR-En | Not Set | 344 | 2 | HoldingRegister | 123 | FALSE | 0 | 1 | 4 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7000 | 20
York RTU.Hot Gas Reheat | Hot Gas Reheat Command | HGR | Not Set | 344 | 2 | InputRegister | 379 | FALSE | 0 | 1 | 4 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7001 | 20
York RTU.Hot Gas Reheat | Hot Gas Reheat Status | HGR-S | Not Set | 344 | 2 | InputRegister | 380 | FALSE | 0 | 1 | 4 | 0 = Off-Idle 1 = On-Normal Command 2 = On-Alternate Operation Command 3 = Off-Disabled |  | FALSE | 9 |  | SE RTU Hot Gas Reheat | 1744 | [5 empty] | SE RTU Hot Gas Reheat | 1744 |  |  |  |  | 7002 | 20
York RTU.Hot Gas Reheat | Hot Gas Reheat Humidity Setpoint | HGRHum-Sp | Not Set | 344 | 2 | HoldingRegister | 68 | TRUE | 0 | 10 | 5 | 0 ... 100 %RH |  | TRUE | 4 | 1s | %RH | 507:29 | 0 | 100 |  |  | 1s | %RH | 507:29 | 0 | 100 |  |  | 7003 | 20
York RTU.Hot Gas Reheat | Hot Gas Reheat Alternate Operation Enabled | HGRAlt-En | Not Set | 344 | 2 | HoldingRegister | 124 | FALSE | 0 | 1 | 4 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7004 | 20
York RTU.Hot Gas Reheat | Hot Gas Reheat Alternate Operation Writeable | HGRAltWrite | Not Set | 344 | 2 | HoldingRegister | 410 | FALSE | 0 | 1 | 4 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7005 | 20
York RTU.Hot Gas Reheat | HGR Unoccupied Humidity Setpoint | HGRUnoccHum-SP | Not Set | 344 | 2 | HoldingRegister | 78 | TRUE | 0 | 10 | 5 | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7006 | 20
York RTU.Hot Gas Reheat | HGR Enabled for Unoccupied Operation | HGRUnocc-En | Not Set | 344 | 2 | HoldingRegister | 133 | FALSE | 0 | 1 | 4 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7007 | 20
York RTU.Exhaust Fan Control | Exhaust Fan Command | ExFan | Not Set | 344 | 2 | InputRegister | 376 | FALSE | 0 | 1 | 4 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7001 | 21
York RTU.Exhaust Fan Control | Exhaust Fan VFD % Command | ExFanVFD | Not Set | 344 | 2 | InputRegister | 258 | TRUE | 0 | 10 | 5 | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7002 | 21
York RTU.Exhaust Fan Control | Exhaust Fan Status | ExF-S | Not Set | 344 | 2 | InputRegister | 377 | FALSE | 0 | 1 | 4 | 0 = Off-Idle 1 = On-Normal Command 2 = Off-Disabled 3 = Off-VFD Fault ... |  | FALSE | 9 |  | SE RTU Exhaust Fan | 1745 | [5 empty] | SE RTU Exhaust Fan | 1745 |  |  |  |  | 7003 | 21
York RTU.Exhaust Fan Control | Exhaust Fan VFD Fault | ExFanVFDFlt | Not Set | 344 | 2 | InputRegister | 378 | FALSE | 0 | 1 | 4 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7004 | 21
York RTU.Exhaust Fan Control | Exhaust Fan Accumulated Runtime | ExF-RunTim | Not Set | 344 | 2 | InputRegister | 259 | FALSE | 0 | 10 | 5 | hours |  | FALSE | 4 | 1s | hours | 507:71 |  |  |  |  | 1s | hours | 507:71 |  |  |  |  | 7005 | 21
York RTU.Exhaust Fan Control | Building Pressure Setpoint | Bldg-Sp | Not Set | 344 | 2 | HoldingRegister | 63 | TRUE | 0 | 1000 | 7 | -0.25 ... 0.25 in wc (-0.07 ... 0.07 kPa) |  | TRUE | 4 | 1000ths | in wc | 507:58 | -0.25 | 0.25 |  |  | 1000ths | kPa | 507:54 | -0.07 | 0.07 |  |  | 7006 | 21
York RTU.Exhaust Fan Control | Building Static Pressure | BldgPres | Not Set | 344 | 2 | InputRegister | 260 | TRUE | 0 | 1000 | 7 | in wc (kPa) |  | FALSE | 4 | 1000ths | in wc | 507:58 |  |  |  |  | 1000ths | kPa | 507:54 |  |  |  |  | 7007 | 21
York RTU.Exhaust Fan Control | Exhaust Damper % Command | EAD-O | Not Set | 344 | 2 | InputRegister | 261 | TRUE | 0 | 10 | 5 | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7008 | 21
York RTU.Exhaust Fan Control | Exhaust Damper Position for Exhaust Fan to Turn On | ExDmpPosFanOn | Not Set | 344 | 2 | HoldingRegister | 64 | TRUE | 0 | 10 | 5 | 20 ... 99 % |  | TRUE | 4 | 1s | % | 507:98 | 20 | 99 |  |  | 1s | % | 507:98 | 20 | 99 |  |  | 7009 | 21
York RTU.Exhaust Fan Control | Exhaust Damper Position for Exhaust Fan to Turn Off | ExDmpPosFanOff | Not Set | 344 | 2 | HoldingRegister | 65 | TRUE | 0 | 10 | 5 | 10 ... 89 % |  | TRUE | 4 | 1s | % | 507:98 | 10 | 89 |  |  | 1s | % | 507:98 | 10 | 89 |  |  | 7010 | 21
York RTU.Exhaust Fan Control | Economizer Damper Position for Exhaust Fan to Turn On | EconDmpPosFanOn | Not Set | 344 | 2 | HoldingRegister | 66 | TRUE | 0 | 10 | 5 | 20 ... 99 % |  | TRUE | 4 | 1s | % | 507:98 | 20 | 99 |  |  | 1s | % | 507:98 | 20 | 99 |  |  | 7011 | 21
York RTU.Exhaust Fan Control | Economizer Damper Position for Exhaust Fan to Turn Off | EconDmpPosFanOff | Not Set | 344 | 2 | HoldingRegister | 67 | TRUE | 0 | 10 | 5 | 10 ... 89 % |  | TRUE | 4 | 1s | % | 507:98 | 10 | 89 |  |  | 1s | % | 507:98 | 10 | 89 |  |  | 7012 | 21
York RTU.Exhaust Fan Control | ERV Enabled | ERV-En | Not Set | 344 | 2 | HoldingRegister | 121 | FALSE | 0 | 1 | 4 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7013 | 21
York RTU.Exhaust Fan Control | ERV Unoccupied Fan Enabled | ERVUnoccFan-En | Not Set | 344 | 2 | HoldingRegister | 122 | FALSE | 0 | 1 | 4 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7014 | 21
York RTU.Demand Ventilation Control | Demand Ventilation Mode of Operation | DVent-Mode | Not Set | 344 | 2 | HoldingRegister | 120 | FALSE | 0 | 1 | 4 | 0 = Disabled 1 = Controlled by IAQ 2 = Diff between IAQ and OAQ |  | TRUE | 9 |  | SE RTU DCV Mode | 1729 | [5 empty] | SE RTU DCV Mode | 1729 |  |  |  |  | 7000 | 23
York RTU.Demand Ventilation Control | Demand Ventilation Maximum Economizer Position | DVentMaxEconPos | Not Set | 344 | 2 | HoldingRegister | 60 | TRUE | 0 | 10 | 5 | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7001 | 23
York RTU.Demand Ventilation Control | Demand Ventilation Indoor Air Quality Setpoint | DVentIAQ-Sp | Not Set | 344 | 2 | HoldingRegister | 61 | TRUE | 0 | 10 | 5 | 0 ... 5000 ppm |  | TRUE | 4 | 1s | ppm | 507:96 | 0 | 5000 |  |  | 1s | ppm | 507:96 | 0 | 5000 |  |  | 7002 | 23
York RTU.Demand Ventilation Control | Demand Ventilation Differential Setpoint | DVentDiff-Sp | Not Set | 344 | 2 | HoldingRegister | 62 | TRUE | 0 | 10 | 5 | 0 ... 5000 ppm |  | TRUE | 4 | 1s | ppm | 507:96 | 0 | 5000 |  |  | 1s | ppm | 507:96 | 0 | 5000 |  |  | 7003 | 23
York RTU.Air Monitor Station | Fresh Air Intake Setpoint | MOAFlow-Sp | Not Set | 344 | 2 | HoldingRegister | 69 | TRUE | 0 | 10 | 5 | 0 ... 50000 cfm (0 ... 25000 L/s) |  | TRUE | 4 | 10s | cfm | 507:84 | 0 | 50000 |  |  | 10s | L/s | 507:87 | 0 | 25000 |  |  | 7000 | 24
York RTU.Air Monitor Station | Fresh Air Intake Value | OA-Flow | Not Set | 344 | 2 | InputRegister | 262 | TRUE | 0 | 10 | 5 | cfm (L/s) |  | FALSE | 4 | 1s | cfm | 507:84 |  |  |  |  | 1s | L/s | 507:87 |  |  |  |  | 7001 | 24
York RTU.Air Monitor Station | Fresh Air Intake Max Sensor Range | MOA-Range | Not Set | 344 | 2 | HoldingRegister | 70 | TRUE | 0 | 10 | 5 | 0 ... 50000 cfm (0 ... 25000 L/s) |  | TRUE | 4 | 10s | cfm | 507:84 | 0 | 50000 |  |  | 10s | L/s | 507:87 | 0 | 25000 |  |  | 7002 | 24
York RTU.Air Monitor Station | Fresh Air Intake Enable | FrAir-En | Not Set | 344 | 2 | InputRegister | 134 | FALSE | 0 | 1 | 4 | 0 = Disable 1 = Enable |  | TRUE | 9 |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 |  |  |  |  | 7004 | 24
York RTU.HVAC Zone | Occupancy Input Source | OccSrc | Not Set | 344 | 2 | InputRegister | 290 | FALSE | 0 | 1 | 4 | 0 = Local Input 1 = Local Network Sensor 2 = BAS Network Request 3 = Local Schedule 4 = Temporary Occupancy |  | FALSE | 9 |  | Effective Occupancy Source | 1668 | [5 empty] | Effective Occupancy Source | 1668 |  |  |  |  | 7000 | 25
York RTU.HVAC Zone | Operational Occupancy | OprOcc | Not Set | 344 | 2 | InputRegister | 292 | FALSE | 0 | 1 | 4 | 0 = Occupied 1 = UnOccupied 2 = Bypass 3 = Standby |  | FALSE | 9 |  | Occ Effective | 345 | [5 empty] | Occ Effective | 345 |  |  |  |  | 7001 | 25
York RTU.HVAC Zone | Occupancy Mode | OccMode | Not Set | 344 | 2 | HoldingRegister | 82 | FALSE | 0 | 1 | 4 | 0 = Schedule 1 = External |  | TRUE | 9 |  | SE Occupancy Mode | 1728 | [5 empty] | SE Occupancy Mode | 1728 |  |  |  |  | 7002 | 25
York RTU.HVAC Zone | Network Temporary Occupancy Request | NetTempOcc | Not Set | 344 | 2 | HoldingRegister | 83 | FALSE | 0 | 1 | 4 | 0 = False 1 = True |  | TRUE | 9 |  | False/True | 1701 | [5 empty] | False/True | 1701 |  |  |  |  | 7003 | 25
York RTU.HVAC Zone | Network Occupancy Request | NetOcc | Not Set | 344 | 2 | HoldingRegister | 84 | FALSE | 0 | 1 | 4 | 0 = Occupied 1 = UnOccupied 2 = Not Set |  | TRUE | 9 |  | Occ Sensor | 344 | [5 empty] | Occ Sensor | 344 |  |  |  |  | 7004 | 25
York RTU.HVAC Zone | Temporary Occupancy Timeout | TempOccTimeout | Not Set | 344 | 2 | HoldingRegister | 85 | FALSE | 0 | 1 | 4 | 30 ... 600 minutes |  | TRUE | 17 | 1s | minutes | 507:72 | 30 | 600 |  |  | 1s | minutes | 507:72 | 30 | 600 |  |  | 7005 | 25
York RTU.HVAC Zone | Operational Space Temperature | OprST | Not Set | 344 | 2 | InputRegister | 135 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7006 | 25
York RTU.HVAC Zone | Space Temperature Source | STSrc | Not Set | 344 | 2 | InputRegister | 293 | FALSE | 0 | 1 | 4 | 0 = Unreliable 1 = Return Air Temp 2 = Local Input 3 = Network Sensor ... |  | FALSE | 9 |  | Effective Input Source | 1715 | [5 empty] | Effective Input Source | 1715 |  |  |  |  | 7007 | 25
York RTU.HVAC Zone | Space Temperature Alarm Setpoint Offset | STAlarmOffset | Not Set | 344 | 2 | HoldingRegister | 274 | TRUE | 0 | 10 | 5 | 0 ... 25 delta deg F (0 ... 14 delta deg C) |  | TRUE | 4 | 1s | delta deg F | 507:120 | 0 | 25 |  |  | 1s | delta deg C | 507:359 | 0 | 14 |  |  | 7008 | 25
York RTU.HVAC Zone | Space Temperature Alarm Time Delay | STAlarmDelay | Not Set | 344 | 2 | HoldingRegister | 86 | FALSE | 0 | 1 | 4 | 0 ... 120 minutes |  | TRUE | 17 | 1s | minutes | 507:72 | 0 | 120 |  |  | 1s | minutes | 507:72 | 0 | 120 |  |  | 7009 | 25
York RTU.HVAC Zone | Network Override Space Temperature | NetST | Not Set | 344 | 2 | HoldingRegister | 1 | TRUE | 0 | 10 | 5 | 0 ... 100 deg F (4 ... 38 deg C) |  | TRUE | 4 | 10ths | deg F | 507:64 | 0 | 100 |  |  | 10ths | deg C | 507:62 | 4 | 38 |  |  | 7011 | 25
York RTU.HVAC Zone | Operational Indoor Air Quality | OprIAQ | Not Set | 344 | 2 | InputRegister | 136 | TRUE | 0 | 10 | 5 | ppm |  | FALSE | 4 | 10s | ppm | 507:96 |  |  |  |  | 10s | ppm | 507:96 |  |  |  |  | 7012 | 25
York RTU.HVAC Zone | Indoor Air Quality Source | IAQSrc | Not Set | 344 | 2 | InputRegister | 294 | FALSE | 0 | 1 | 4 | 0 = Unreliable 1 = Local Input 2 = Network Sensor 3 = High Priority ... |  | FALSE | 9 |  | Effective Input Source 2 | 1732 | [5 empty] | Effective Input Source 2 | 1732 |  |  |  |  | 7013 | 25
York RTU.HVAC Zone | Indoor Air Quality Sensor Range | IAQRange | Not Set | 344 | 2 | HoldingRegister | 2 | TRUE | 0 | 10 | 5 | 0 ... 5000 ppm |  | TRUE | 4 | 1s | ppm | 507:96 | 0 | 5000 |  |  | 1s | ppm | 507:96 | 0 | 5000 |  |  | 7015 | 25
York RTU.HVAC Zone | Network Override Indoor Air Quality | NetIAQ | Not Set | 344 | 2 | HoldingRegister | 3 | TRUE | 0 | 10 | 5 | 0 ... 5000 ppm |  | TRUE | 4 | 10s | ppm | 507:96 | 0 | 5000 |  |  | 10s | ppm | 507:96 | 0 | 5000 |  |  | 7016 | 25
York RTU.HVAC Zone | Operational Space Humidity | OprSH | Not Set | 344 | 2 | InputRegister | 137 | TRUE | 0 | 10 | 5 | %RH |  | FALSE | 4 | 10ths | %RH | 507:29 |  |  |  |  | 10ths | %RH | 507:29 |  |  |  |  | 7017 | 25
York RTU.HVAC Zone | Space Humidity Source | SHSrc | Not Set | 344 | 2 | InputRegister | 295 | FALSE | 0 | 1 | 4 | 0 = Unreliable 1 = Local Input 2 = Network Sensor 3 = High Priority ... |  | FALSE | 9 |  | Effective Input Source 2 | 1732 | [5 empty] | Effective Input Source 2 | 1732 |  |  |  |  | 7018 | 25
York RTU.HVAC Zone | Space Humidity RAH Input | RAH | Not Set | 344 | 2 | InputRegister | 138 | TRUE | 0 | 10 | 5 | %RH |  | FALSE | 4 | 10ths | %RH | 507:29 |  |  |  |  | 10ths | %RH | 507:29 |  |  |  |  | 7019 | 25
York RTU.HVAC Zone | Network Override Zone Humidity | NetSH | Not Set | 344 | 2 | HoldingRegister | 4 | TRUE | 0 | 10 | 5 | 0 ... 100 %RH |  | TRUE | 4 | 10ths | %RH | 507:29 | 0 | 100 |  |  | 10ths | %RH | 507:29 | 0 | 100 |  |  | 7020 | 25
York RTU.HVAC Zone | Operating Fan Request | OprFanReq | Not Set | 344 | 2 | InputRegister | 296 | FALSE | 0 | 1 | 4 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7021 | 25
York RTU.HVAC Zone | Fan Request Source | FanReqSrc | Not Set | 344 | 2 | InputRegister | 297 | FALSE | 0 | 1 | 4 | 0 = Unreliable 1 = Local Input 2 = Network Sensor 3 = High Priority ... |  | FALSE | 9 |  | Effective Input Source 2 | 1732 | [5 empty] | Effective Input Source 2 | 1732 |  |  |  |  | 7022 | 25
York RTU.HVAC Zone | Network Override Fan Request | NetFanReq | Not Set | 344 | 2 | HoldingRegister | 87 | FALSE | 0 | 1 | 4 | 0 = Off 1 = On |  | TRUE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7023 | 25
York RTU.HVAC Zone | Operational Space Temperature Setpoint Offset | OprSSO | Not Set | 344 | 2 | InputRegister | 140 | TRUE | 0 | 10 | 5 | delta deg F (delta deg C) |  | FALSE | 4 | 10ths | delta deg F | 507:120 |  |  |  |  | 10ths | delta deg C | 507:359 |  |  |  |  | 7024 | 25
York RTU.HVAC Zone | Space Temperature Setpoint Offset Source | SSOSrc | Not Set | 344 | 2 | InputRegister | 298 | FALSE | 0 | 1 | 4 | 0 = Unreliable 1 = Local Input 2 = Network Sensor 3 = High Priority ... |  | FALSE | 9 |  | Effective Input Source 2 | 1732 | [5 empty] | Effective Input Source 2 | 1732 |  |  |  |  | 7025 | 25
York RTU.HVAC Zone | Space Temp Setpoint Offset Input | SSO | Not Set | 344 | 2 | InputRegister | 141 | TRUE | 0 | 10 | 5 | delta deg F (delta deg C) |  | FALSE | 4 | 10ths | delta deg F | 507:120 |  |  |  |  | 10ths | delta deg C | 507:359 |  |  |  |  | 7026 | 25
York RTU.HVAC Zone | Network Override Space Setpoint Offset | NetSSO | Not Set | 344 | 2 | HoldingRegister | 5 | TRUE | 0 | 10 | 5 | -5 ... 5 delta deg F (-3 ... 3 delta deg C) |  | TRUE | 4 | 10ths | delta deg F | 507:120 | -5 | 5 |  |  | 10ths | delta deg C | 507:359 | -3 | 3 |  |  | 7027 | 25
York RTU.HVAC Zone | Occupancy Input | OCC | Not Set | 344 | 2 | InputRegister | 291 | FALSE | 0 | 1 | 4 | 0 = Occupied 1 = Unoccupied |  | FALSE | 9 |  | SE RTU Unocc/Occ | 1658 | [5 empty] | SE RTU Unocc/Occ | 1658 |  |  |  |  | 7030 | 25
York RTU.HVAC Zone | Return Air Temperature | RAT | Not Set | 344 | 2 | InputRegister | 139 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7038 | 25
York RTU.HVAC Zone | Temporary Occupancy Input | TempOCC | Not Set | 344 | 2 | HoldingRegister | 81 | FALSE | 0 | 1 | 4 | 0 = Disable 1 = Enable |  | TRUE | 9 |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 |  |  |  |  | 7040 | 25
York RTU.HVAC Zone | Load Shed Active | LoadShedEnable | Not Set | 344 | 2 | HoldingRegister | 127 | FALSE | 0 | 1 | 4 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7043 | 25
York RTU.HVAC Zone | Load Shed Rate Limit | LoadShedRateLim | Not Set | 344 | 2 | HoldingRegister | 71 | FALSE | 0 | 1000 | 7 | 0 ... 1 deg F/min (0 ... 1 deg C/min) |  | TRUE | 4 | 1000ths | deg F/min | 507:94 | 0 | 1 |  |  | 1000ths | deg C/min | 507:92 | 0 | 1 |  |  | 7044 | 25
York RTU.HVAC Zone | Load Shed Adjust | LoadShedAdjust | Not Set | 344 | 2 | HoldingRegister | 72 | FALSE | 0 | 10 | 5 | 0 ... 8 delta deg F (0 ... 4.4 delta deg C) |  | TRUE | 4 | 10ths | delta deg F | 507:120 | 0 | 8 |  |  | 10ths | delta deg C | 507:359 | 0 | 4.4 |  |  | 7045 | 25
York RTU.HVAC Zone | Time to Next Occupancy Period | TimeToNextOcc | Not Set | 344 | 2 | InputRegister | 142 | FALSE | 0 | 10 | 5 | minutes |  | FALSE | 4 | 10ths | minutes | 507:72 |  |  |  |  | 10ths | minutes | 507:72 |  |  |  |  | 7046 | 25
York RTU.HVAC Zone | Operating Mode | OprMode | Not Set | 344 | 2 | InputRegister | 299 | FALSE | 0 | 1 | 4 | 0 = Normal 1 = Warmup 2 = Cooldown 3 = Coast |  | FALSE | 9 |  | OST Warmup Cooldown | 366 | [5 empty] | OST Warmup Cooldown | 366 |  |  |  |  | 7047 | 25
York RTU.HVAC Zone | Off During Unoccupied | OffDurUnocc | Not Set | 344 | 2 | HoldingRegister | 88 | FALSE | 0 | 1 | 4 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7059 | 25
York RTU.HVAC Zone | Direct Loadshed | DirLoadshd | Not Set | 344 | 2 | HoldingRegister | 128 | FALSE | 0 | 1 | 4 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7061 | 25
York RTU.HVAC Zone | Redline | Redline | Not Set | 344 | 2 | HoldingRegister | 129 | FALSE | 0 | 1 | 4 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7062 | 25
York RTU.HVAC Zone | PID Tuning Reset | PIDTunRst | Not Set | 344 | 2 | HoldingRegister | 130 | FALSE | 0 | 1 | 4 | 0 = False 1 = True |  | TRUE | 9 |  | False/True | 1701 | [5 empty] | False/True | 1701 |  |  |  |  | 7063 | 25
York RTU.Weather Information | Operational Outdoor Air Temperature | OprOAT | Not Set | 344 | 2 | InputRegister | 153 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7000 | 26
York RTU.Weather Information | Outdoor Air Temperature Source | OATSrc | Not Set | 344 | 2 | InputRegister | 300 | FALSE | 0 | 1 | 4 | 0 = Unreliable 1 = Local Input 2 = Network Sensor 3 = High Priority ... |  | FALSE | 9 |  | Effective Input Source 2 | 1732 | [5 empty] | Effective Input Source 2 | 1732 |  |  |  |  | 7001 | 26
York RTU.Weather Information | Network Override Outdoor Air Temperature | NetOAT | Not Set | 344 | 2 | HoldingRegister | 6 | TRUE | 0 | 10 | 5 | -50 ... 125 deg F (-18 ... 52 deg C) |  | TRUE | 4 | 10ths | deg F | 507:64 | -50 | 125 |  |  | 10ths | deg C | 507:62 | -18 | 52 |  |  | 7003 | 26
York RTU.Weather Information | Operational Outdoor Air Humidity | OprOAH | Not Set | 344 | 2 | InputRegister | 154 | TRUE | 0 | 10 | 5 | %RH |  | FALSE | 4 | 1s | %RH | 507:29 |  |  |  |  | 1s | %RH | 507:29 |  |  |  |  | 7004 | 26
York RTU.Weather Information | Outdoor Air Enthalpy | OA-Enth | Not Set | 344 | 2 | InputRegister | 155 | TRUE | 0 | 10 | 5 | Btu/lb (kJ/kg) |  | FALSE | 4 | 1s | Btu/lb | 507:117 |  |  |  |  | 1s | kJ/kg | 507:125 |  |  |  |  | 7005 | 26
York RTU.Weather Information | Network Override Outdoor Air Humidity | NetOAH | Not Set | 344 | 2 | HoldingRegister | 7 | TRUE | 0 | 10 | 5 | 0 ... 100 %RH |  | TRUE | 4 | 10ths | %RH | 507:29 | 0 | 100 |  |  | 10ths | %RH | 507:29 | 0 | 100 |  |  | 7008 | 26
York RTU.Weather Information | Operational Outdoor Air Quality | OprOAQ | Not Set | 344 | 2 | InputRegister | 156 | TRUE | 0 | 10 | 5 | ppm |  | FALSE | 4 | 10s | ppm | 507:96 |  |  |  |  | 10s | ppm | 507:96 |  |  |  |  | 7009 | 26
York RTU.Weather Information | Outdoor Air Quality Source | OAQSrc | Not Set | 344 | 2 | InputRegister | 301 | FALSE | 0 | 1 | 4 | 0 = Unreliable 1 = Local Input 2 = Network Sensor 3 = High Priority ... |  | FALSE | 9 |  | Effective Input Source 2 | 1732 | [5 empty] | Effective Input Source 2 | 1732 |  |  |  |  | 7010 | 26
York RTU.Weather Information | Network Override Outdoor Air Quality | NetOAQ | Not Set | 344 | 2 | HoldingRegister | 8 | TRUE | 0 | 10 | 5 | 0 ... 5000 ppm |  | TRUE | 4 | 10s | ppm | 507:96 | 0 | 5000 |  |  | 10s | ppm | 507:96 | 0 | 5000 |  |  | 7013 | 26
York RTU.Shutdown Input | Operating Purge Command | OprPurgeCmd | Not Set | 344 | 2 | InputRegister | 381 | FALSE | 0 | 1 | 4 | 0 = False 1 = True |  | FALSE | 9 |  | False/True | 1701 | [5 empty] | False/True | 1701 |  |  |  |  | 7000 | 27
York RTU.Shutdown Input | Purge Command Source | PurgeCmdSrc | Not Set | 344 | 2 | InputRegister | 382 | FALSE | 0 | 1 | 4 | 0 = Unreliable 1 = Local Input 2 = Network Sensor 3 = High Priority ... |  | FALSE | 9 |  | Effective Input Source 2 | 1732 | [5 empty] | Effective Input Source 2 | 1732 |  |  |  |  | 7001 | 27
York RTU.Shutdown Input | Local Purge Command Input | Purge | Not Set | 344 | 2 | InputRegister | 383 | FALSE | 0 | 1 | 4 | 0 = False 1 = True |  | FALSE | 9 |  | False/True | 1701 | [5 empty] | False/True | 1701 |  |  |  |  | 7002 | 27
York RTU.Shutdown Input | Network Override Purge Command | NetPurge | Not Set | 344 | 2 | HoldingRegister | 125 | FALSE | 0 | 1 | 4 | 0 = False 1 = True |  | TRUE | 9 |  | False/True | 1701 | [5 empty] | False/True | 1701 |  |  |  |  | 7003 | 27
York RTU.Shutdown Input | Shutdown Input/Smoke Detector | SD | Not Set | 344 | 2 | InputRegister | 384 | FALSE | 0 | 1 | 4 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7004 | 27
York RTU.System Controllers | Econ Controller | EconCntlr | Not Set | 344 | 2 | InputRegister | 385 | FALSE | 0 | 1 | 4 | 0 = Not Present 1 = Offline 2 = Online |  | FALSE | 9 |  | EIO Connection Status | 1662 | [5 empty] | EIO Connection Status | 1662 |  |  |  |  | 7004 | 29
York RTU.System Controllers | 4 Stage Controller | 4StgCntlr | Not Set | 344 | 2 | InputRegister | 386 | FALSE | 0 | 1 | 4 | 0 = Not Present 1 = Offline 2 = Online |  | FALSE | 9 |  | EIO Connection Status | 1662 | [5 empty] | EIO Connection Status | 1662 |  |  |  |  | 7005 | 29
York RTU.System Controllers | FDD Manager Controller | FDDMCntlr | Not Set | 344 | 2 | InputRegister | 387 | FALSE | 0 | 1 | 4 | 0 = Not Present 1 = Offline 2 = Online |  | FALSE | 9 |  | EIO Connection Status | 1662 | [5 empty] | EIO Connection Status | 1662 |  |  |  |  | 7006 | 29
York RTU.System Controllers | FDD Subordinate Controller | FDDSCntlr | Not Set | 344 | 2 | InputRegister | 388 | FALSE | 0 | 1 | 4 | 0 = Not Present 1 = Offline 2 = Online |  | FALSE | 9 |  | EIO Connection Status | 1662 | [5 empty] | EIO Connection Status | 1662 |  |  |  |  | 7007 | 29
York RTU.Heat Pump Control | Number of Heat Pump Stages Installed | #HtPumpStgs | Not Set | 344 | 2 | HoldingRegister | 434 | FALSE | 0 | 1 | 4 | 0 ... 2 |  | TRUE | 4 | 1s |  | 507:95 | 0 | 2 |  |  | 1s |  | 507:95 | 0 | 2 |  |  | 7000 | 38
York RTU.Heat Pump Control | Defrost Curve Selection | DefrostCurveSel | Not Set | 344 | 2 | HoldingRegister | 117 | FALSE | 0 | 1 | 4 | 0 = Curve 1 1 = Curve 2 2 = Curve 3 3 = Curve 4 ... |  | TRUE | 9 |  | SE RTU Defrost Curves | 1665 | [5 empty] | SE RTU Defrost Curves | 1665 |  |  |  |  | 7004 | 38
York RTU.Heat Pump Control | Reversing Valve | RevVlv | Not Set | 344 | 2 | InputRegister | 366 | FALSE | 0 | 1 | 4 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7011 | 38
York RTU.Heat Pump Control | Auxiliary Heat | AuxHtg | Not Set | 344 | 2 | InputRegister | 367 | FALSE | 0 | 1 | 4 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7012 | 38
York RTU.Heat Pump Control | Mode | Mode | Not Set | 344 | 2 | InputRegister | 368 | FALSE | 0 | 1 | 4 | 0 = Heating 1 = Cooling |  | FALSE | 9 |  | Heating/Cooling | 350 | [5 empty] | Heating/Cooling | 350 |  |  |  |  | 7013 | 38
York RTU | Unit Enable | UnitEn | Not Set | 344 | 2 | HoldingRegister | 411 | FALSE | 0 | 1 | 4 | 0 = Shutdown 1 = Enable |  | TRUE | 9 |  | Shutdown/Enable | 349 | [5 empty] | Shutdown/Enable | 349 |  |  |  |  | 7019 | 1
York RTU.Cooling Control | SZ VAV Occupied Cooling Setpoint | SZVCLGOCSP | Not Set | 344 | 2 | HoldingRegister | 270 | TRUE | 0 | 10 | 5 | 45 ... 98 deg F (7 ... 36 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 45 | 98 |  |  | 1s | deg C | 507:62 | 7 | 36 |  |  | 7048 | 4
York RTU.Cooling Control | SZ VAV Unoccupied Cooling Setpoint | SZVCLGUNSP | Not Set | 344 | 2 | HoldingRegister | 271 | TRUE | 0 | 10 | 5 | 45 ... 98 deg F (7 ... 36 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 45 | 98 |  |  | 1s | deg C | 507:62 | 7 | 36 |  |  | 7049 | 4
York RTU.Cooling Control | SZ VAV Operating Cooling Setpoint | OPSZVCLGSP | Not Set | 344 | 2 | InputRegister | 850 | FALSE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 100ths | deg F | 507:64 |  |  |  |  | 100ths | deg C | 507:62 |  |  |  |  | 7061 | 4
York RTU.Cooling Control | SZ VAV Cooling Load | SZVAVCLGLD | Not Set | 344 | 2 | InputRegister | 438 | FALSE | 0 | 10 | 5 | % |  | FALSE | 4 | 10ths | % | 507:98 |  |  |  |  | 10ths | % | 507:98 |  |  |  |  | 7053 | 4
York RTU.Heating Control | SZ VAV Heating Load | SZVAVHTGLD | Not Set | 344 | 2 | InputRegister | 439 | FALSE | 0 | 10 | 5 | % |  | FALSE | 4 | 10ths | % | 507:98 |  |  |  |  | 10ths | % | 507:98 |  |  |  |  | 7050 | 13
York RTU | Event 1 Value | Event1Value | Not Set | 344 | 2 | InputRegister | 268 | FALSE | 0 | 1 | 4 |  |  | FALSE | 18 | 1s |  | 507:95 |  |  |  |  | 1s |  | 507:95 |  |  |  |  | 7023 | 1
York RTU | Event 2 Value | Event2Value | Not Set | 344 | 2 | InputRegister | 269 | FALSE | 0 | 1 | 4 |  |  | FALSE | 18 | 1s |  | 507:95 |  |  |  |  | 1s |  | 507:95 |  |  |  |  | 7024 | 1
York RTU | Event 3 Value | Event3Value | Not Set | 344 | 2 | InputRegister | 276 | FALSE | 0 | 1 | 4 |  |  | FALSE | 18 | 1s |  | 507:95 |  |  |  |  | 1s |  | 507:95 |  |  |  |  | 7025 | 1
York RTU | Event 4 Value | Event4Value | Not Set | 344 | 2 | InputRegister | 277 | FALSE | 0 | 1 | 4 |  |  | FALSE | 18 | 1s |  | 507:95 |  |  |  |  | 1s |  | 507:95 |  |  |  |  | 7026 | 1
York RTU | Event 5 Value | Event5Value | Not Set | 344 | 2 | InputRegister | 278 | FALSE | 0 | 1 | 4 |  |  | FALSE | 18 | 1s |  | 507:95 |  |  |  |  | 1s |  | 507:95 |  |  |  |  | 7027 | 1
York RTU | Event 1 Set | Event1Set | Not Set | 344 | 2 | InputRegister | 394 | FALSE | 0 | 1 | 4 |  |  | FALSE | 18 | 1s |  | 507:95 |  |  |  |  | 1s |  | 507:95 |  |  |  |  | 7028 | 1
York RTU | Event 2 Set | Event2Set | Not Set | 344 | 2 | InputRegister | 395 | FALSE | 0 | 1 | 4 |  |  | FALSE | 18 | 1s |  | 507:95 |  |  |  |  | 1s |  | 507:95 |  |  |  |  | 7029 | 1
York RTU | Event 3 Set | Event3Set | Not Set | 344 | 2 | InputRegister | 396 | FALSE | 0 | 1 | 4 |  |  | FALSE | 18 | 1s |  | 507:95 |  |  |  |  | 1s |  | 507:95 |  |  |  |  | 7030 | 1
York RTU | Event 4 Set | Event4Set | Not Set | 344 | 2 | InputRegister | 397 | FALSE | 0 | 1 | 4 |  |  | FALSE | 18 | 1s |  | 507:95 |  |  |  |  | 1s |  | 507:95 |  |  |  |  | 7031 | 1
York RTU | Event 5 Set | Event5Set | Not Set | 344 | 2 | InputRegister | 398 | FALSE | 0 | 1 | 4 |  |  | FALSE | 18 | 1s |  | 507:95 |  |  |  |  | 1s |  | 507:95 |  |  |  |  | 7032 | 1
York RTU | High Alarm Text | CriticalActiveEvent | Not Set | 344 | 2 | InputRegister | 834 | FALSE | 0 | 1 | 4 | 0 = None 1 = Event Generator Configuration Error 2 = Calibration Error 100 = Parameters Not Configured, Use Default ... |  | FALSE | 9 |  | SE Event Active Critical Codes | 1716 | [5 empty] | SE Event Active Critical Codes | 1716 |  |  |  |  | 7037 | 1
York RTU | Low Alarm Text | CriticalInactiveEvent | Not Set | 344 | 2 | InputRegister | 835 | FALSE | 0 | 1 | 4 | 0 = None 1 = Event Generator Configuration Error 2 = Calibration Error 100 = Parameters Not Configured, Use Default ... |  | FALSE | 9 |  | SE Event Inactive Critical Codes | 1719 | [5 empty] | SE Event Inactive Critical Codes | 1719 |  |  |  |  | 7038 | 1
York RTU | High Alarm Text | ServicePriorityActiveEvent | Not Set | 344 | 2 | InputRegister | 836 | FALSE | 0 | 1 | 4 | 0 = None 1 = Firmware versions do not match package 100 = FDD Firmware Failure 101 = No Dehum Due to Space Humidity ... |  | FALSE | 9 |  | SE Event Active Service Priority Codes | 1717 | [5 empty] | SE Event Active Service Priority Codes | 1717 |  |  |  |  | 7039 | 1
York RTU | Low Alarm Text | ServicePriorityInactiveEvent | Not Set | 344 | 2 | InputRegister | 837 | FALSE | 0 | 1 | 4 | 0 = None 1 = Firmware versions do not match package 100 = FDD Firmware Failure 101 = No Dehum Due to Space Humidity ... |  | FALSE | 9 |  | SE Event Inactive Service Priority Codes | 1720 | [5 empty] | SE Event Inactive Service Priority Codes | 1720 |  |  |  |  | 7040 | 1
York RTU | High Alarm Text | ServiceActiveEvent | Not Set | 344 | 2 | InputRegister | 838 | FALSE | 0 | 1 | 4 | 0 = None 1 = Reboot 100 = Econ Not Economizing When It Should 101 = Econ Economizing When It Should Not ... |  | FALSE | 9 |  | SE Event Active Service Codes | 1718 | [5 empty] | SE Event Active Service Codes | 1718 |  |  |  |  | 7041 | 1
York RTU | Low Alarm Text | ServiceInactiveEvent | Not Set | 344 | 2 | InputRegister | 839 | FALSE | 0 | 1 | 4 | 0 = None 1 = Reboot 100 = Econ Not Economizing When It Should 101 = Econ Economizing When It Should Not ... |  | FALSE | 9 |  | SE Event Inactive Service Codes | 1721 | [5 empty] | SE Event Inactive Service Codes | 1721 |  |  |  |  | 7042 | 1
York RTU.Heating Control | SZ VAV Occupied Heating Setpoint | SZVHTGOCSP | Not Set | 344 | 2 | HoldingRegister | 272 | TRUE | 0 | 10 | 5 | 46 ... 99 deg F (8 ... 37 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 46 | 99 |  |  | 1s | deg C | 507:62 | 8 | 37 |  |  | 7047 | 13
York RTU.Heating Control | SZ VAV Unoccupied Heating Setpoint | SZVHTGUNSP | Not Set | 344 | 2 | HoldingRegister | 273 | TRUE | 0 | 10 | 5 | 45 ... 98 deg F (7 ... 36 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 45 | 98 |  |  | 1s | deg C | 507:62 | 7 | 36 |  |  | 7048 | 13
York RTU.HVAC Zone | Heat Cool Setpoint Mode | HtgClgSP-Mode | HtgClgSP-Mode | 1709 | 701 | HoldingRegister | 852 | FALSE | 0 | 1 | 4 | 0 = Common Setpoint 1 = Individual Setpoints |  | TRUE | 9 |  | Heat Cool Setpoint Mode | 2596 | [5 empty] | Heat Cool Setpoint Mode | 2596 |  |  |  |  | 7075 | 25
York RTU.HVAC Zone | Common Setpoint | Common-SP | Common-SP | 1709 | 702 | HoldingRegister | 853 | TRUE | 0 | 10 | 5 | 45 ... 98 deg F (8 ... 36 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 45 | 98 |  |  | 1s | deg C | 507:62 | 8 | 36 |  |  | 7074 | 25
York RTU.Fan Control | Dehumidification % Command | Dehum%Cmd | Not Set | 344 | 2 | HoldingRegister | 851 | TRUE | 0 | 10 | 5 | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7042 | 3
York RTU.Hot Gas Reheat | Hot Gas Reheat Command | ModHGR | Not Set | 344 | 2 | InputRegister | 389 | TRUE | 0 | 10 | 5 | % |  | FALSE | 4 | 10ths | % | 507:98 |  |  |  |  | 10ths | % | 507:98 |  |  |  |  | 7027 | 20
York RTU.Economizer | Economizer Fault Detection Enable | CalFaultDetectEn | Not Set | 344 | 2 | HoldingRegister | 843 | FALSE | 0 | 1 | 4 | 0 = Disable 1 = Enable |  | TRUE | 9 |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 |  |  |  |  | 7028 | 19
York RTU.Shutdown Input | Pressurize Instead Of Purge | PressurizeNotPurge | Not Set | 344 | 2 | HoldingRegister | 844 | FALSE | 0 | 1 | 4 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7005 | 27
York RTU.Cooling Control | Cooling Allowed During Heat Limit | CoolDuringHeatLimit | Not Set | 344 | 2 | HoldingRegister | 845 | FALSE | 0 | 1 | 4 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7060 | 4
York RTU.Fan Control | Low Pressure Limit 1 | DAP-Min | Not Set | 344 | 2 | HoldingRegister | 846 | TRUE | 0 | 100 | 6 | 0.01 ... 1 in wc (2.5 ... 250 Pa) |  | TRUE | 4 | 100ths | in wc | 507:58 | 0.01 | 1 |  |  | 100ths | Pa | 507:53 | 2.5 | 250 |  |  | 7038 | 3
York RTU.Fan Control | Time | DAP-AlmDly | Not Set | 344 | 2 | HoldingRegister | 847 | TRUE | 0 | 1 | 4 | 0 ... 600 seconds |  | TRUE | 18 | 1s | seconds | 507:73 | 0 | 600 |  |  | 1s | seconds | 507:73 | 0 | 600 |  |  | 7040 | 3
York RTU.Hot Gas Reheat | Evaporator Coil Temp | EVAP-T | Not Set | 344 | 2 | InputRegister | 854 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7026 | 20
York RTU.Hot Gas Reheat | Hot Gas Reheat Bleed Valve Command | HGRB-C | Not Set | 344 | 2 | InputRegister | 855 | FALSE | 0 | 1 | 4 | 0 = Close 1 = Open |  | FALSE | 9 |  | Close/Open | 939 | [5 empty] | Close/Open | 939 |  |  |  |  | 7029 | 20
York RTU.Cooling Control | FDD Alarm Enable | FDDAlarmEn | Not Set | 344 | 2 | HoldingRegister | 848 | FALSE | 0 | 1 | 4 | 0 = Disable 1 = Enable |  | TRUE | 9 |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 |  |  |  |  | 7062 | 4
York RTU.Cooling Control | SZ VAV Operating Cooling Setpoint | OprClgDAT-SP | Not Set | 344 | 2 | InputRegister | 266 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7050 | 4
York RTU.Economizer | Econ Sensor Fault Indications | EconSensorFaults | Not Set | 344 | 2 | HoldingRegister | 849 | FALSE | 0 | 1 | 4 | 0 = Disable 1 = Enable |  | TRUE | 9 |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 |  |  |  |  | 7033 | 19
York RTU.Cooling Control | Modulating Condenser Fan 1 Output | ModCondFan1Out | Not Set | 344 | 2 | InputRegister | 856 | TRUE | 0 | 10 | 5 | 0 ... 100 % |  | FALSE | 4 | 10ths | % | 507:98 | 0 | 100 |  |  | 10ths | % | 507:98 | 0 | 100 |  |  | 7065 | 4
York RTU.Cooling Control | Modulating Condenser Fan 2 Output | ModCondFan2Out | Not Set | 344 | 2 | InputRegister | 857 | TRUE | 0 | 10 | 5 | 0 ... 100 % |  | FALSE | 4 | 10ths | % | 507:98 | 0 | 100 |  |  | 10ths | % | 507:98 | 0 | 100 |  |  | 7066 | 4
York RTU.Cooling Control | Modulating Compressor Output | ModCompOut | Not Set | 344 | 2 | InputRegister | 858 | TRUE | 0 | 10 | 5 | 0 ... 100 % |  | FALSE | 4 | 10ths | % | 507:98 | 0 | 100 |  |  | 10ths | % | 507:98 | 0 | 100 |  |  | 7067 | 4
York RTU.Cooling Control | Circuit 1 OAT Cooling Cutout | Circ1ClgOATCutout | Not Set | 344 | 2 | HoldingRegister | 859 | FALSE | 0 | 10 | 5 | ... 100 deg F ( ... 38 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 |  | 100 | 7070 |  | 1s | deg C | 507:62 |  | 38 | 7070 |  | 7068 | 4
York RTU.Cooling Control | Circuit 2 OAT Cooling Cutout | Circ2ClgOATCutout | Not Set | 344 | 2 | HoldingRegister | 860 | TRUE | 0 | 10 | 5 | ... 100 deg F ( ... 38 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 |  | 100 | 7071 |  | 1s | deg C | 507:62 |  | 38 | 7071 |  | 7069 | 4
York RTU.Cooling Control | Compressor VFD Alarm | CompVFD-Alarm | CompVFD-Alarm | 2645 | 445 | InputRegister | 861 | FALSE | 0 | 1 | 4 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7075 | 4
York RTU.Cooling Control | Saturated Suction Temperature 1 | SatSucTemp1 | Saturated Suction Temperature 1 | 2644 | 374 | InputRegister | 862 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7078 | 4
York RTU.Cooling Control | Saturated Discharge Temperature 1 | SatDischTemp1 | Saturated Discharge Temperature 1 | 2644 | 370 | InputRegister | 863 | FALSE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7079 | 4
York RTU.Cooling Control | Saturated Discharge Temperature 2 | SatDischTemp2 | Saturated Discharge Temperature 2 | 2644 | 371 | InputRegister | 864 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7080 | 4
York RTU.Cooling Control | Saturated Suction Temperature 2 | SatSucTemp2 | Saturated Suction Temperature 2 | 2644 | 375 | InputRegister | 865 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7081 | 4
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Discharge Line Pressure | DLP1 | Discharge Line Pressure 1 | 2644 | 378 | InputRegister | 866 | TRUE | 0 | 10 | 5 | 0 ... 750 psi (0 ... 5172 kPa) |  | FALSE | 4 | 10ths | psi | 507:56 | 0 | 750 |  |  | 1s | kPa | 507:54 | 0 | 5172 |  |  | 7024 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Discharge Line Temperature | DLT1 | Discharge Line Temperature 1 | 2644 | 380 | InputRegister | 867 | TRUE | 0 | 10 | 5 | -50 ... 250 deg F (-45.6 ... 121.1 deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 | -50 | 250 |  |  | 10ths | deg C | 507:62 | -45.6 | 121.1 |  |  | 7025 | 6
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Discharge Line Pressure | DLP2 | Discharge Line Pressure 2 | 2644 | 379 | InputRegister | 868 | TRUE | 0 | 10 | 5 | 0 ... 750 psi (0 ... 5172 kPa) |  | FALSE | 4 | 10ths | psi | 507:56 | 0 | 750 |  |  | 1s | kPa | 507:54 | 0 | 5172 |  |  | 7024 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Discharge Line Temperature | DLT2 | Discharge Line Temperature 2 | 2644 | 381 | InputRegister | 869 | TRUE | 0 | 10 | 5 | -50 ... 250 deg F (-45.6 ... 121.1 deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 | -50 | 250 |  |  | 10ths | deg C | 507:62 | -45.6 | 121.1 |  |  | 7025 | 8
York RTU.Cooling Control | Suction Superheat 1 | SucSuperheat1 | Suction Superheat 1 | 2644 | 366 | InputRegister | 870 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7082 | 4
York RTU.HVAC Zone | Space Temperature Setpoint Offset Range | SSORange | SSORange | 1709 | 50 | HoldingRegister | 871 | TRUE | 0 | 10 | 5 | 0 ... 5 delta deg F (0 ... 3 delta deg C) |  | TRUE | 4 | 10ths | delta deg F | 507:120 | 0 | 5 |  |  | 10ths | delta deg C | 507:359 | 0 | 3 |  |  | 7028 | 25
York RTU.Hot Gas Reheat | Operational Evap Temperature Sp | OprEvapTempSp | OprEvapTempSp | 1709 | 729 | InputRegister | 872 | TRUE | 0 | 10 | 5 | 0 ... 100 deg F (0 ... 100 deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 | 0 | 100 |  |  | 10ths | deg C | 507:62 | 0 | 100 |  |  | 7015 | 20
York RTU.Hot Gas Reheat | Operational HGR Temperature Sp | OprHGRTempSp | OprHGRTempSp | 1709 | 730 | InputRegister | 873 | TRUE | 0 | 10 | 5 | 0 ... 100 deg F (0 ... 100 deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 | 0 | 100 |  |  | 10ths | deg C | 507:62 | 0 | 100 |  |  | 7016 | 20
York RTU.Hot Gas Reheat | Dehum Evap Low Setpoint | DehumEvapLowSp | DehumEvapLowSp | 1709 | 725 | HoldingRegister | 874 | TRUE | 0 | 10 | 5 | 40 ... deg F (4 ... deg C) |  | TRUE | 4 | 10ths | deg F | 507:64 | 40 |  |  | 7017 | 10ths | deg C | 507:62 | 4 |  |  | 7017 | 7018 | 20
York RTU.Hot Gas Reheat | Dehumidify In Satisfied | SatisfiedDehum | SatisfiedDehum | 1709 | 726 | HoldingRegister | 875 | FALSE | 0 | 1 | 4 | 0 = False 1 = True |  | TRUE | 9 |  | False/True | 1701 | [5 empty] | False/True | 1701 |  |  |  |  | 7012 | 20
York RTU.Hot Gas Reheat | Modulating HGR Valve Full Open Allowed | ModHGRFullOpenAllowed | ModHGRFullOpenAllowed | 1709 | 728 | HoldingRegister | 876 | FALSE | 0 | 1 | 4 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7024 | 20
York RTU.Hot Gas Reheat | Condenser Fan 2 OAT Cutout Setpoint | CondFan2OATCutoutSP | CondFan2OATCutoutSP | 1709 | 732 | HoldingRegister | 877 | TRUE | 0 | 10 | 5 | 50 ... 80 deg F (10 ... 27 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 50 | 80 |  |  | 1s | deg C | 507:62 | 10 | 27 |  |  | 7023 | 20
York RTU.Cooling Control | Cooling Rapid Start Enable | ClgRapidStartEn | ClgRapidStartEn | 1709 | 767 | HoldingRegister | 878 | FALSE | 0 | 1 | 4 | 0 = Disable 1 = Enable |  | TRUE | 9 |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 |  |  |  |  | 7101 | 4
York RTU.Heating Control | Heating Rapid Start Enable | HtgRapidStartEn | HtgRapidStartEn | 1709 | 768 | HoldingRegister | 879 | FALSE | 0 | 1 | 4 | 0 = Disable 1 = Enable |  | TRUE | 9 |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 |  |  |  |  | 7056 | 13
York RTU.Heating Control | SZ VAV Operating Heating Setpoint | OprHtgDAT-SP | OprHtgDAT-SP | 2645 | 359 | InputRegister | 880 | TRUE | 0 | 10 | 5 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7049 | 13
York RTU.Economizer | Mixed Air Temperature Cooling Limit | MATClgLim | MATClgLim | 2645 | 293 | HoldingRegister | 881 | FALSE | 0 | 1 | 4 | 0 = Disable 1 = Enable |  | TRUE | 9 |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 |  |  |  |  | 7034 | 19
York RTU.Heat Pump Control | OAT Heat Pump Cutout | OATHPCutout | OATHPCutout | 1709 | 780 | HoldingRegister | 882 | TRUE | 0 | 10 | 5 | -20 ... 50 deg F (-29 ... 10 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | -20 | 50 |  |  | 1s | deg C | 507:62 | -29 | 10 |  |  | 7017 | 38
York RTU.Hot Gas Reheat | Use OprST for HGR | UseOprSTforHGR | UseOprSTforHGR | 1709 | 777 | HoldingRegister | 883 | FALSE | 0 | 1 | 4 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7031 | 20
York RTU.Hot Gas Reheat | Min Heating Setpoint | HGRModVlvMinSP | HGRModVlvMinSP | 1709 | 783 | HoldingRegister | 884 | TRUE | 0 | 10 | 5 | 0 ... 100 % |  | TRUE | 4 | 10ths | % | 507:98 | 0 | 100 |  |  | 10ths | % | 507:98 | 0 | 100 |  |  | 7014 | 20
York RTU.Hot Gas Reheat | Max Heating Setpoint | HGRModVlvMaxSP | HGRModVlvMaxSP | 1709 | 782 | HoldingRegister | 885 | TRUE | 0 | 10 | 5 | 0 ... 100 % |  | TRUE | 4 | 10ths | % | 507:98 | 0 | 100 |  |  | 10ths | % | 507:98 | 0 | 100 |  |  | 7013 | 20
York RTU.Hot Gas Reheat | HGR Humidity Setpoint Differential | HGR-Diff | HGR-Diff | 1709 | 669 | HoldingRegister | 886 | TRUE | 0 | 10 | 5 | 1 ... 10 % |  | TRUE | 4 | 1s | % | 507:98 | 1 | 10 |  |  | 1s | % | 507:98 | 1 | 10 |  |  | 7008 | 20
York RTU.Hot Gas Reheat | Use DFS For Dehum | UseDFSforDehum | UseDFSforDehum | 1709 | 721 | HoldingRegister | 887 | FALSE | 0 | 1 | 4 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7010 | 20
York RTU.Hot Gas Reheat | Aux Mode | HybridMode | HybridMode | 1709 | 781 | HoldingRegister | 888 | FALSE | 0 | 1 | 4 | 0 = Off 1 = On |  | TRUE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7009 | 20
York RTU.Cooling Control | Cooling Rapid Start Time | ClgRapidStartTime | ClgRapidStartTime | 1709 | 769 | HoldingRegister | 889 | FALSE | 0 | 1 | 4 | 2 ... 30 minutes |  | TRUE | 4 | 1s | minutes | 507:72 | 2 | 30 |  |  | 1s | minutes | 507:72 | 2 | 30 |  |  | 7102 | 4
York RTU.Heating Control | Heating Rapid Start Time | HtgRapidStartTime | HtgRapidStartTime | 1709 | 770 | HoldingRegister | 890 | FALSE | 0 | 1 | 4 | 2 ... 30 minutes |  | TRUE | 4 | 1s | minutes | 507:72 | 2 | 30 |  |  | 1s | minutes | 507:72 | 2 | 30 |  |  | 7057 | 13
York RTU.Cooling Control | A2L Leak Detector Alarm | A2LLeakAlarm | A2LLeakAlarm | 1709 | 787 | InputRegister | 891 | FALSE | 0 | 1 | 4 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7103 | 4
York RTU.Cooling Control | A2L Leak Detector Alarm-Lockout | A2LLeakAlarm-LO | A2LLeakAlarm-LO | 1709 | 791 | InputRegister | 892 | FALSE | 0 | 1 | 4 | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7106 | 4
York RTU.Cooling Control | Condensate Overflow Switch | COS | COS | 1709 | 788 | InputRegister | 893 | FALSE | 0 | 1 | 4 | 0 = Alarm 1 = Normal |  | FALSE | 9 |  | Alarm/Normal | 1696 | [5 empty] | Alarm/Normal | 1696 |  |  |  |  | 7108 | 4
York RTU.Hot Gas Reheat | Neutral Air ModHGR Enable | NeuAirModHGR-En | NeuAirModHGR-En | 1709 | 792 | HoldingRegister | 894 | FALSE | 0 | 1 | 4 | 0 = Disable 1 = Enable |  | TRUE | 9 |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 |  |  |  |  | 7032 | 20
York RTU.Hot Gas Reheat | Neutral Air ModHGR Offset | NeuAirModHGR-Off | NeuAirModHGR-Off | 1709 | 793 | HoldingRegister | 895 | TRUE | 0 | 10 | 5 | -10 ... 10 delta deg F (-6 ... 6 delta deg C) |  | TRUE | 4 | 1s | delta deg F | 507:120 | -10 | 10 |  |  | 1s | delta deg C | 507:359 | -6 | 6 |  |  | 7033 | 20
York RTU.Heat Pump Control | Dual Fuel OAT HP Cutout | DualFuelOATHPCutout | DualFuelOATHPCutout | 1709 | 796 | HoldingRegister | 896 | TRUE | 0 | 10 | 5 | 0 ... 65 deg F (-18 ... 18 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 0 | 65 |  |  | 1s | deg C | 507:62 | -18 | 18 |  |  | 7019 | 38
York RTU.Cooling Control | Condensate Alarm Enable | COS-En | COS-En | 1709 | 797 | HoldingRegister | 897 | FALSE | 0 | 1 | 4 | 0 = Disable 1 = Enable |  | TRUE | 9 |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 |  |  |  |  | 7107 | 4

## FC-Bus N2
Model Fullname | Attribute | Name (free) | Name (Dict) | Name SetId | Name EnumId | Object Type | Object Idx | Enum Set / Range | Remarks | Write-able | Data Type Id | Display Prec. (IP) | Unit (IP) | Unit Id (IP) | Min Value (IP) | Max Value (IP) | Min Prop. (IP) | Max Prop. (IP) | Display Prec. (SI) | Unit (SI) | Unit Id (SI) | Min Value (SI) | Max Value (SI) | Min Prop. (SI) | Max Prop. (SI) | Prop. Id | EM Object Id
York RTU.Heating Control | VAV Unoccupied Heating Setpoint | VHTGUNSP | VAV Unoccupied Heating Setpoint | 1675 | 207 | ADF | 119 | 45 ... 98 deg F (7 ... 36 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 45 | 98 |  |  | 1s | deg C | 507:62 | 7 | 36 |  |  | 7018 | 13
York RTU.Heating Control | VAV Operating Heating Setpoint | VOPHTGSP | VAV Operating Heating Setpoint | 1675 | 208 | ADF | 120 | deg F (deg C) |  | FALSE | 4 | 100ths | deg F | 507:64 |  |  |  |  | 100ths | deg C | 507:62 |  |  |  |  | 7019 | 13
York RTU.Heating Control | Morning Warmup Enabled | MRNWRMEN | Morning Warmup Enabled | 1675 | 209 | ADI | 73 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7020 | 13
York RTU.Heating Control | Morning Warmup/Return Air Temp Setpoint | WRMRATSP | Morning Warmup/Return Air Temp Setpoint | 1675 | 210 | ADF | 121 | 50 ... 85 deg F (10 ... 30 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 50 | 85 |  |  | 1s | deg C | 507:62 | 10 | 30 |  |  | 7021 | 13
York RTU.Heating Control | VAV Box Heat Command | VAVBOX-C | VAV Box Heat Command | 1675 | 211 | BO | 9 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7022 | 13
York RTU.Heating Control | CV Occupied Heating Setpoint | CVHTOCSP | CV Occupied Heating Setpoint | 1675 | 212 | ADF | 122 | 46 ... 99 deg F (8 ... 37 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 46 | 99 |  |  | 1s | deg C | 507:62 | 8 | 37 |  |  | 7023 | 13
York RTU.Heating Control | CV Unoccupied Heating Setpoint | CVHTUNSP | CV Unoccupied Heating Setpoint | 1675 | 213 | ADF | 123 | 45 ... 98 deg F (7 ... 36 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 45 | 98 |  |  | 1s | deg C | 507:62 | 7 | 36 |  |  | 7024 | 13
York RTU.Heating Control | CV Operating Heating Setpoint | CVHTOPSP | CV Operating Heating Setpoint | 1675 | 214 | ADF | 124 | deg F (deg C) |  | FALSE | 4 | 100ths | deg F | 507:64 |  |  |  |  | 100ths | deg C | 507:62 |  |  |  |  | 7025 | 13
York RTU.Heating Control | Morning Cooldown Enabled | MRNCLDEN | Morning Cooldown Enabled | 1675 | 375 | ADI | 74 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7034 | 13
York RTU.Heating Control | Morning Cooldown/Return Air Temp Setpoint | CLDRATSP | Morning Cooldown/Return Air Temp Setpoint | 1675 | 376 | ADF | 125 | 50 ... 85 deg F (10 ... 30 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 50 | 85 |  |  | 1s | deg C | 507:62 | 10 | 30 |  |  | 7035 | 13
York RTU.Heating Control | Optimal Start Enabled | OST-EN | Optimal Start Enabled | 1675 | 377 | ADI | 75 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7036 | 13
York RTU.Heating Control | Occupancy BI Enabled | OCCBI-EN | Occupancy BI Enabled | 1675 | 378 | ADI | 76 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7037 | 13
York RTU.Heating Control | Early Start Period | ERLYSTPD | Early Start Period | 1675 | 379 | ADF | 126 | 0 ... 120 minutes |  | TRUE | 4 | 1s | minutes | 507:72 | 0 | 120 |  |  | 1s | minutes | 507:72 | 0 | 120 |  |  | 7038 | 13
York RTU.Heating Control | Number of Limit Switches | NUMLIMSW | Number of Limit Switches | 1675 | 490 | ADF | 128 |  |  | FALSE | 4 | 1s |  | 507:95 |  |  |  |  | 1s |  | 507:95 |  |  |  |  | 7042 | 13
York RTU.Heating Control.Staged Heat Control.Heating Stage 1 | Heat Stage Command | H1-C | Heating Stage Command 1 | 1714 | 149 | BO | 10 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7000 | 15
York RTU.Heating Control.Staged Heat Control.Heating Stage 1 | Heat Stage Status | H1-S | Heating Stage 1 Status | 1714 | 103 | BI | 36 | 0 = Off-Idle 1 = On-Minimum Runtime Timer 2 = On-Normal Command 3 = Off-Heating Is Disabled ... |  | FALSE | 9 |  | SE RTU Heating Stage 1 Status | 1743 | [5 empty] | SE RTU Heating Stage 1 Status | 1743 |  |  |  |  | 7001 | 15
York RTU.Heating Control.Staged Heat Control.Heating Stage 1 | Heat Stage Accumulated Runtime | H1-RT | Heating Stage 1 Accumulated Runtime | 1714 | 108 | ADF | 129 | 0 ... 10000 hours |  | TRUE | 4 | 1s | hours | 507:71 | 0 | 10000 |  |  | 1s | hours | 507:71 | 0 | 10000 |  |  | 7006 | 15
York RTU.Heating Control.Staged Heat Control.Heating Stage 2 | Heat Stage Command | H2-C | Heating Stage Command 2 | 1714 | 150 | BO | 11 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7000 | 16
York RTU.Heating Control.Staged Heat Control.Heating Stage 2 | Heat Stage Status | H2-S | Heating Stage 2 Status | 1714 | 109 | BI | 37 | 0 = Off-Idle 1 = On-Minimum Runtime Timer 2 = On-Normal Command 3 = Off-Heating Is Disabled ... |  | FALSE | 9 |  | SE RTU Heating Stage 1 Status | 1743 | [5 empty] | SE RTU Heating Stage 1 Status | 1743 |  |  |  |  | 7001 | 16
York RTU.Heating Control.Staged Heat Control.Heating Stage 2 | Heat Stage Accumulated Runtime | H2-RT | Heating Stage 2 Accumulated Runtime | 1714 | 114 | ADF | 130 | 0 ... 10000 hours |  | TRUE | 4 | 1s | hours | 507:71 | 0 | 10000 |  |  | 1s | hours | 507:71 | 0 | 10000 |  |  | 7006 | 16
York RTU.Heating Control.Staged Heat Control.Heating Stage 3 | Heat Stage Command | H3-C | Heating Stage Command 3 | 1714 | 151 | BO | 12 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7000 | 17
York RTU.Heating Control.Staged Heat Control.Heating Stage 3 | Heat Stage Status | H3-S | Heating Stage 3 Status | 1714 | 115 | BI | 38 | 0 = Off-Idle 1 = On-Minimum Runtime Timer 2 = On-Normal Command 3 = Off-Heating Is Disabled ... |  | FALSE | 9 |  | SE RTU Heating Stage 1 Status | 1743 | [5 empty] | SE RTU Heating Stage 1 Status | 1743 |  |  |  |  | 7001 | 17
York RTU.Heating Control.Staged Heat Control.Heating Stage 3 | Heat Stage Accumulated Runtime | H3-RT | Heating Stage 3 Accumulated Runtime | 1714 | 120 | ADF | 131 | 0 ... 10000 hours |  | TRUE | 4 | 1s | hours | 507:71 | 0 | 10000 |  |  | 1s | hours | 507:71 | 0 | 10000 |  |  | 7006 | 17
York RTU.Heating Control.Hydronic Heat Control | Hydronic Heat Valve % Command | HWVLV-O | Hydronic Heat Valve % Command | 1675 | 218 | AO | 2 | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7000 | 18
York RTU.Heating Control.Hydronic Heat Control | Hydronic Heat Valve Reverse Acting | HWVLVREV | Hydronic Heat Valve Reverse Acting | 1675 | 219 | ADI | 79 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7001 | 18
York RTU.Heating Control.Hydronic Heat Control | Hydronic Heating Stage #1 Supply Air Setpoint | HWH1SASP | Hydronic Heating Stage #1 Supply Air Setpoint | 1675 | 220 | ADF | 132 | 80 ... 180 deg F (27 ... 82 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 80 | 180 |  |  | 1s | deg C | 507:62 | 27 | 82 |  |  | 7002 | 18
York RTU.Heating Control.Hydronic Heat Control | Hydronic Heating Stage #2 Supply Air Setpoint | HWH2SASP | Hydronic Heating Stage #2 Supply Air Setpoint | 1675 | 221 | ADF | 133 | 80 ... 180 deg F (27 ... 82 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 80 | 180 |  |  | 1s | deg C | 507:62 | 27 | 82 |  |  | 7003 | 18
York RTU.Heating Control.Hydronic Heat Control | Hydronic Heat SAT Tempering Enabled | SATEMPEN | Hydronic Heat SAT Tempering Enabled | 1675 | 222 | ADI | 80 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7004 | 18
York RTU.Heating Control.Hydronic Heat Control | Hydronic Heat SAT Tempering Setpoint | SATEMPSP | Hydronic Heat SAT Tempering Setpoint | 1675 | 223 | ADF | 134 | 40 ... 60 deg F (4 ... 15 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 40 | 60 |  |  | 1s | deg C | 507:62 | 4 | 15 |  |  | 7005 | 18
York RTU.Heat Pump Control | Defrost Curve Selection | DEFCURVE | Defrost Curve Selection | 1675 | 384 | ADI | 81 | 0 = Curve 1 1 = Curve 2 2 = Curve 3 3 = Curve 4 ... |  | TRUE | 9 |  | SE RTU Defrost Curves | 1665 | [5 empty] | SE RTU Defrost Curves | 1665 |  |  |  |  | 7004 | 38
York RTU.Heat Pump Control | Reversing Valve | REVVLV-C | Reversing Valve | 1675 | 482 | BO | 13 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7011 | 38
York RTU.Heat Pump Control | Auxiliary Heat | AUXHTG-C | Auxiliary Heat | 1675 | 483 | BO | 14 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7012 | 38
York RTU.Heat Pump Control | Mode | HP-MODE | Mode | 1675 | 484 | ADI | 83 | 0 = Heating 1 = Cooling |  | FALSE | 9 |  | Heating/Cooling | 350 | [5 empty] | Heating/Cooling | 350 |  |  |  |  | 7013 | 38
York RTU.Economizer | Economizer Enabled For Operation | ECON-EN | Economizer Enabled For Operation | 1675 | 50 | ADI | 84 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7000 | 19
York RTU.Economizer | Economizer Damper % Command | OAD-O | Economizer Damper % Command | 1675 | 51 | AO | 3 | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7001 | 19
York RTU.Economizer | Economizer Damper Minimum Position Low Speed Fan | LSFNMINPOS | Economizer Damper Minimum Position Low Speed Fan | 1675 | 327 | ADF | 135 | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7025 | 19
York RTU.Economizer | Econ Free Cooling Available | FCAVAIL | Econ Free Cooling Available | 1675 | 52 | ADI | 85 | 0 = No 1 = Yes |  | FALSE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7002 | 19
York RTU.Economizer | Economizer Status | ECON-S | Economizer Status | 1675 | 53 | ADI | 86 | 0 = Disabled 1 = Damper Not Functional 2 = Purge 3 = Unavailable-Sensor Fault ... |  | FALSE | 9 |  | SE RTU Economizer Status | 1738 | [5 empty] | SE RTU Economizer Status | 1738 |  |  |  |  | 7003 | 19
York RTU.Economizer | Free Cooling Current Mode | FCMODE | Free Cooling Current Mode | 1675 | 54 | ADI | 87 | 0 = Dry Bulb Temperature 1 = Differential Dry Bulb 2 = Single Enthalpy 3 = Dual Enthalpy 4 = Unreliable |  | FALSE | 9 |  | Actual Economizer Type Advanced | 3338 | [5 empty] | Actual Economizer Type Advanced | 3338 |  |  |  |  | 7004 | 19
York RTU.Economizer | Free Cooling Selection | FC-SEL | Free Cooling Selection | 1675 | 55 | ADI | 88 | 0 = Dry Bulb Temperature 1 = Single Enthalpy 2 = Dual Enthalpy 3 = Auto 4 = Differential Dry Bulb |  | TRUE | 9 |  | SE RTU Economizer Type | 3398 | [5 empty] | SE RTU Economizer Type | 3398 |  |  |  |  | 7005 | 19
York RTU.Economizer | Economizer Outdoor Air Temp Enable Setpoint | FCOATSP | Economizer Outdoor Air Temp Enable Setpoint | 1675 | 56 | ADF | 136 | 0 ... 80 deg F (-17.8 ... 27 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 0 | 80 |  |  | 1s | deg C | 507:62 | -17.8 | 27 |  |  | 7006 | 19
York RTU.Economizer | Economizer Outdoor Air Enthalpy Setpoint | FCOAENSP | Economizer Outdoor Air Enthalpy Setpoint | 1675 | 57 | ADF | 137 | 10 ... 50 Btu/lb dry air (23 ... 116 kJ/kg) |  | TRUE | 4 | 1s | Btu/lb dry air | 507:24 | 10 | 50 |  |  | 1s | kJ/kg | 507:125 | 23 | 116 |  |  | 7007 | 19
York RTU.Economizer | Low Ambient Economizer Setpoint | LOWAMBSP | Low Ambient Economizer Setpoint | 1675 | 58 | ADF | 138 | -20 ... 60 deg F (-29 ... 15 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | -20 | 60 |  |  | 1s | deg C | 507:62 | -29 | 15 |  |  | 7008 | 19
York RTU.Economizer | Low Ambient Economizer Minimum Position | LAMINPOS | Low Ambient Economizer Minimum Position | 1675 | 59 | ADF | 139 | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7009 | 19
York RTU.Economizer | Economizer Damper Position | OADMPPOS | Economizer Damper Position | 1675 | 335 | ADF | 141 | % open |  | FALSE | 4 | 1s | % open | 507:264 |  |  |  |  | 1s | % open | 507:264 |  |  |  |  | 7011 | 19
York RTU.Economizer | Mixed Air Temperature | MA-T | Mixed Air Temperature | 1675 | 62 | AI | 29 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7012 | 19
York RTU.Economizer | Supply Air Humidity | SA-H | Supply Air Humidity | 1675 | 224 | AI | 30 | %RH |  | FALSE | 4 | 1s | %RH | 507:29 |  |  |  |  | 1s | %RH | 507:29 |  |  |  |  | 7014 | 19
York RTU.Economizer | Return Air Enthalpy | RA-ENTH | Return Air Enthalpy | 1675 | 64 | ADF | 142 | Btu/lb (kJ/kg) |  | FALSE | 4 | 1s | Btu/lb | 507:117 |  |  |  |  | 1s | kJ/kg | 507:125 |  |  |  |  | 7015 | 19
York RTU.Economizer | Excess Outdoor Air | EXCOAALM | Excess Outdoor Air | 1675 | 293 | ADI | 89 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7018 | 19
York RTU.Economizer | Not Economizing When Should | NOTECALM | Not Economizing When Should | 1675 | 294 | ADI | 90 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7019 | 19
York RTU.Economizer | Damper Not Modulating | DMNOTALM | Damper Not Modulating | 1675 | 295 | ADI | 91 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7020 | 19
York RTU.Economizer | Economizing When Should Not | ECON-ALM | Economizing When Should Not | 1675 | 296 | ADI | 92 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7021 | 19
York RTU.Demand Ventilation Control | Demand Ventilation Mode of Operation | DMVMODE | Demand Ventilation Mode of Operation | 1675 | 225 | ADI | 93 | 0 = Disabled 1 = Controlled by IAQ 2 = Diff between IAQ and OAQ |  | TRUE | 9 |  | SE RTU DCV Mode | 1729 | [5 empty] | SE RTU DCV Mode | 1729 |  |  |  |  | 7000 | 23
York RTU.Demand Ventilation Control | Demand Ventilation Maximum Economizer Position | DMVMEPOS | Demand Ventilation Maximum Economizer Position | 1675 | 226 | ADF | 143 | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7001 | 23
York RTU.Demand Ventilation Control | Demand Ventilation Indoor Air Quality Setpoint | DMVIAQSP | Demand Ventilation Indoor Air Quality Setpoint | 1675 | 227 | ADF | 144 | 0 ... 5000 ppm |  | TRUE | 4 | 1s | ppm | 507:96 | 0 | 5000 |  |  | 1s | ppm | 507:96 | 0 | 5000 |  |  | 7002 | 23
York RTU.Demand Ventilation Control | Demand Ventilation Differential Setpoint | DVNTDFSP | Demand Ventilation Differential Setpoint | 1675 | 228 | ADF | 145 | 0 ... 5000 ppm |  | TRUE | 4 | 1s | ppm | 507:96 | 0 | 5000 |  |  | 1s | ppm | 507:96 | 0 | 5000 |  |  | 7003 | 23
York RTU.Exhaust Fan Control | Exhaust Fan Command | EXHFAN-C | Exhaust Fan Command | 1675 | 235 | BO | 15 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7001 | 21
York RTU.Exhaust Fan Control | Exhaust Fan VFD % Command | EFVFD-O | Exhaust Fan VFD % Command | 1675 | 236 | AO | 4 | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7002 | 21
York RTU.Exhaust Fan Control | Exhaust Fan Status | EXHFAN-S | Exhaust Fan Status | 1675 | 237 | BI | 39 | 0 = Off-Idle 1 = On-Normal Command 2 = Off-Disabled 3 = Off-VFD Fault ... |  | FALSE | 9 |  | SE RTU Exhaust Fan | 1745 | [5 empty] | SE RTU Exhaust Fan | 1745 |  |  |  |  | 7003 | 21
York RTU.Exhaust Fan Control | Exhaust Fan VFD Fault | EFVFDFLT | Exhaust Fan VFD Fault | 1675 | 238 | BI | 40 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7004 | 21
York RTU.Exhaust Fan Control | Exhaust Fan Accumulated Runtime | EF-RT | Exhaust Fan Accumulated Runtime | 1675 | 239 | ADF | 146 | hours |  | FALSE | 4 | 1s | hours | 507:71 |  |  |  |  | 1s | hours | 507:71 |  |  |  |  | 7005 | 21
York RTU.Exhaust Fan Control | Building Pressure Setpoint | BLDG-SP | Building Pressure Setpoint | 1675 | 240 | ADF | 147 | -0.25 ... 0.25 in wc (-0.07 ... 0.07 kPa) |  | TRUE | 4 | 1000ths | in wc | 507:58 | -0.25 | 0.25 |  |  | 1000ths | kPa | 507:54 | -0.07 | 0.07 |  |  | 7006 | 21
York RTU.Exhaust Fan Control | Building Static Pressure | BLDG-P | Building Static Pressure | 1675 | 241 | AI | 33 | in wc (kPa) |  | FALSE | 4 | 1000ths | in wc | 507:58 |  |  |  |  | 1000ths | kPa | 507:54 |  |  |  |  | 7007 | 21
York RTU.Exhaust Fan Control | Exhaust Damper % Command | EAD-O | Exhaust Damper % Command | 1675 | 242 | AO | 5 | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7008 | 21
York RTU.Exhaust Fan Control | Exhaust Damper Position for Exhaust Fan to Turn On | EXDMFNON | Exhaust Damper Position for Exhaust Fan to Turn On | 1675 | 243 | ADF | 149 | 20 ... 99 % |  | TRUE | 4 | 1s | % | 507:98 | 20 | 99 |  |  | 1s | % | 507:98 | 20 | 99 |  |  | 7009 | 21
York RTU.Exhaust Fan Control | Exhaust Damper Position for Exhaust Fan to Turn Off | EXDMFNOF | Exhaust Damper Position for Exhaust Fan to Turn Off | 1675 | 244 | ADF | 150 | 10 ... 89 % |  | TRUE | 4 | 1s | % | 507:98 | 10 | 89 |  |  | 1s | % | 507:98 | 10 | 89 |  |  | 7010 | 21
York RTU.Exhaust Fan Control | Economizer Damper Position for Exhaust Fan to Turn On | ECNDMPFNON | Economizer Damper Position for Exhaust Fan to Turn On | 1675 | 245 | ADF | 151 | 20 ... 99 % |  | TRUE | 4 | 1s | % | 507:98 | 20 | 99 |  |  | 1s | % | 507:98 | 20 | 99 |  |  | 7011 | 21
York RTU.Exhaust Fan Control | Economizer Damper Position for Exhaust Fan to Turn Off | ECNDMPFNOF | Economizer Damper Position for Exhaust Fan to Turn Off | 1675 | 246 | ADF | 152 | 10 ... 89 % |  | TRUE | 4 | 1s | % | 507:98 | 10 | 89 |  |  | 1s | % | 507:98 | 10 | 89 |  |  | 7012 | 21
York RTU.Exhaust Fan Control | ERV Enabled | ERV-EN | ERV Enabled | 1675 | 247 | ADI | 94 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7013 | 21
York RTU.Exhaust Fan Control | ERV Unoccupied Fan Enabled | ERVUNFNEN | ERV Unoccupied Fan Enabled | 1675 | 248 | ADI | 95 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7014 | 21
York RTU.Hot Gas Reheat | Hot Gas Reheat Enabled For Operation | HGR-EN | Hot Gas Reheat Enabled For Operation | 1675 | 249 | ADI | 96 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7000 | 20
York RTU.Hot Gas Reheat | Hot Gas Reheat Command | HGR-C | Hot Gas Reheat Command | 1675 | 250 | BO | 16 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7001 | 20
York RTU.Hot Gas Reheat | Hot Gas Reheat Status | HGR-S | Hot Gas Reheat Status | 1675 | 251 | BI | 41 | 0 = Off-Idle 1 = On-Normal Command 2 = On-Alternate Operation Command 3 = Off-Disabled |  | FALSE | 9 |  | SE RTU Hot Gas Reheat | 1744 | [5 empty] | SE RTU Hot Gas Reheat | 1744 |  |  |  |  | 7002 | 20
York RTU.Hot Gas Reheat | Hot Gas Reheat Humidity Setpoint | HGRHUMSP | Hot Gas Reheat Humidity Setpoint | 1675 | 252 | ADF | 153 | 0 ... 100 %RH |  | TRUE | 4 | 1s | %RH | 507:29 | 0 | 100 |  |  | 1s | %RH | 507:29 | 0 | 100 |  |  | 7003 | 20
York RTU.Hot Gas Reheat | Hot Gas Reheat Alternate Operation Enabled | HGRALTEN | Hot Gas Reheat Alternate Operation Enabled | 1675 | 253 | ADI | 97 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7004 | 20
York RTU.Air Monitor Station | Fresh Air Intake Setpoint | MOAFLWSP | Fresh Air Intake Setpoint | 1675 | 255 | ADF | 154 | 0 ... 50000 cfm (0 ... 25000 L/s) |  | TRUE | 4 | 10s | cfm | 507:84 | 0 | 50000 |  |  | 10s | L/s | 507:87 | 0 | 25000 |  |  | 7000 | 24
York RTU.Air Monitor Station | Fresh Air Intake Value | OA-FLOW | Fresh Air Intake Value | 1675 | 256 | ADF | 155 | cfm (L/s) |  | FALSE | 4 | 1s | cfm | 507:84 |  |  |  |  | 1s | L/s | 507:87 |  |  |  |  | 7001 | 24
York RTU.Air Monitor Station | Fresh Air Intake Max Sensor Range | MOARANGE | Fresh Air Intake Max Sensor Range | 1675 | 257 | ADF | 156 | 0 ... 50000 cfm (0 ... 25000 L/s) |  | TRUE | 4 | 10s | cfm | 507:84 | 0 | 50000 |  |  | 10s | L/s | 507:87 | 0 | 25000 |  |  | 7002 | 24
York RTU.Shutdown Input | Operating Purge Command | OPRPRG-C | Operating Purge Command | 1675 | 258 | ADI | 98 | 0 = False 1 = True |  | FALSE | 9 |  | False/True | 1701 | [5 empty] | False/True | 1701 |  |  |  |  | 7000 | 27
York RTU.Shutdown Input | Purge Command Source | PRGCMSRC | Purge Command Source | 1675 | 259 | ADI | 99 | 0 = Unreliable 1 = Local Input 2 = Network Sensor 3 = High Priority ... |  | FALSE | 9 |  | Effective Input Source 2 | 1732 | [5 empty] | Effective Input Source 2 | 1732 |  |  |  |  | 7001 | 27
York RTU.Shutdown Input | Local Purge Command Input | PURGE-S | Local Purge Command Input | 1675 | 260 | ADI | 100 | 0 = False 1 = True |  | FALSE | 9 |  | False/True | 1701 | [5 empty] | False/True | 1701 |  |  |  |  | 7002 | 27
York RTU.Shutdown Input | Network Override Purge Command | NETPURGE | Network Override Purge Command | 1675 | 261 | ADI | 101 | 0 = False 1 = True |  | TRUE | 9 |  | False/True | 1701 | [5 empty] | False/True | 1701 |  |  |  |  | 7003 | 27
York RTU.Shutdown Input | Shutdown Input/Smoke Detector | SMOKE-A | Shutdown Input/Smoke Detector | 1675 | 262 | ADI | 102 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7004 | 27
York RTU.System Controllers | Econ Controller | ECONCNT | Econ Controller | 1675 | 315 | ADI | 103 | 0 = Not Present 1 = Offline 2 = Online |  | FALSE | 9 |  | EIO Connection Status | 1662 | [5 empty] | EIO Connection Status | 1662 |  |  |  |  | 7004 | 29
York RTU.System Controllers | 4 Stage Controller | 4STGCNT | 4 Stage Controller | 1675 | 316 | ADI | 104 | 0 = Not Present 1 = Offline 2 = Online |  | FALSE | 9 |  | EIO Connection Status | 1662 | [5 empty] | EIO Connection Status | 1662 |  |  |  |  | 7005 | 29
York RTU.System Controllers | FDD Manager Controller | FDDMCNT | FDD Manager Controller | 1675 | 317 | ADI | 105 | 0 = Not Present 1 = Offline 2 = Online |  | FALSE | 9 |  | EIO Connection Status | 1662 | [5 empty] | EIO Connection Status | 1662 |  |  |  |  | 7006 | 29
York RTU.System Controllers | FDD Subordinate Controller | FDDSCNT | FDD Subordinate Controller | 1675 | 318 | ADI | 106 | 0 = Not Present 1 = Offline 2 = Online |  | FALSE | 9 |  | EIO Connection Status | 1662 | [5 empty] | EIO Connection Status | 1662 |  |  |  |  | 7007 | 29
York RTU | Hardware Reset | HDW-RST | Hardware Reset | 1675 | 499 | ADI | 109 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7021 | 1
York RTU.HVAC Zone | Load Shed Active | LOADSHEDEN | Load Shed Active | 1675 | 421 | ADI | 110 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7043 | 25
York RTU.HVAC Zone | Load Shed Rate Limit | LOADSHEDRT | Load Shed Rate Limit | 1675 | 422 | ADF | 157 | 0 ... 1 deg F/min (0 ... 1 deg C/min) |  | TRUE | 4 | 1000ths | deg F/min | 507:94 | 0 | 1 |  |  | 1000ths | deg C/min | 507:92 | 0 | 1 |  |  | 7044 | 25
York RTU.HVAC Zone | Load Shed Adjust | LOADSHEDAD | Load Shed Adjust | 1675 | 423 | ADF | 158 | 0 ... 8 delta deg F (0 ... 4.4 delta deg C) |  | TRUE | 4 | 10ths | delta deg F | 507:120 | 0 | 8 |  |  | 10ths | delta deg C | 507:359 | 0 | 4.4 |  |  | 7045 | 25
York RTU.HVAC Zone | Direct Loadshed | DIRLOADSHD | Direct Loadshed | 1675 | 497 | ADI | 111 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7061 | 25
York RTU.HVAC Zone | Redline | REDLINE | Redline | 1675 | 500 | ADI | 112 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7062 | 25
York RTU.HVAC Zone | PID Tuning Reset | PIDTUNERST | PID Tuning Reset | 1675 | 631 | ADI | 113 | 0 = False 1 = True |  | TRUE | 9 |  | False/True | 1701 | [5 empty] | False/True | 1701 |  |  |  |  | 7063 | 25
York RTU.Fan Control | SZ VAV Minimum Fan Speed | SZVMNFNSPD | SZ VAV Minimum Fan Speed | 1675 | 627 | ADF | 159 | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7037 | 3
York RTU.Cooling Control | DAT Cooling Min SP | DATCLMSP | DAT Cooling Min SP | 1675 | 494 | ADF | 160 | 50 ... 60 deg F (9.5 ... 15.6 deg C) |  | TRUE | 4 | 10ths | deg F | 507:64 | 50 | 60 |  |  | 10ths | deg C | 507:62 | 9.5 | 15.6 |  |  | 7045 | 4
York RTU.Cooling Control | Staged Cooling Command | STGCLGCMD | Staged Cooling Command | 1675 | 628 | ADF | 165 | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7047 | 4
York RTU.Heating Control | DAT Max Heating SP | DATMHTSP | DAT Max Heating SP | 1675 | 492 | ADF | 161 | 80 ... 110 deg F (26.6 ... 43.4 deg C) |  | TRUE | 4 | 10ths | deg F | 507:64 | 80 | 110 |  |  | 10ths | deg C | 507:62 | 26.6 | 43.4 |  |  | 7043 | 13
York RTU.Heating Control | DAT Satisfied SP | DATSATSP | DAT Satisfied SP | 1675 | 493 | ADF | 162 | 65 ... 75 deg F (18.3 ... 23.9 deg C) |  | TRUE | 4 | 10ths | deg F | 507:64 | 65 | 75 |  |  | 10ths | deg C | 507:62 | 18.3 | 23.9 |  |  | 7044 | 13
York RTU.Heating Control | Staged Heating Command | STGHTGCMD | Staged Heating Command | 1675 | 629 | ADF | 166 | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7045 | 13
York RTU.Economizer | Economizer Minimum Position Setpoint | MINOA-PCT | Economizer Minimum Position Setpoint | 1675 | 292 | ADF | 163 | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7017 | 19
York RTU.Economizer | Economizer Fault Detection Enable | ECNFLTDET | Economizer Fault Detection Enable | 1675 | 626 | ADI | 115 | 0 = Disable 1 = Enable |  | TRUE | 9 |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 |  |  |  |  | 7028 | 19
York RTU.Hot Gas Reheat | HGR Unoccupied Humidity Setpoint | HGRUNCHSP | HGR Unoccupied Humidity Setpoint | 1675 | 602 | ADF | 164 | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7006 | 20
York RTU.Hot Gas Reheat | HGR Enabled for Unoccupied Operation | HGRUNC-EN | HGR Enabled for Unoccupied Operation | 1675 | 603 | ADI | 116 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7007 | 20
York RTU.Cooling Control | VAV Unoccupied Cooling Setpoint | VCLGUNCSP | VAV Unoccupied Cooling Setpoint | 1675 | 740 | ADF | 168 | 46 ... 99 deg F (8 ... 37 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 46 | 99 |  |  | 1s | deg C | 507:62 | 8 | 37 |  |  | 7052 | 4
York RTU.Air Monitor Station | Fresh Air Intake Enable | FRSHAIR-EN | Fresh Air Intake Enable | 1675 | 741 | ADI | 117 | 0 = Disable 1 = Enable |  | TRUE | 9 |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 |  |  |  |  | 7004 | 24
York RTU.Cooling Control | Cooling Adaptive Tuning Enable | CLADTNEN | Cooling Adaptive Tuning Enable | 1675 | 486 | ADI | 35 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7043 | 4
York RTU.Cooling Control | SZ VAV Occupied Cooling Setpoint | SZVCLGOCSP | SZ VAV Occupied Cooling Setpoint | 1675 | 644 | ADF | 169 | 45 ... 98 deg F (7 ... 36 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 45 | 98 |  |  | 1s | deg C | 507:62 | 7 | 36 |  |  | 7048 | 4
York RTU.Cooling Control | SZ VAV Unoccupied Cooling Setpoint | SZVCLGUNSP | SZ VAV Unoccupied Cooling Setpoint | 1675 | 646 | ADF | 170 | 45 ... 98 deg F (7 ... 36 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 45 | 98 |  |  | 1s | deg C | 507:62 | 7 | 36 |  |  | 7049 | 4
York RTU.Cooling Control | SZ VAV Operating Cooling Setpoint | OPSZVCLGSP | SZ VAV Operating Cooling Setpoint | 1675 | 648 | ADF | 171 | deg F (deg C) |  | FALSE | 4 | 100ths | deg F | 507:64 |  |  |  |  | 100ths | deg C | 507:62 |  |  |  |  | 7061 | 4
York RTU.Heating Control | Heating Adaptive Tuning Enable | HTADTNEN | Heating Adaptive Tuning Enable | 1675 | 485 | ADI | 78 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7041 | 13
York RTU.Heating Control | SZ VAV Occupied Heating Setpoint | SZVHTGOCSP | SZ VAV Occupied Heating Setpoint | 1675 | 643 | ADF | 172 | 46 ... 99 deg F (8 ... 37 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 46 | 99 |  |  | 1s | deg C | 507:62 | 8 | 37 |  |  | 7047 | 13
York RTU.Heating Control | SZ VAV Unoccupied Heating Setpoint | SZVHTGUNSP | SZ VAV Unoccupied Heating Setpoint | 1675 | 645 | ADF | 173 | 45 ... 98 deg F (7 ... 36 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 45 | 98 |  |  | 1s | deg C | 507:62 | 7 | 36 |  |  | 7048 | 13
York RTU | SZ VAV Enabled | SZVAVEN | SZ VAV Enabled | 1675 | 491 | ADI | 118 | 0 = Off 1 = On |  | TRUE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7020 | 1
York RTU.Fan Control | Fan Control Type | FANCTLTYPE | Fan Control Type | 1675 | 173 | ADI | 119 | 0 = Single Speed 1 = Not Used 2 = Fixed Variable 3 = Variable Speed |  | TRUE | 9 |  | SE RTU Fan Control Type | 1619 | [5 empty] | SE RTU Fan Control Type | 1619 |  |  |  |  | 7005 | 3
York RTU.Cooling Control | Number of Cooling Stages Installed | NUMCLGSTGS | Number of Cooling Stages Installed | 1675 | 67 | ADI | 120 | 1 ... 4 |  | TRUE | 16 | 1s |  | 507:95 | 1 | 4 |  |  | 1s |  | 507:95 | 1 | 4 |  |  | 7001 | 4
York RTU.Cooling Control | Lead/Lag Equalize Cooling Stage Runtime Enabled | LEADLAG-EN | Lead/Lag Equalize Cooling Stage Runtime Enabled | 1675 | 72 | ADI | 121 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7004 | 4
York RTU.Cooling Control | Unit Type | UNITTYPE | Unit Type | 1675 | 130 | ADI | 122 | 0 = Not Used 1 = Package Cool 2 = Package HP 3 = Split Cool ... |  | TRUE | 9 |  | SE RTU Equipment Type | 1685 | [5 empty] | SE RTU Equipment Type | 1685 |  |  |  |  | 7020 | 4
York RTU.Cooling Control | EER | EER | EER | 1675 | 131 | ADF | 175 | 0 ... 20 |  | TRUE | 4 | 1s |  | 507:95 | 0 | 20 |  |  | 1s |  | 507:95 | 0 | 20 |  |  | 7021 | 4
York RTU.Cooling Control | Refrigerant Type | REFRIGTYPE | Refrigerant Type | 1675 | 133 | ADI | 123 | 0 = R22 1 = R12 2 = R500 3 = R134A ... |  | TRUE | 9 |  | SE RTU Refrigerant Type | 1682 | [5 empty] | SE RTU Refrigerant Type | 1682 |  |  |  |  | 7023 | 4
York RTU.Cooling Control | Evaporator Coil Type | EVPCOILTYP | Evaporator Coil Type | 1675 | 101 | ADI | 124 | 0 = MicroChannel 1 = Tube and Fin |  | TRUE | 9 |  | Cooling Coil Type | 1722 | [5 empty] | Cooling Coil Type | 1722 |  |  |  |  | 7025 | 4
York RTU.Cooling Control.DX Cooling Circuit 1 | Hot Gas Bypass Present | HGBP-INST | Hot Gas Bypass Present | 1675 | 89 | ADI | 125 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7004 | 5
York RTU.Cooling Control | Unit Capacity | UNITCAP | Unit Capacity | 1675 | 371 | ADF | 176 | 0 ... 130 tons refr (0 ... 460 kW) |  | TRUE | 4 | 10ths | tons refr | 507:52 | 0 | 130 |  |  | 10ths | kW | 507:48 | 0 | 460 |  |  | 7038 | 4
York RTU.Economizer | EconMech Setup | ECNMECHSTP | EconMech Setup | 1675 | 498 | ADI | 126 | 0 = Option A 1 = Option B |  | TRUE | 9 |  | SE RTU EconMech Setup | 1752 | [5 empty] | SE RTU EconMech Setup | 1752 |  |  |  |  | 7027 | 19
York RTU.Hot Gas Reheat | Hot Gas Reheat Alternate Operation Writeable | HGRALTWRIT | Hot Gas Reheat Alternate Operation Writeable | 1675 | 254 | ADI | 127 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7005 | 20
York RTU | Unit Enable | UNITEN | Unit Enable | 1675 | 462 | ADI | 128 | 0 = Shutdown 1 = Enable |  | TRUE | 9 |  | Shutdown/Enable | 349 | [5 empty] | Shutdown/Enable | 349 |  |  |  |  | 7019 | 1
York RTU | Exhaust Type | EXFTYPE | Exhaust Type | 1675 | 147 | ADI | 129 | 0 = None 1 = Non-Modulating 2 = Modulating Damper 3 = Variable Frequency Fan |  | TRUE | 9 |  | SE RTU Exhaust Setup | 1639 | [5 empty] | SE RTU Exhaust Setup | 1639 |  |  |  |  | 7008 | 1
York RTU.Thermostat Control | Thermostat Only Control Enabled | TSTATONLY | Thermostat Only Control Enabled | 1675 | 160 | BI | 42 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7010 | 2
York RTU.Fan Control | Air Proving Switch Setup | APSSETUP | Air Proving Switch Setup | 1675 | 174 | ADI | 130 | 0 = Constant Volume 1 = Variable Volume 2 = None |  | TRUE | 9 |  | Fan Setup | 1622 | [5 empty] | Fan Setup | 1622 |  |  |  |  | 7006 | 3
York RTU.Fan Control | Fan Off Delay for Cool | FNOFFDLCL | Fan Off Delay for Cool | 1675 | 177 | ADI | 131 | 0 ... 255 seconds |  | TRUE | 17 | 1s | seconds | 507:73 | 0 | 255 |  |  | 1s | seconds | 507:73 | 0 | 255 |  |  | 7009 | 3
York RTU.Fan Control | Fan On Delay for Heat | FNONDLHT | Fan On Delay for Heat | 1675 | 178 | ADI | 132 | 0 ... 30 seconds |  | TRUE | 17 | 1s | seconds | 507:73 | 0 | 30 |  |  | 1s | seconds | 507:73 | 0 | 30 |  |  | 7010 | 3
York RTU.Fan Control | Fan Off Delay for Heat | FNOFFDLHT | Fan Off Delay for Heat | 1675 | 179 | ADI | 133 | 0 ... 255 seconds |  | TRUE | 17 | 1s | seconds | 507:73 | 0 | 255 |  |  | 1s | seconds | 507:73 | 0 | 255 |  |  | 7011 | 3
York RTU.Cooling Control | Low Ambient Fan Pre-run Time For Cooling | LOAMBFPRCL | Low Ambient Fan Pre-run Time For Cooling | 1675 | 73 | ADI | 134 | 0 ... 255 seconds |  | TRUE | 17 | 1s | seconds | 507:73 | 0 | 255 |  |  | 1s | seconds | 507:73 | 0 | 255 |  |  | 7005 | 4
York RTU.Cooling Control | Low Ambient Cooling Stages 10 on 5 off Setpoint | LA10ON5OFF | Low Ambient Cooling Stages 10 on 5 off Setpoint | 1675 | 78 | ADF | 177 | 0 ... 60 deg F (-18 ... 15 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 0 | 60 |  |  | 1s | deg C | 507:62 | -18 | 15 |  |  | 7010 | 4
York RTU.Cooling Control | Freeze Condition Setpoint | FREEZE-SP | Freeze Condition Setpoint | 1675 | 99 | ADF | 178 | 20 ... 32 deg F (-7 ... 0 deg C) |  | TRUE | 4 | 10ths | deg F | 507:64 | 20 | 32 |  |  | 10ths | deg C | 507:62 | -7 | 0 |  |  | 7017 | 4
York RTU.Cooling Control | Subcooling Goal | SUBCLGOAL | Subcooling Goal | 1675 | 132 | ADF | 179 | -10 ... 20 deg F (-23 ... -6 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | -10 | 20 |  |  | 1s | deg C | 507:62 | -23 | -6 |  |  | 7022 | 4
York RTU.Cooling Control | High Side Port Location | HIPORTLOC | High Side Port Location | 1675 | 134 | ADI | 135 | 0 = Liquid 1 = Discharge |  | TRUE | 9 |  | SE RTU High Side Port | 1681 | [5 empty] | SE RTU High Side Port | 1681 |  |  |  |  | 7024 | 4
York RTU.Cooling Control | Condenser Coil Type | CNDCOILTYP | Condenser Coil Type | 1675 | 103 | ADI | 136 | 0 = MicroChannel 1 = Tube and Fin |  | TRUE | 9 |  | Cooling Coil Type | 1722 | [5 empty] | Cooling Coil Type | 1722 |  |  |  |  | 7026 | 4
York RTU.Cooling Control | Indoor Metering Device Type | INMDTYPE | Indoor Metering Device Type | 1675 | 135 | ADI | 137 | 0 = TxV 1 = FO 2 = TxV Or FO 3 = n |  | TRUE | 9 |  | SE RTU Expansion Device | 1684 | [5 empty] | SE RTU Expansion Device | 1684 |  |  |  |  | 7027 | 4
York RTU.Cooling Control | Outdoor Metering Device Type | OUTMDTYPE | Outdoor Metering Device Type | 1675 | 136 | ADI | 138 | 0 = TxV 1 = FO 2 = TxV Or FO 3 = n |  | TRUE | 9 |  | SE RTU Expansion Device | 1684 | [5 empty] | SE RTU Expansion Device | 1684 |  |  |  |  | 7028 | 4
York RTU.Cooling Control | Fan Power | FANPOWER | Fan Power | 1675 | 372 | ADF | 180 | 0 ... 19 kW |  | TRUE | 4 | 10ths | kW | 507:48 | 0 | 19 |  |  | 10ths | kW | 507:48 | 0 | 19 |  |  | 7039 | 4
York RTU.Cooling Control | Super Heat Goal | SUPRHTGOAL | Super Heat Goal | 1675 | 373 | ADF | 181 | 10 ... 30 deg F (-12.2 ... -1.1 deg C) |  | TRUE | 4 | 10ths | deg F | 507:64 | 10 | 30 |  |  | 10ths | deg C | 507:62 | -12.2 | -1.1 |  |  | 7040 | 4
York RTU.Cooling Control | Pump Out Enable | PMPOUT-EN | Pump Out Enable | 1675 | 619 | ADI | 139 | 0 = Disable 1 = Enable |  | TRUE | 9 |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 |  |  |  |  | 7046 | 4
York RTU.Cooling Control | Low Ambient Enabled | LOWAMB-EN | Low Ambient Enabled | 1675 | 649 | ADI | 140 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7051 | 4
York RTU.Heating Control.Staged Heat Control | Number of Heating Stages Installed | NUMHTGSTGS | Number of Heating Stages Installed | 1675 | 215 | ADI | 141 | 0 ... 3 |  | TRUE | 16 | 1s |  | 507:95 | 0 | 3 |  |  | 1s |  | 507:95 | 0 | 3 |  |  | 7000 | 14
York RTU.Economizer | FDD Economizer Alarm Delay | ECONALMDLY | FDD Economizer Alarm Delay | 1675 | 633 | ADF | 182 | 0 ... 3600 seconds |  | TRUE | 4 | 10s | seconds | 507:73 | 0 | 3600 |  |  | 10s | seconds | 507:73 | 0 | 3600 |  |  | 7029 | 19
York RTU.Economizer | FDD Economizer Damper Allowed Error | ECONPOSERR | FDD Economizer Damper Allowed Error | 1675 | 634 | ADF | 183 | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7030 | 19
York RTU.Economizer | FDD Damper Min Position Tolerance | ECONMINERR | FDD Damper Min Position Tolerance | 1675 | 635 | ADF | 184 | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7031 | 19
York RTU.Heat Pump Control | Number of Heat Pump Stages Installed | NUMHPMPSTG | Number of Heat Pump Stages Installed | 1675 | 380 | ADF | 185 | 0 ... 2 |  | TRUE | 4 | 1s |  | 507:95 | 0 | 2 |  |  | 1s |  | 507:95 | 0 | 2 |  |  | 7000 | 38
York RTU.Cooling Control | SZ VAV Cooling Load | SZVAVCLGLD | SZ VAV Cooling Load | 1675 | 744 | ADF | 186 | % |  | FALSE | 4 | 10ths | % | 507:98 |  |  |  |  | 10ths | % | 507:98 |  |  |  |  | 7053 | 4
York RTU.Heating Control | SZ VAV Heating Load | SZVAVHTGLD | SZ VAV Heating Load | 1675 | 745 | ADF | 187 | % |  | FALSE | 4 | 10ths | % | 507:98 |  |  |  |  | 10ths | % | 507:98 |  |  |  |  | 7050 | 13
York RTU.Cooling Control.DX Cooling Circuit 1 | Compressor Stage Accumulated Runtime | C1-RT | Compressor Stage Accumulated Runtime 1 | 1714 | 43 | ADF | 56 | 0 ... 10000 hours |  | TRUE | 4 | 1s | hours | 507:71 | 0 | 10000 |  |  | 1s | hours | 507:71 | 0 | 10000 |  |  | 7005 | 5
York RTU.Cooling Control.DX Cooling Circuit 1 | Min On Time Remaining | C1ONTMR | Min On Time Remaining 1 | 1714 | 41 | ADI | 37 | seconds |  | FALSE | 17 | 1s | seconds | 507:73 |  |  |  |  | 1s | seconds | 507:73 |  |  |  |  | 7007 | 5
York RTU.Cooling Control.DX Cooling Circuit 1 | Anti-Short Cycle Delay Time Remaining | C1ASCDTM | Anti-Short Cycle Delay Time Remaining 1 | 1714 | 42 | ADI | 38 | seconds |  | FALSE | 17 | 1s | seconds | 507:73 |  |  |  |  | 1s | seconds | 507:73 |  |  |  |  | 7008 | 5
York RTU.Cooling Control.DX Cooling Circuit 1 | High Pressure Limit | HPS1-S | High Pressure Limit 1 | 1714 | 121 | BI | 15 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7009 | 5
York RTU.Cooling Control.DX Cooling Circuit 1 | High Pressure Lockout | HPS1-LO | High Pressure Lockout 1 | 1714 | 129 | ADI | 39 | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7010 | 5
York RTU.Cooling Control.DX Cooling Circuit 1 | Low Pressure Limit | LPS1-S | Low Pressure Limit 1 | 1714 | 122 | BI | 16 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7011 | 5
York RTU.Cooling Control.DX Cooling Circuit 1 | Low Pressure Lockout | LPS1-LO | Low Pressure Lockout 1 | 1714 | 130 | ADI | 40 | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7012 | 5
York RTU.Cooling Control.DX Cooling Circuit 1 | Freeze Condition | FS1-S | Freeze Condition 1 | 1714 | 131 | BI | 17 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7013 | 5
York RTU.Cooling Control.DX Cooling Circuit 1 | Freeze Condition Lockout | FS1-LO | Freeze Condition Lockout 1 | 1714 | 132 | ADI | 41 | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7014 | 5
York RTU.Cooling Control.DX Cooling Circuit 1 | Evaporator Coil Temp | EVAP1-T | Evaporator Coil Temp 1 | 1714 | 44 | AI | 5 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7015 | 5
York RTU.Cooling Control.DX Cooling Circuit 1 | Condenser Coil Temp | COND1-T | Condenser Coil Temp 1 | 1714 | 45 | AI | 6 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7016 | 5
York RTU.Cooling Control.DX Cooling Circuit 2 | Compressor Stage Command | COMP2-C | Compressor Stage Command 2 | 1714 | 146 | BO | 6 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7001 | 7
York RTU.Cooling Control.DX Cooling Circuit 2 | Compressor Stage Status | COMP2-S | Compressor Stage 2 Status | 1714 | 55 | BI | 18 | 0 = Off-Idle 1 = On-Minimum On Time 2 = On-Normal Command 3 = Off-Cooling Is Disabled ... |  | FALSE | 9 |  | SE RTU DX Cooling Circuit 1 Status | 1741 | [5 empty] | SE RTU DX Cooling Circuit 1 Status | 1741 |  |  |  |  | 7002 | 7
York RTU.Cooling Control.DX Cooling Circuit 2 | Compressor Stage Enabled | C2-EN | Compressor Stage 2 Enabled | 1714 | 56 | ADI | 42 | 0 = Yes 1 = No |  | TRUE | 9 |  | Yes/No | 1698 | [5 empty] | Yes/No | 1698 |  |  |  |  | 7003 | 7
York RTU.Cooling Control.DX Cooling Circuit 2 | Compressor Stage Accumulated Runtime | C2-RT | Compressor Stage Accumulated Runtime 2 | 1714 | 59 | ADF | 57 | 0 ... 10000 hours |  | TRUE | 4 | 1s | hours | 507:71 | 0 | 10000 |  |  | 1s | hours | 507:71 | 0 | 10000 |  |  | 7005 | 7
York RTU.Cooling Control.DX Cooling Circuit 2 | Min On Time Remaining | C2ONTMR | Min On Time Remaining 2 | 1714 | 57 | ADI | 43 | seconds |  | FALSE | 17 | 1s | seconds | 507:73 |  |  |  |  | 1s | seconds | 507:73 |  |  |  |  | 7007 | 7
York RTU.Cooling Control.DX Cooling Circuit 2 | Anti-Short Cycle Delay Time Remaining | C2ASCDTM | Anti-Short Cycle Delay Time Remaining 2 | 1714 | 58 | ADI | 44 | seconds |  | FALSE | 17 | 1s | seconds | 507:73 |  |  |  |  | 1s | seconds | 507:73 |  |  |  |  | 7008 | 7
York RTU.Cooling Control.DX Cooling Circuit 2 | High Pressure Limit | HPS2-S | High Pressure Limit 2 | 1714 | 123 | BI | 19 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7009 | 7
York RTU.Cooling Control.DX Cooling Circuit 2 | High Pressure Lockout | HPS2-LO | High Pressure Lockout 2 | 1714 | 133 | ADI | 45 | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7010 | 7
York RTU.Cooling Control.DX Cooling Circuit 2 | Low Pressure Limit | LPS2-S | Low Pressure Limit 2 | 1714 | 124 | BI | 20 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7011 | 7
York RTU.Cooling Control.DX Cooling Circuit 2 | Low Pressure Lockout | LPS2-LO | Low Pressure Lockout 2 | 1714 | 134 | ADI | 46 | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7012 | 7
York RTU.Cooling Control.DX Cooling Circuit 2 | Freeze Condition | FS2-S | Freeze Condition 2 | 1714 | 135 | BI | 21 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7013 | 7
York RTU.Cooling Control.DX Cooling Circuit 2 | Freeze Condition Lockout | FS2-LO | Freeze Condition Lockout 2 | 1714 | 136 | ADI | 47 | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7014 | 7
York RTU.Cooling Control.DX Cooling Circuit 2 | Evaporator Coil Temp | EVAP2-T | Evaporator Coil Temp 2 | 1714 | 60 | AI | 7 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7015 | 7
York RTU.Cooling Control.DX Cooling Circuit 2 | Condenser Coil Temp | COND2-T | Condenser Coil Temp 2 | 1714 | 61 | AI | 8 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7016 | 7
York RTU.Cooling Control.DX Cooling Circuit 3 | Compressor Stage Command | COMP3-C | Compressor Stage Command 3 | 1714 | 147 | BO | 7 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7001 | 9
York RTU.Cooling Control.DX Cooling Circuit 3 | Compressor Stage Status | COMP3-S | Compressor Stage 3 Status | 1714 | 71 | BI | 22 | 0 = Off-Idle 1 = On-Minimum On Time 2 = On-Normal Command 3 = Off-Cooling Is Disabled ... |  | FALSE | 9 |  | SE RTU DX Cooling Circuit 1 Status | 1741 | [5 empty] | SE RTU DX Cooling Circuit 1 Status | 1741 |  |  |  |  | 7002 | 9
York RTU.Cooling Control.DX Cooling Circuit 3 | Compressor Stage Enabled | C3-EN | Compressor Stage 3 Enabled | 1714 | 72 | ADI | 48 | 0 = Yes 1 = No |  | TRUE | 9 |  | Yes/No | 1698 | [5 empty] | Yes/No | 1698 |  |  |  |  | 7003 | 9
York RTU.Cooling Control.DX Cooling Circuit 3 | Compressor Stage Accumulated Runtime | C3-RT | Compressor Stage Accumulated Runtime 3 | 1714 | 75 | ADF | 58 | 0 ... 10000 hours |  | TRUE | 4 | 1s | hours | 507:71 | 0 | 10000 |  |  | 1s | hours | 507:71 | 0 | 10000 |  |  | 7005 | 9
York RTU.Cooling Control.DX Cooling Circuit 3 | Min On Time Remaining | C3ONTMR | Min On Time Remaining 3 | 1714 | 73 | ADI | 49 | seconds |  | FALSE | 17 | 1s | seconds | 507:73 |  |  |  |  | 1s | seconds | 507:73 |  |  |  |  | 7007 | 9
York RTU.Cooling Control.DX Cooling Circuit 3 | Anti-Short Cycle Delay Time Remaining | C3ASCDTM | Anti-Short Cycle Delay Time Remaining 3 | 1714 | 74 | ADI | 50 | seconds |  | FALSE | 17 | 1s | seconds | 507:73 |  |  |  |  | 1s | seconds | 507:73 |  |  |  |  | 7008 | 9
York RTU.Cooling Control.DX Cooling Circuit 3 | High Pressure Limit | HPS3-S | High Pressure Limit 3 | 1714 | 125 | BI | 23 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7009 | 9
York RTU.Cooling Control.DX Cooling Circuit 3 | High Pressure Lockout | HPS3-LO | High Pressure Lockout 3 | 1714 | 137 | ADI | 51 | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7010 | 9
York RTU.Cooling Control.DX Cooling Circuit 3 | Low Pressure Limit | LPS3-S | Low Pressure Limit 3 | 1714 | 126 | BI | 24 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7011 | 9
York RTU.Cooling Control.DX Cooling Circuit 3 | Low Pressure Lockout | LPS3-LO | Low Pressure Lockout 3 | 1714 | 138 | ADI | 52 | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7012 | 9
York RTU.Cooling Control.DX Cooling Circuit 3 | Freeze Condition | FS3-S | Freeze Condition 3 | 1714 | 139 | BI | 25 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7013 | 9
York RTU.Cooling Control.DX Cooling Circuit 3 | Freeze Condition Lockout | FS3-LO | Freeze Condition Lockout 3 | 1714 | 140 | ADI | 53 | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7014 | 9
York RTU.Cooling Control.DX Cooling Circuit 3 | Evaporator Coil Temp | EVAP3-T | Evaporator Coil Temp 3 | 1714 | 76 | AI | 9 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7015 | 9
York RTU.Cooling Control.DX Cooling Circuit 3 | Condenser Coil Temp | COND3-T | Condenser Coil Temp 3 | 1714 | 77 | AI | 10 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7016 | 9
York RTU.Cooling Control.DX Cooling Circuit 4 | Compressor Stage Command | COMP4-C | Compressor Stage Command 4 | 1714 | 148 | BO | 8 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7001 | 11
York RTU.Cooling Control.DX Cooling Circuit 4 | Compressor Stage Status | COMP4-S | Compressor Stage 4 Status | 1714 | 87 | BI | 26 | 0 = Off-Idle 1 = On-Minimum On Time 2 = On-Normal Command 3 = Off-Cooling Is Disabled ... |  | FALSE | 9 |  | SE RTU DX Cooling Circuit 1 Status | 1741 | [5 empty] | SE RTU DX Cooling Circuit 1 Status | 1741 |  |  |  |  | 7002 | 11
York RTU.Cooling Control.DX Cooling Circuit 4 | Compressor Stage Enabled | C4-EN | Compressor Stage 4 Enabled | 1714 | 88 | ADI | 54 | 0 = Yes 1 = No |  | TRUE | 9 |  | Yes/No | 1698 | [5 empty] | Yes/No | 1698 |  |  |  |  | 7003 | 11
York RTU.Cooling Control.DX Cooling Circuit 4 | Compressor Stage Accumulated Runtime | C4-RT | Compressor Stage Accumulated Runtime 4 | 1714 | 91 | ADF | 59 | 0 ... 10000 hours |  | TRUE | 4 | 1s | hours | 507:71 | 0 | 10000 |  |  | 1s | hours | 507:71 | 0 | 10000 |  |  | 7005 | 11
York RTU.Cooling Control.DX Cooling Circuit 4 | Min On Time Remaining | C4ONTMR | Min On Time Remaining 4 | 1714 | 89 | ADI | 55 | seconds |  | FALSE | 17 | 1s | seconds | 507:73 |  |  |  |  | 1s | seconds | 507:73 |  |  |  |  | 7007 | 11
York RTU.Cooling Control.DX Cooling Circuit 4 | Anti-Short Cycle Delay Time Remaining | C4ASCDTM | Anti-Short Cycle Delay Time Remaining 4 | 1714 | 90 | ADI | 56 | seconds |  | FALSE | 17 | 1s | seconds | 507:73 |  |  |  |  | 1s | seconds | 507:73 |  |  |  |  | 7008 | 11
York RTU.Cooling Control.DX Cooling Circuit 4 | High Pressure Limit | HPS4-S | High Pressure Limit 4 | 1714 | 127 | BI | 27 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7009 | 11
York RTU.Cooling Control.DX Cooling Circuit 4 | High Pressure Lockout | HPS4-LO | High Pressure Lockout 4 | 1714 | 141 | ADI | 57 | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7010 | 11
York RTU.Cooling Control.DX Cooling Circuit 4 | Low Pressure Limit | LPS4-S | Low Pressure Limit 4 | 1714 | 128 | BI | 28 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7011 | 11
York RTU.Cooling Control.DX Cooling Circuit 4 | Low Pressure Lockout | LPS4-LO | Low Pressure Lockout 4 | 1714 | 142 | ADI | 58 | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7012 | 11
York RTU.Cooling Control.DX Cooling Circuit 4 | Freeze Condition | FS4-S | Freeze Condition 4 | 1714 | 143 | BI | 29 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7013 | 11
York RTU.Cooling Control.DX Cooling Circuit 4 | Freeze Condition Lockout | FS4-LO | Freeze Condition Lockout 4 | 1714 | 144 | ADI | 59 | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7014 | 11
York RTU.Cooling Control.DX Cooling Circuit 4 | Evaporator Coil Temp | EVAP4-T | Evaporator Coil Temp 4 | 1714 | 92 | AI | 11 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7015 | 11
York RTU.Cooling Control.DX Cooling Circuit 4 | Condenser Coil Temp | COND4-T | Condenser Coil Temp 4 | 1714 | 93 | AI | 12 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7016 | 11
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Cooling Circuit Test Status | C1-TS | ClgCktTestS-1 | 1709 | 478 | ADI | 60 | 0 = Unknown Status 1 = Basic Data Not Available Manual Entry 2 = Basic Data Not Available 3 = Return Wet Bulb Temp Not Available ... |  | FALSE | 9 |  | SE FDD Codes | 1694 | [5 empty] | SE FDD Codes | 1694 |  |  |  |  | 7000 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Condenser Temperature Over Ambient Low | CT1OAMBL | Condenser Temperature Over Ambient Low | 1675 | 441 | ADF | 67 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7016 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Superheat High | C1-SUPHH | Superheat High | 1675 | 442 | ADF | 68 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7017 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Superheat Low | C1-SUPHL | Superheat Low | 1675 | 443 | ADF | 69 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7018 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Subcool High | C1-SCHGH | Subcool High | 1675 | 444 | ADF | 70 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7019 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Subcool Low | C1-SCLOW | Subcool Low | 1675 | 445 | ADF | 71 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7020 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Evaporating Temperature High | C1-ETHGH | Evaporating Temperature High | 1675 | 446 | ADF | 72 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7021 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Evaporating Temperature Low | C1-ETLOW | Evaporating Temperature Low | 1675 | 447 | ADF | 73 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7022 | 6
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Cooling Circuit Test Status | C2-TS | ClgCktTestS-2 | 1709 | 479 | ADI | 61 | 0 = Unknown Status 1 = Basic Data Not Available Manual Entry 2 = Basic Data Not Available 3 = Return Wet Bulb Temp Not Available ... |  | FALSE | 9 |  | SE FDD Codes | 1694 | [5 empty] | SE FDD Codes | 1694 |  |  |  |  | 7000 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Suction Pressure | SLP-2 | Suction Pressure 2 | 1714 | 62 | AI | 17 | psi (kPa) |  | FALSE | 4 | 10ths | psi | 507:56 |  |  |  |  | 1s | kPa | 507:54 |  |  |  |  | 7001 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Liquid Pressure | LLP-2 | Return Air Humidity | 1675 | 63 | AI | 18 | psi (kPa) |  | FALSE | 4 | 10ths | psi | 507:56 |  |  |  |  | 1s | kPa | 507:54 |  |  |  |  | 7002 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Suction Temperature | SLT-2 | Suction Temperature 2 | 1714 | 64 | AI | 19 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7003 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Liquid Temperature | LLT-2 | Liquid Temperature 2 | 1714 | 65 | AI | 20 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7004 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Superheat | C2-SUPHT | C2-SuperHeat | 1709 | 205 | ADF | 74 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7005 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Subcooling | C2-SUBCL | C2-SubCool | 1709 | 209 | ADF | 75 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7006 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Condensing Temperature over Ambient | CT2O-AMB | Condensing Temperature over Ambient 2 | 1714 | 70 | ADF | 76 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7007 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Efficiency Index | C2-EI | Efficiency Index 2 | 1714 | 68 | ADF | 77 | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7008 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Capacity Index | C2-CI | Capacity Index 2 | 1714 | 69 | ADF | 78 | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7009 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Evaporating Temp Value | C2-ETVAL | Evaporating Temperature Value Circuit 2 | 1714 | 165 | ADF | 79 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7014 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Condenser Temperature Over Ambient High | CT2OAMBH | Condenser Temperature Over Ambient High | 1675 | 440 | ADF | 80 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7015 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Condenser Temperature Over Ambient Low | CT2OAMBL | Condenser Temperature Over Ambient Low | 1675 | 441 | ADF | 81 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7016 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Superheat High | C2-SUPHH | Superheat High | 1675 | 442 | ADF | 82 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7017 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Superheat Low | C2-SUPHL | Superheat Low | 1675 | 443 | ADF | 83 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7018 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Subcool High | C2-SCHGH | Subcool High | 1675 | 444 | ADF | 84 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7019 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Subcool Low | C2-SCLOW | Subcool Low | 1675 | 445 | ADF | 85 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7020 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Evaporating Temperature High | C2-ETHGH | Evaporating Temperature High | 1675 | 446 | ADF | 86 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7021 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Evaporating Temperature Low | C2-ETLOW | Evaporating Temperature Low | 1675 | 447 | ADF | 87 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7022 | 8
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Cooling Circuit Test Status | C3-TS | ClgCktTestS-3 | 1709 | 480 | ADI | 62 | 0 = Unknown Status 1 = Basic Data Not Available Manual Entry 2 = Basic Data Not Available 3 = Return Wet Bulb Temp Not Available ... |  | FALSE | 9 |  | SE FDD Codes | 1694 | [5 empty] | SE FDD Codes | 1694 |  |  |  |  | 7000 | 10
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Suction Pressure | SLP-3 | Suction Pressure 3 | 1714 | 78 | AI | 21 | psi (kPa) |  | FALSE | 4 | 10ths | psi | 507:56 |  |  |  |  | 1s | kPa | 507:54 |  |  |  |  | 7001 | 10
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Liquid Pressure | LLP-3 | Liquid Pressure 3 | 1714 | 79 | AI | 22 | psi (kPa) |  | FALSE | 4 | 10ths | psi | 507:56 |  |  |  |  | 1s | kPa | 507:54 |  |  |  |  | 7002 | 10
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Suction Temperature | SLT-3 | Suction Temperature 3 | 1714 | 80 | AI | 23 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7003 | 10
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Liquid Temperature | LLT-3 | Liquid Temperature 3 | 1714 | 81 | AI | 24 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7004 | 10
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Superheat | C3-SUPHT | C3-SuperHeat | 1709 | 206 | ADF | 88 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7005 | 10
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Subcooling | C3-SUBCL | C3-SubCool | 1709 | 210 | ADF | 89 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7006 | 10
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Condensing Temperature over Ambient | CT3O-AMB | Condensing Temperature over Ambient 3 | 1714 | 86 | ADF | 90 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7007 | 10
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Efficiency Index | C3-EI | Efficiency Index 3 | 1714 | 84 | ADF | 91 | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7008 | 10
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Capacity Index | C3-CI | Capacity Index 3 | 1714 | 85 | ADF | 92 | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7009 | 10
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Evaporating Temp Value | C3-ETVAL | Evaporating Temperature Value Circuit 3 | 1714 | 166 | ADF | 93 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7014 | 10
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Condenser Temperature Over Ambient High | CT3OAMBH | Condenser Temperature Over Ambient High | 1675 | 440 | ADF | 94 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7015 | 10
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Condenser Temperature Over Ambient Low | CT3OAMBL | Condenser Temperature Over Ambient Low | 1675 | 441 | ADF | 95 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7016 | 10
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Superheat High | C3-SUPHH | Superheat High | 1675 | 442 | ADF | 96 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7017 | 10
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Superheat Low | C3-SUPHL | Superheat Low | 1675 | 443 | ADF | 97 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7018 | 10
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Subcool High | C3-SCHGH | Subcool High | 1675 | 444 | ADF | 98 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7019 | 10
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Subcool Low | C3-SCLOW | Subcool Low | 1675 | 445 | ADF | 99 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7020 | 10
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Evaporating Temperature High | C3-ETHGH | Evaporating Temperature High | 1675 | 446 | ADF | 100 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7021 | 10
York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics | Evaporating Temperature Low | C3-ETLOW | Evaporating Temperature Low | 1675 | 447 | ADF | 101 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7022 | 10
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Cooling Circuit Test Status | C4-TS | ClgCktTestS-4 | 1709 | 481 | ADI | 63 | 0 = Unknown Status 1 = Basic Data Not Available Manual Entry 2 = Basic Data Not Available 3 = Return Wet Bulb Temp Not Available ... |  | FALSE | 9 |  | SE FDD Codes | 1694 | [5 empty] | SE FDD Codes | 1694 |  |  |  |  | 7000 | 12
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Suction Pressure | SLP-4 | Suction Pressure 4 | 1714 | 94 | AI | 25 | psi (kPa) |  | FALSE | 4 | 10ths | psi | 507:56 |  |  |  |  | 1s | kPa | 507:54 |  |  |  |  | 7001 | 12
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Liquid Pressure | LLP-4 | Liquid Pressure 4 | 1714 | 95 | AI | 26 | psi (kPa) |  | FALSE | 4 | 10ths | psi | 507:56 |  |  |  |  | 1s | kPa | 507:54 |  |  |  |  | 7002 | 12
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Suction Temperature | SLT-4 | Suction Temperature 4 | 1714 | 96 | AI | 27 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7003 | 12
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Liquid Temperature | LLT-4 | Liquid Temperature 4 | 1714 | 97 | AI | 28 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7004 | 12
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Superheat | C4-SUPHT | C4-SuperHeat | 1709 | 207 | ADF | 102 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7005 | 12
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Subcooling | C4-SUBCL | C4-SubCool | 1709 | 211 | ADF | 103 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7006 | 12
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Condensing Temperature over Ambient | CT4O-AMB | Condensing Temperature over Ambient 4 | 1714 | 102 | ADF | 104 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7007 | 12
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Efficiency Index | C4-EI | Efficiency Index 4 | 1714 | 100 | ADF | 105 | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7008 | 12
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Capacity Index | C4-CI | Capacity Index 4 | 1714 | 101 | ADF | 106 | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7009 | 12
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Evaporating Temp Value | C4-ETVAL | Evaporating Temperature Value Circuit 4 | 1714 | 167 | ADF | 107 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7014 | 12
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Condenser Temperature Over Ambient High | CT4OAMBH | Condenser Temperature Over Ambient High | 1675 | 440 | ADF | 108 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7015 | 12
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Condenser Temperature Over Ambient Low | CT4OAMBL | Condenser Temperature Over Ambient Low | 1675 | 441 | ADF | 109 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7016 | 12
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Superheat High | C4-SUPHH | Superheat High | 1675 | 442 | ADF | 110 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7017 | 12
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Superheat Low | C4-SUPHL | Superheat Low | 1675 | 443 | ADF | 111 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7018 | 12
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Subcool High | C4-SCHGH | Subcool High | 1675 | 444 | ADF | 112 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7019 | 12
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Subcool Low | C4-SCLOW | Subcool Low | 1675 | 445 | ADF | 113 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7020 | 12
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Evaporating Temperature High | C4-ETHGH | Evaporating Temperature High | 1675 | 446 | ADF | 114 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7021 | 12
York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics | Evaporating Temperature Low | C4-ETLOW | Evaporating Temperature Low | 1675 | 447 | ADF | 115 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7022 | 12
York RTU.Heating Control | Heating Mode Enabled For Operation | HTG-EN | Heating Mode Enabled For Operation | 1675 | 105 | ADI | 64 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7000 | 13
York RTU.Heating Control | Heating Status | HTG-S | Heating Status | 1675 | 106 | ADI | 65 | 0 = Off-Idle 1 = On-Defrost 2 = SAT Tempering 3 = Morning Warmup ... |  | FALSE | 9 |  | SE RTU Heating Control Status | 1742 | [5 empty] | SE RTU Heating Control Status | 1742 |  |  |  |  | 7001 | 13
York RTU.Heating Control | SAT Air Temp Limit for Heating Enabled | SATHL-EN | SAT Air Temp Limit for Heating Enabled | 1675 | 108 | ADI | 66 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7002 | 13
York RTU.Heating Control | SAT Air Temp Limit For Heating Setpoint | SATHL-SP | SAT Air Temp Limit For Heating Setpoint | 1675 | 109 | ADF | 116 | 100 ... 180 deg F (38 ... 82 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 100 | 180 |  |  | 1s | deg C | 507:62 | 38 | 82 |  |  | 7003 | 13
York RTU.Heating Control | Outdoor Air Temp Heating Cutout Setpoint | OATHCOSP | Outdoor Air Temp Heating Cutout Setpoint | 1675 | 110 | ADF | 117 | 0 ... 100 deg F (-18 ... 38 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 0 | 100 |  |  | 1s | deg C | 507:62 | -18 | 38 |  |  | 7004 | 13
York RTU.Heating Control | Hot Water Freeze Stat | FSHW | Hot Water Freeze Stat | 1675 | 203 | ADI | 67 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7005 | 13
York RTU.Heating Control | Gas Valve1 Input | GV1-S | Gas Valve1 Input | 1675 | 118 | BI | 30 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7006 | 13
York RTU.Heating Control | Gas Valve2 Input | GV2-S | Gas Valve2 Input | 1675 | 119 | BI | 31 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7007 | 13
York RTU.Heating Control | Gas Valve3 Input | GV3-S | Gas Valve3 Input | 1675 | 120 | BI | 32 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7008 | 13
York RTU.Heating Control | Heat Limit1 Switch | LIM1-SW | Heat Limit1 Switch | 1675 | 121 | BI | 33 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7009 | 13
York RTU.Heating Control | Heat Limit1 Switch Lockout | LIMIT1LO | Heat Limit1 Switch Lockout | 1675 | 122 | ADI | 68 | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7010 | 13
York RTU.Heating Control | Heat Limit2 Switch | LIM2-SW | Heat Limit2 Switch | 1675 | 123 | BI | 34 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7011 | 13
York RTU.Heating Control | Heat Limit2 Switch Lockout | LIMIT2LO | Heat Limit2 Switch Lockout | 1675 | 124 | ADI | 69 | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7012 | 13
York RTU.Heating Control | Heat Limit3 Switch | LM3-SW | Heat Limit3 Switch | 1675 | 125 | BI | 35 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7013 | 13
York RTU.Heating Control | Heat Limit3 Switch Lockout | LIMIT3LO | Heat Limit3 Switch Lockout | 1675 | 126 | ADI | 70 | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7014 | 13
York RTU.Heating Control | VAV Occupied Heating Enabled | VHTGOCEN | VAV Occupied Heating Enabled | 1675 | 204 | ADI | 71 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7015 | 13
York RTU.Heating Control | VAV Occupied Heating Setpoint | VHTGOCSP | VAV Occupied Heating Setpoint | 1675 | 205 | ADF | 118 | 40 ... 85 deg F (4 ... 30 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 40 | 85 |  |  | 1s | deg C | 507:62 | 4 | 30 |  |  | 7016 | 13
York RTU.Heating Control | Unoccupied Heating Enabled | VHTGUNEN | Unoccupied Heating Enabled | 1675 | 206 | ADI | 72 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7017 | 13
York RTU | Unit Status | UNIT-S | Unit Status | 1675 | 0 | ADI | 1 | 0 = Idle 1 = SD Alarm 2 = Purge Command 3 = Self Test ... |  | FALSE | 9 |  | SE RTU Unit Status | 1737 | [5 empty] | SE RTU Unit Status | 1737 |  |  |  |  | 7000 | 1
York RTU | Reset Lockouts | RESETLO | Reset Lockouts | 1675 | 337 | ADI | 2 | 0 = Off 1 = On |  | TRUE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7011 | 1
York RTU.Thermostat Control | Y1 - Thermostat | Y1-TSTAT | Y1 - Thermostat | 1675 | 150 | BI | 1 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7000 | 2
York RTU.Thermostat Control | Y2 - Thermostat | Y2-TSTAT | Y2 - Thermostat | 1675 | 151 | BI | 2 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7001 | 2
York RTU.Thermostat Control | Y3 - Thermostat | Y3-TSTAT | Y3 - Thermostat | 1675 | 152 | BI | 3 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7002 | 2
York RTU.Thermostat Control | Y4 - Thermostat | Y4-TSTAT | Y4 - Thermostat | 1675 | 153 | BI | 4 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7003 | 2
York RTU.Thermostat Control | W1 - Thermostat | W1-TSTAT | W1 - Thermostat | 1675 | 154 | BI | 5 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7004 | 2
York RTU.Thermostat Control | W2 - Thermostat | W2-TSTAT | W2 - Thermostat | 1675 | 155 | BI | 6 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7005 | 2
York RTU.Thermostat Control | W3 - Thermostat | W3-TSTAT | W3 - Thermostat | 1675 | 156 | BI | 7 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7006 | 2
York RTU.Thermostat Control | G - Thermostat | G-TSTAT | G - Thermostat | 1675 | 157 | BI | 8 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7007 | 2
York RTU.Thermostat Control | X-OUT | X-C | X-OUT | 1675 | 159 | BO | 1 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7009 | 2
York RTU.HVAC Zone | Occupancy Input Source | OCCSRC | Occupancy Input Source | 1675 | 9 | ADI | 3 | 0 = Local Input 1 = Local Network Sensor 2 = BAS Network Request 3 = Local Schedule 4 = Temporary Occupancy |  | FALSE | 9 |  | Effective Occupancy Source | 1668 | [5 empty] | Effective Occupancy Source | 1668 |  |  |  |  | 7000 | 25
York RTU.HVAC Zone | Occupancy Input | OCC-S | Occupancy Input | 1675 | 291 | BI | 9 | 0 = Occupied 1 = Unoccupied |  | FALSE | 9 |  | SE RTU Unocc/Occ | 1658 | [5 empty] | SE RTU Unocc/Occ | 1658 |  |  |  |  | 7030 | 25
York RTU.HVAC Zone | Temporary Occupancy Input | TEMPOCCEN | Temporary Occupancy Input | 1675 | 329 | ADI | 4 | 0 = Disable 1 = Enable |  | TRUE | 9 |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 |  |  |  |  | 7040 | 25
York RTU.HVAC Zone | Operational Occupancy | OPROCC | Operational Occupancy | 1675 | 10 | ADI | 5 | 0 = Occupied 1 = UnOccupied 2 = Bypass 3 = Standby |  | FALSE | 9 |  | Occ Effective | 345 | [5 empty] | Occ Effective | 345 |  |  |  |  | 7001 | 25
York RTU.HVAC Zone | Occupancy Mode | OCCENMODE | Occupancy Mode | 1675 | 161 | ADI | 6 | 0 = Schedule 1 = External |  | TRUE | 9 |  | SE Occupancy Mode | 1728 | [5 empty] | SE Occupancy Mode | 1728 |  |  |  |  | 7002 | 25
York RTU.HVAC Zone | Network Temporary Occupancy Request | NETTMPOC | Network Temporary Occupancy Request | 1675 | 12 | ADI | 7 | 0 = False 1 = True |  | TRUE | 9 |  | False/True | 1701 | [5 empty] | False/True | 1701 |  |  |  |  | 7003 | 25
York RTU.HVAC Zone | Network Occupancy Request | NETOCCRQ | Network Occupancy Request | 1675 | 13 | ADI | 8 | 0 = Occupied 1 = UnOccupied 2 = Not Set |  | TRUE | 9 |  | Occ Sensor | 344 | [5 empty] | Occ Sensor | 344 |  |  |  |  | 7004 | 25
York RTU.HVAC Zone | Temporary Occupancy Timeout | TMPOCCTO | Temporary Occupancy Timeout | 1675 | 14 | ADI | 9 | 30 ... 600 minutes |  | TRUE | 17 | 1s | minutes | 507:72 | 30 | 600 |  |  | 1s | minutes | 507:72 | 30 | 600 |  |  | 7005 | 25
York RTU.HVAC Zone | Operational Space Temperature | OPRST | Operational Space Temperature | 1675 | 15 | AI | 31 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7006 | 25
York RTU.HVAC Zone | Space Temperature Source | STSRC | Space Temperature Source | 1675 | 16 | ADI | 10 | 0 = Unreliable 1 = Return Air Temp 2 = Local Input 3 = Network Sensor ... |  | FALSE | 9 |  | Effective Input Source | 1715 | [5 empty] | Effective Input Source | 1715 |  |  |  |  | 7007 | 25
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Suction Pressure | SLP-1 | Suction Pressure 1 | 1714 | 46 | AI | 13 | psi (kPa) |  | FALSE | 4 | 10ths | psi | 507:56 |  |  |  |  | 1s | kPa | 507:54 |  |  |  |  | 7001 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Liquid Pressure | LLP-1 | Liquid Pressure 1 | 1714 | 47 | AI | 14 | psi (kPa) |  | FALSE | 4 | 10ths | psi | 507:56 |  |  |  |  | 1s | kPa | 507:54 |  |  |  |  | 7002 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Suction Temperature | SLT-1 | Suction Temperature 1 | 1714 | 48 | AI | 15 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7003 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Liquid Temperature | LLT-1 | Liquid Temperature 1 | 1714 | 49 | AI | 16 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7004 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Superheat | C1-SUPHT | C1-SuperHeat | 1709 | 204 | ADF | 60 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7005 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Subcooling | C1-SUBCL | C1-SubCool | 1709 | 208 | ADF | 61 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7006 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Condensing Temperature over Ambient | CT1O-AMB | Condensing Temperature over Ambient 1 | 1714 | 54 | ADF | 62 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7007 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Efficiency Index | C1-EI | Efficiency Index 1 | 1714 | 52 | ADF | 63 | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7008 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Capacity Index | C1-CI | Capacity Index 1 | 1714 | 53 | ADF | 64 | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7009 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Evaporating Temp Value | C1-ETVAL | Evaporating Temperature Value Circuit 1 | 1714 | 164 | ADF | 65 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7014 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Condenser Temperature Over Ambient High | CT1OAMBH | Condenser Temperature Over Ambient High | 1675 | 440 | ADF | 66 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7015 | 6
York RTU.HVAC Zone | Space Temperature Alarm Setpoint Offset | STALMOFF | Space Temperature Alarm Setpoint Offset | 1675 | 162 | ADF | 2 | 0 ... 25 delta deg F (0 ... 14 delta deg C) |  | TRUE | 4 | 1s | delta deg F | 507:120 | 0 | 25 |  |  | 1s | delta deg C | 507:359 | 0 | 14 |  |  | 7008 | 25
York RTU.HVAC Zone | Space Temperature Alarm Time Delay | STALMDLY | Space Temperature Alarm Time Delay | 1675 | 163 | ADI | 11 | 0 ... 120 minutes |  | TRUE | 17 | 1s | minutes | 507:72 | 0 | 120 |  |  | 1s | minutes | 507:72 | 0 | 120 |  |  | 7009 | 25
York RTU.HVAC Zone | Network Override Space Temperature | NETST | Network Override Space Temperature | 1675 | 18 | ADF | 3 | 0 ... 100 deg F (4 ... 38 deg C) |  | TRUE | 4 | 10ths | deg F | 507:64 | 0 | 100 |  |  | 10ths | deg C | 507:62 | 4 | 38 |  |  | 7011 | 25
York RTU.HVAC Zone | Operational Indoor Air Quality | OPRIAQ | Operational Indoor Air Quality | 1675 | 165 | ADF | 4 | ppm |  | FALSE | 4 | 10s | ppm | 507:96 |  |  |  |  | 10s | ppm | 507:96 |  |  |  |  | 7012 | 25
York RTU.HVAC Zone | Indoor Air Quality Source | IAQSRC | Indoor Air Quality Source | 1675 | 20 | ADI | 12 | 0 = Unreliable 1 = Local Input 2 = Network Sensor 3 = High Priority ... |  | FALSE | 9 |  | Effective Input Source 2 | 1732 | [5 empty] | Effective Input Source 2 | 1732 |  |  |  |  | 7013 | 25
York RTU.HVAC Zone | Indoor Air Quality Sensor Range | IAQRANGE | Indoor Air Quality Sensor Range | 1675 | 166 | ADF | 5 | 0 ... 5000 ppm |  | TRUE | 4 | 1s | ppm | 507:96 | 0 | 5000 |  |  | 1s | ppm | 507:96 | 0 | 5000 |  |  | 7015 | 25
York RTU.HVAC Zone | Network Override Indoor Air Quality | NETIAQ | Network Override Indoor Air Quality | 1675 | 22 | ADF | 6 | 0 ... 5000 ppm |  | TRUE | 4 | 10s | ppm | 507:96 | 0 | 5000 |  |  | 10s | ppm | 507:96 | 0 | 5000 |  |  | 7016 | 25
York RTU.HVAC Zone | Operational Space Humidity | OPRSH | Operational Space Humidity | 1675 | 23 | AI | 32 | %RH |  | FALSE | 4 | 10ths | %RH | 507:29 |  |  |  |  | 10ths | %RH | 507:29 |  |  |  |  | 7017 | 25
York RTU.HVAC Zone | Space Humidity Source | SHSRC | Space Humidity Source | 1675 | 24 | ADI | 13 | 0 = Unreliable 1 = Local Input 2 = Network Sensor 3 = High Priority ... |  | FALSE | 9 |  | Effective Input Source 2 | 1732 | [5 empty] | Effective Input Source 2 | 1732 |  |  |  |  | 7018 | 25
York RTU.HVAC Zone | Space Humidity RAH Input | RA-H | Space Humidity RAH Input | 1675 | 25 | AI | 1 | %RH |  | FALSE | 4 | 10ths | %RH | 507:29 |  |  |  |  | 10ths | %RH | 507:29 |  |  |  |  | 7019 | 25
York RTU.HVAC Zone | Return Air Temperature | RA-T | Return Air Temperature | 1675 | 65 | AI | 2 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7038 | 25
York RTU.HVAC Zone | Network Override Zone Humidity | NETSH | Network Override Zone Humidity | 1675 | 26 | ADF | 8 | 0 ... 100 %RH |  | TRUE | 4 | 10ths | %RH | 507:29 | 0 | 100 |  |  | 10ths | %RH | 507:29 | 0 | 100 |  |  | 7020 | 25
York RTU.HVAC Zone | Operating Fan Request | OPRFNREQ | Operating Fan Request | 1675 | 27 | ADI | 14 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7021 | 25
York RTU.HVAC Zone | Fan Request Source | FNREQSRC | Fan Request Source | 1675 | 28 | ADI | 15 | 0 = Unreliable 1 = Local Input 2 = Network Sensor 3 = High Priority ... |  | FALSE | 9 |  | Effective Input Source 2 | 1732 | [5 empty] | Effective Input Source 2 | 1732 |  |  |  |  | 7022 | 25
York RTU.HVAC Zone | Network Override Fan Request | NETFNREQ | Network Override Fan Request | 1675 | 29 | ADI | 16 | 0 = Off 1 = On |  | TRUE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7023 | 25
York RTU.HVAC Zone | Operational Space Temperature Setpoint Offset | OPRSSO | Operational Space Temperature Setpoint Offset | 1675 | 30 | ADF | 9 | delta deg F (delta deg C) |  | FALSE | 4 | 10ths | delta deg F | 507:120 |  |  |  |  | 10ths | delta deg C | 507:359 |  |  |  |  | 7024 | 25
York RTU.HVAC Zone | Space Temperature Setpoint Offset Source | SSOSRC | Space Temperature Setpoint Offset Source | 1675 | 31 | ADI | 17 | 0 = Unreliable 1 = Local Input 2 = Network Sensor 3 = High Priority ... |  | FALSE | 9 |  | Effective Input Source 2 | 1732 | [5 empty] | Effective Input Source 2 | 1732 |  |  |  |  | 7025 | 25
York RTU.HVAC Zone | Space Temp Setpoint Offset Input | SSO | Space Temp Setpoint Offset Input | 1675 | 32 | ADF | 10 | delta deg F (delta deg C) |  | FALSE | 4 | 10ths | delta deg F | 507:120 |  |  |  |  | 10ths | delta deg C | 507:359 |  |  |  |  | 7026 | 25
York RTU.HVAC Zone | Network Override Space Setpoint Offset | NETSSO | Network Override Space Setpoint Offset | 1675 | 33 | ADF | 11 | -5 ... 5 delta deg F (-3 ... 3 delta deg C) |  | TRUE | 4 | 10ths | delta deg F | 507:120 | -5 | 5 |  |  | 10ths | delta deg C | 507:359 | -3 | 3 |  |  | 7027 | 25
York RTU.HVAC Zone | Time to Next Occupancy Period | T2NOCPER | Time to Next Occupancy Period | 1675 | 425 | ADF | 12 | minutes |  | FALSE | 4 | 10ths | minutes | 507:72 |  |  |  |  | 10ths | minutes | 507:72 |  |  |  |  | 7046 | 25
York RTU.HVAC Zone | Operating Mode | OPERMODE | Operating Mode | 1675 | 426 | ADI | 18 | 0 = Normal 1 = Warmup 2 = Cooldown 3 = Coast |  | FALSE | 9 |  | OST Warmup Cooldown | 366 | [5 empty] | OST Warmup Cooldown | 366 |  |  |  |  | 7047 | 25
York RTU.HVAC Zone | Off During Unoccupied | OFFDURUNC | Off During Unoccupied | 1675 | 501 | ADI | 19 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7059 | 25
York RTU.Weather Information | Operational Outdoor Air Temperature | OPROAT | Operational Outdoor Air Temperature | 1675 | 36 | ADF | 23 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7000 | 26
York RTU.Weather Information | Outdoor Air Temperature Source | OATSRC | Outdoor Air Temperature Source | 1675 | 37 | ADI | 21 | 0 = Unreliable 1 = Local Input 2 = Network Sensor 3 = High Priority ... |  | FALSE | 9 |  | Effective Input Source 2 | 1732 | [5 empty] | Effective Input Source 2 | 1732 |  |  |  |  | 7001 | 26
York RTU.Weather Information | Network Override Outdoor Air Temperature | NETOAT | Network Override Outdoor Air Temperature | 1675 | 39 | ADF | 24 | -50 ... 125 deg F (-18 ... 52 deg C) |  | TRUE | 4 | 10ths | deg F | 507:64 | -50 | 125 |  |  | 10ths | deg C | 507:62 | -18 | 52 |  |  | 7003 | 26
York RTU.Weather Information | Operational Outdoor Air Humidity | OPROAH | Operational Outdoor Air Humidity | 1675 | 40 | ADF | 25 | %RH |  | FALSE | 4 | 1s | %RH | 507:29 |  |  |  |  | 1s | %RH | 507:29 |  |  |  |  | 7004 | 26
York RTU.Weather Information | Outdoor Air Enthalpy | OA-ENTH | Outdoor Air Enthalpy | 1675 | 41 | ADF | 26 | Btu/lb (kJ/kg) |  | FALSE | 4 | 1s | Btu/lb | 507:117 |  |  |  |  | 1s | kJ/kg | 507:125 |  |  |  |  | 7005 | 26
York RTU.Weather Information | Network Override Outdoor Air Humidity | NETOAH | Network Override Outdoor Air Humidity | 1675 | 44 | ADF | 27 | 0 ... 100 %RH |  | TRUE | 4 | 10ths | %RH | 507:29 | 0 | 100 |  |  | 10ths | %RH | 507:29 | 0 | 100 |  |  | 7008 | 26
York RTU.Weather Information | Operational Outdoor Air Quality | OPROAQ | Operational Outdoor Air Quality | 1675 | 45 | ADF | 28 | ppm |  | FALSE | 4 | 10s | ppm | 507:96 |  |  |  |  | 10s | ppm | 507:96 |  |  |  |  | 7009 | 26
York RTU.Weather Information | Outdoor Air Quality Source | OAQSRC | Outdoor Air Quality Source | 1675 | 46 | ADI | 22 | 0 = Unreliable 1 = Local Input 2 = Network Sensor 3 = High Priority ... |  | FALSE | 9 |  | Effective Input Source 2 | 1732 | [5 empty] | Effective Input Source 2 | 1732 |  |  |  |  | 7010 | 26
York RTU.Weather Information | Network Override Outdoor Air Quality | NETOAQ | Network Override Outdoor Air Quality | 1675 | 49 | ADF | 29 | 0 ... 5000 ppm |  | TRUE | 4 | 10s | ppm | 507:96 | 0 | 5000 |  |  | 10s | ppm | 507:96 | 0 | 5000 |  |  | 7013 | 26
York RTU.Fan Control | Fan Status | FAN-S | Fan Status | 1675 | 168 | ADI | 23 | 0 = Off-Idle 1 = On-Purge 2 = On-Gas Valve or Limit Fault 3 = On-Defrost ... |  | FALSE | 9 |  | SE RTU Fan Status | 1739 | [5 empty] | SE RTU Fan Status | 1739 |  |  |  |  | 7000 | 3
York RTU.Fan Control | Fan % Command | SFPCT-O | Fan % Command | 1675 | 169 | AO | 1 | % |  | FALSE | 4 | 1s | % | 507:98 |  |  |  |  | 1s | % | 507:98 |  |  |  |  | 7001 | 3
York RTU.Fan Control | Fan VFD Fault | FNVFDFLT | Fan VFD Fault | 1675 | 170 | BI | 10 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7002 | 3
York RTU.Fan Control | Fan Overload | FAN-OL | Fan Overload | 1675 | 171 | BI | 11 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7003 | 3
York RTU.Fan Control | Fan Accumulated Runtime | FAN-RT | Fan Accumulated Runtime | 1675 | 172 | ADF | 30 | 0 ... 10000 hours |  | TRUE | 4 | 1s | hours | 507:71 | 0 | 10000 |  |  | 1s | hours | 507:71 | 0 | 10000 |  |  | 7004 | 3
York RTU.Fan Control | Air Proving Switch | APS | Air Proving Switch | 1675 | 175 | BI | 12 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7007 | 3
York RTU.Fan Control | Fan On Delay for Cool | FNONDLCL | Fan On Delay for Cool | 1675 | 176 | ADI | 24 | 0 ... 30 seconds |  | TRUE | 17 | 1s | seconds | 507:73 | 0 | 30 |  |  | 1s | seconds | 507:73 | 0 | 30 |  |  | 7008 | 3
York RTU.Fan Control | Dirty Filter Switch | FILTER-S | Dirty Filter Switch | 1675 | 180 | BI | 13 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7012 | 3
York RTU.Fan Control | Fan Command | FAN-C | Fan Command | 1675 | 181 | BO | 2 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7013 | 3
York RTU.Fan Control | Supply Air Temperature | SA-T | Supply Air Temperature | 1675 | 182 | AI | 3 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7014 | 3
York RTU.Fan Control | Duct Static Pressure | DUCT-P | Duct Static Pressure | 1675 | 183 | AI | 4 | in wc (kPa) |  | FALSE | 4 | 100ths | in wc | 507:58 |  |  |  |  | 100ths | kPa | 507:54 |  |  |  |  | 7015 | 3
York RTU.Fan Control | Duct Pressure Setpoint | DCTPRSSP | Duct Pressure Setpoint | 1675 | 184 | ADF | 31 | 0 ... 5 in wc (0 ... 1.25 kPa) |  | TRUE | 4 | 100ths | in wc | 507:58 | 0 | 5 |  |  | 100ths | kPa | 507:54 | 0 | 1.25 |  |  | 7016 | 3
York RTU.Fan Control | Duct Pressure Shutdown Setpoint | DCTSDSP | Duct Pressure Shutdown Setpoint | 1675 | 185 | ADF | 32 | 0 ... 5 in wc (0 ... 1.25 kPa) |  | TRUE | 4 | 100ths | in wc | 507:58 | 0 | 5 |  |  | 100ths | kPa | 507:54 | 0 | 1.25 |  |  | 7017 | 3
York RTU.Fan Control | Continuous Fan Operation in Occupied Mode | FANONOCC | Continuous Fan Operation in Occupied Mode | 1675 | 186 | ADI | 25 | 0 = Yes 1 = No |  | TRUE | 9 |  | Yes/No | 1698 | [5 empty] | Yes/No | 1698 |  |  |  |  | 7018 | 3
York RTU.Fan Control | Turn Off Continuous Fan Operation When Starting Heat | FNOFSTHT | Turn Off Continuous Fan Operation When Starting Heat | 1675 | 187 | ADI | 26 | 0 = Yes 1 = No |  | TRUE | 9 |  | Yes/No | 1698 | [5 empty] | Yes/No | 1698 |  |  |  |  | 7019 | 3
York RTU.Fan Control | Occupied: No Heat or Cool % Command | FOPCT | Occupied: No Heat or Cool % Command | 1675 | 188 | ADF | 33 | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7020 | 3
York RTU.Fan Control | Occupied: One Stage of Cool % Command | 1CSPCT | Occupied: One Stage of Cool % Command | 1675 | 189 | ADF | 34 | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7021 | 3
York RTU.Fan Control | Occupied: Two Stage of Cool % Command | 2CSPCT | Occupied: Two Stage of Cool % Command | 1675 | 190 | ADF | 35 | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7022 | 3
York RTU.Fan Control | Occupied: Three Stage of Cool % Command | 3CSPCT | Occupied: Three Stage of Cool % Command | 1675 | 320 | ADF | 36 | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7027 | 3
York RTU.Fan Control | Occupied: Four Stage of Cool % Command | 4CSPCT | Occupied: Four Stage of Cool % Command | 1675 | 321 | ADF | 37 | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7028 | 3
York RTU.Fan Control | Occupied: One Stage of Heat % Command | 1HSPCT | Occupied: One Stage of Heat % Command | 1675 | 191 | ADF | 38 | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7023 | 3
York RTU.Fan Control | Occupied: Two Stage of Heat % Command | 2HSPCT | Occupied: Two Stage of Heat % Command | 1675 | 192 | ADF | 39 | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7024 | 3
York RTU.Fan Control | Occupied: Three Stage of Heat % Command | 3HSPCT | Occupied: Three Stage of Heat % Command | 1675 | 322 | ADF | 40 | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7029 | 3
York RTU.Cooling Control | Cooling Mode Enabled For Operation | CLG-EN | Cooling Mode Enabled For Operation | 1675 | 66 | ADI | 27 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7000 | 4
York RTU.Cooling Control | Cooling Status | CLG-S | Cooling Status | 1675 | 69 | ADI | 28 | 0 = Off-Idle 1 = Thermostat Cooling 2 = Unoccupied Cooling 3 = Occupied Cooling ... |  | FALSE | 9 |  | SE RTU Cooling Control Status | 1740 | [5 empty] | SE RTU Cooling Control Status | 1740 |  |  |  |  | 7002 | 4
York RTU.Cooling Control | Minimum Runtime for a Cooling Stage | MNRTCLST | Minimum Runtime for a Cooling Stage | 1675 | 71 | ADF | 41 | 3 ... 10 minutes |  | TRUE | 16 | 1s | minutes | 507:72 | 3 | 10 |  |  | 1s | minutes | 507:72 | 3 | 10 |  |  | 7003 | 4
York RTU.Cooling Control | OAT Cooling Cutout Enabled | CLOACOEN | OAT Cooling Cutout Enabled | 1675 | 127 | ADI | 29 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7006 | 4
York RTU.Cooling Control | OAT Cooling Cutout | CLOACOSP | OAT Cooling Cutout | 1675 | 74 | ADF | 42 | 0 ... 100 deg F (-18 ... 38 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 0 | 100 |  |  | 1s | deg C | 507:62 | -18 | 38 |  |  | 7007 | 4
York RTU.Cooling Control | Economizer Loading Enabled | ECNLD-EN | Economizer Loading Enabled | 1675 | 76 | ADI | 30 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7008 | 4
York RTU.Cooling Control | All Compressors Off in Free Cooling | CLOFFECN | All Compressors Off in Free Cooling | 1675 | 77 | ADI | 31 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7009 | 4
York RTU.Cooling Control | Temperature/Humidity (Return) Control Enable | THCTRLEN | Temperature/Humidity (Return) Control Enable | 1675 | 79 | ADI | 32 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7011 | 4
York RTU.Cooling Control | Temperature/Humidity Setpoint | TEMPHMSP | Temperature/Humidity Setpoint | 1675 | 80 | ADF | 43 | 20 ... 80 %RH |  | TRUE | 4 | 1s | %RH | 507:29 | 20 | 80 |  |  | 1s | %RH | 507:29 | 20 | 80 |  |  | 7012 | 4
York RTU.Cooling Control | Maximum Temperature / Humidity Setpoint Offset | MXTHSPOF | Maximum Temperature / Humidity Setpoint Offset | 1675 | 81 | ADF | 44 | 0 ... 5 delta deg F (0 ... 3 delta deg C) |  | TRUE | 4 | 10ths | delta deg F | 507:120 | 0 | 5 |  |  | 10ths | delta deg C | 507:359 | 0 | 3 |  |  | 7013 | 4
York RTU.Cooling Control | Temperature / Humidity Value per Degree Offset | THVDGOFF | Temperature / Humidity Value per Degree Offset | 1675 | 82 | ADF | 45 | 1 ... 10 %RH |  | TRUE | 4 | 1s | %RH | 507:29 | 1 | 10 |  |  | 1s | %RH | 507:29 | 1 | 10 |  |  | 7014 | 4
York RTU.Cooling Control | SAT Limit for Cooling Enable | SATCLMEN | SAT Limit for Cooling Enable | 1675 | 143 | ADI | 33 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7015 | 4
York RTU.Cooling Control | SAT Limit for Cooling Setpoint | SATCLMSP | SAT Limit for Cooling Setpoint | 1675 | 75 | ADF | 46 | 40 ... 65 deg F (4 ... 18 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 40 | 65 |  |  | 1s | deg C | 507:62 | 4 | 18 |  |  | 7016 | 4
York RTU.Cooling Control | Condenser Fan 1 | CF1-C | Condenser Fan 1 | 1675 | 128 | BO | 3 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7018 | 4
York RTU.Cooling Control | Condenser Fan 2 | CF2-C | Condenser Fan 2 | 1675 | 129 | BO | 4 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7019 | 4
York RTU.Cooling Control | VAV Cooling Supply Air Temp Upper Setpoint | SATUP-SP | VAV Cooling Supply Air Temp Upper Setpoint | 1675 | 137 | ADF | 47 | 41 ... 70 deg F (5 ... 21 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 41 | 70 |  |  | 1s | deg C | 507:62 | 5 | 21 |  |  | 7029 | 4
York RTU.Cooling Control | VAV Cooling Supply Air Temp Lower Setpoint | SATLO-SP | VAV Cooling Supply Air Temp Lower Setpoint | 1675 | 138 | ADF | 48 | 40 ... 69 deg F (4 ... 20 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 40 | 69 |  |  | 1s | deg C | 507:62 | 4 | 20 |  |  | 7030 | 4
York RTU.Cooling Control | VAV Supply Air Temp Reset Setpoint | SATRSTSP | VAV Supply Air Temp Reset Setpoint | 1675 | 139 | ADF | 49 | 40 ... 85 deg F (4 ... 30 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 40 | 85 |  |  | 1s | deg C | 507:62 | 4 | 30 |  |  | 7031 | 4
York RTU.Cooling Control | VAV Operating Cooling Setpoint | OPRVAVCLSP | VAV Operating Cooling Supply Air Temp Setpoint | 1675 | 140 | ADF | 50 | deg F (deg C) |  | FALSE | 4 | 100ths | deg F | 507:64 |  |  |  |  | 100ths | deg C | 507:62 |  |  |  |  | 7032 | 4
York RTU.Cooling Control | CV Occupied Cooling Setpoint | CLGOCCSP | CV Occupied Cooling Setpoint | 1675 | 141 | ADF | 51 | 45 ... 98 deg F (7 ... 36 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 45 | 98 |  |  | 1s | deg C | 507:62 | 7 | 36 |  |  | 7033 | 4
York RTU.Cooling Control | CV Unoccupied Cooling Setpoint | CLGUNCSP | CV Unoccupied Cooling Setpoint | 1675 | 142 | ADF | 52 | 46 ... 99 deg F (8 ... 37 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 46 | 99 |  |  | 1s | deg C | 507:62 | 8 | 37 |  |  | 7034 | 4
York RTU.Cooling Control | CV Operating Cooling Setpoint | COPCLGSP | CV Operating Cooling Setpoint | 1675 | 144 | ADF | 53 | deg F (deg C) |  | FALSE | 4 | 100ths | deg F | 507:64 |  |  |  |  | 100ths | deg C | 507:62 |  |  |  |  | 7035 | 4
York RTU.Cooling Control | Altitude | ALTITUDE | Altitude | 1675 | 374 | ADF | 54 | -1500 ... 30000 ft (-457.2 ... 9144 m) |  | TRUE | 4 | 10ths | ft | 507:33 | -1500 | 30000 |  |  | 10ths | m | 507:31 | -457.2 | 9144 |  |  | 7041 | 4
York RTU.Cooling Control | Number of Refrig Systems Installed | REFSYS | Number of Refrig Systems Installed | 1675 | 495 | ADF | 55 | 0 ... 4 |  | TRUE | 4 | 1s |  | 507:95 | 0 | 4 |  |  | 1s |  | 507:95 | 0 | 4 |  |  | 7044 | 4
York RTU.Cooling Control.DX Cooling Circuit 1 | Compressor Stage Command | COMP1-C | Compressor Stage Command 1 | 1714 | 145 | BO | 5 | 0 = Off 1 = On |  | FALSE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7001 | 5
York RTU.Cooling Control.DX Cooling Circuit 1 | Compressor Stage Status | COMP1-S | Compressor Stage 1 Status | 1714 | 39 | BI | 14 | 0 = Off-Idle 1 = On-Minimum On Time 2 = On-Normal Command 3 = Off-Cooling Is Disabled ... |  | FALSE | 9 |  | SE RTU DX Cooling Circuit 1 Status | 1741 | [5 empty] | SE RTU DX Cooling Circuit 1 Status | 1741 |  |  |  |  | 7002 | 5
York RTU.Cooling Control.DX Cooling Circuit 1 | Compressor Stage Enabled | C1-EN | Compressor Stage 1 Enabled | 1714 | 40 | ADI | 36 | 0 = Yes 1 = No |  | TRUE | 9 |  | Yes/No | 1698 | [5 empty] | Yes/No | 1698 |  |  |  |  | 7003 | 5
York RTU.HVAC Zone | Heat Cool Setpoint Mode | HTCLSPMODE | HtgClgSP-Mode | 1709 | 701 | ADI | 188 | 0 = Common Setpoint 1 = Individual Setpoints |  | TRUE | 9 |  | Heat Cool Setpoint Mode | 2596 | [5 empty] | Heat Cool Setpoint Mode | 2596 |  |  |  |  | 7075 | 25
York RTU.HVAC Zone | Common Setpoint | COMMON-SP | Common-SP | 1709 | 702 | ADF | 189 | 45 ... 98 deg F (8 ... 36 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 45 | 98 |  |  | 1s | deg C | 507:62 | 8 | 36 |  |  | 7074 | 25
York RTU.Fan Control | Dehumidification % Command | DEHUMSPCT | Dehum%Cmd | 1709 | 731 | ADF | 190 | 0 ... 100 % |  | TRUE | 4 | 1s | % | 507:98 | 0 | 100 |  |  | 1s | % | 507:98 | 0 | 100 |  |  | 7042 | 3
York RTU.Hot Gas Reheat | Hot Gas Reheat Command | MODHGR | HGR | 1709 | 324 | AO | 6 | % |  | FALSE | 4 | 10ths | % | 507:98 |  |  |  |  | 10ths | % | 507:98 |  |  |  |  | 7027 | 20
York RTU.Economizer | Calibration Fault Detect Enable | CALFLTDET | CalFaultDetectEn | 1709 | 723 | ADI | 191 | 0 = Disable 1 = Enable |  | TRUE | 9 |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 |  |  |  |  | 7032 | 19
York RTU.Shutdown Input | Pressurize Instead Of Purge | PRESSURIZE | PressurizeNotPurge | 1709 | 709 | ADI | 192 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7005 | 27
York RTU.Cooling Control | Cooling Allowed During Heat Limit | CLGINHTLIM | CoolDuringHeatLimit | 1709 | 727 | ADI | 193 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7060 | 4
York RTU.Fan Control | Low Pressure Limit 1 | DAPMIN | DAP-Min | 2645 | 244 | ADF | 194 | 0.01 ... 1 in wc (2.5 ... 250 Pa) |  | TRUE | 4 | 100ths | in wc | 507:58 | 0.01 | 1 |  |  | 100ths | Pa | 507:53 | 2.5 | 250 |  |  | 7038 | 3
York RTU.Fan Control | Time | DAPALMDLY | DAP-AlmDly | 2645 | 245 | ADF | 195 | 0 ... 600 seconds |  | TRUE | 18 | 1s | seconds | 507:73 | 0 | 600 |  |  | 1s | seconds | 507:73 | 0 | 600 |  |  | 7040 | 3
York RTU.Hot Gas Reheat | Evaporator Coil Temp | EVAP-T | Evaporator Coil Temp | 1675 | 100 | ADF | 196 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7026 | 20
York RTU.Hot Gas Reheat | Hot Gas Reheat Bleed Valve Command | HGRB-C | Hot Gas Reheat Bleed Valve Command | 2644 | 238 | BO | 17 | 0 = Close 1 = Open |  | FALSE | 9 |  | Close/Open | 939 | [5 empty] | Close/Open | 939 |  |  |  |  | 7029 | 20
York RTU.Cooling Control | FDD Alarm Enable | FDDALMEN | FDD Alarm Enable | 1714 | 236 | ADI | 196 | 0 = Disable 1 = Enable |  | TRUE | 9 |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 |  |  |  |  | 7062 | 4
York RTU.Cooling Control | SZ VAV Operating Cooling Setpoint | OPRDATCLSP | Operating Cooling Discharge Air Temp Setpoint | 2644 | 39 | ADF | 197 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7050 | 4
York RTU.Economizer | Econ Sensor Fault Indications | ECONSNSFLT | Econ Sensor Fault Indications | 1675 | 1605 | ADI | 197 | 0 = Disable 1 = Enable |  | TRUE | 9 |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 |  |  |  |  | 7033 | 19
York RTU.Cooling Control | Modulating Condenser Fan 1 Output | CNDFAN1VFD | Modulating Condenser Fan 1 Output | 2644 | 293 | AO | 7 | 0 ... 100 % |  | FALSE | 4 | 10ths | % | 507:98 | 0 | 100 |  |  | 10ths | % | 507:98 | 0 | 100 |  |  | 7065 | 4
York RTU.Cooling Control | Modulating Condenser Fan 2 Output | CNDFAN2VFD | Modulating Condenser Fan 2 Output | 2644 | 294 | AO | 8 | 0 ... 100 % |  | FALSE | 4 | 10ths | % | 507:98 | 0 | 100 |  |  | 10ths | % | 507:98 | 0 | 100 |  |  | 7066 | 4
York RTU.Cooling Control | Modulating Compressor Output | MODCOMPOUT | Modulating Compressor Output | 2644 | 292 | AO | 9 | 0 ... 100 % |  | FALSE | 4 | 10ths | % | 507:98 | 0 | 100 |  |  | 10ths | % | 507:98 | 0 | 100 |  |  | 7067 | 4
York RTU.Cooling Control | Circuit 1 OAT Cooling Cutout | CLOACOSP1 | Circuit 1 OAT Cooling Cutout | 2644 | 442 | ADF | 198 | ... 100 deg F ( ... 38 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 |  | 100 | 7070 |  | 1s | deg C | 507:62 |  | 38 | 7070 |  | 7068 | 4
York RTU.Cooling Control | Circuit 2 OAT Cooling Cutout | CLOACOSP2 | Circuit 2 OAT Cooling Cutout | 2644 | 443 | ADF | 199 | ... 100 deg F ( ... 38 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 |  | 100 | 7071 |  | 1s | deg C | 507:62 |  | 38 | 7071 |  | 7069 | 4
York RTU.Cooling Control | Compressor VFD Alarm | COMPVFDALM | Compressor VFD Alarm | 2644 | 484 | ADI | 198 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7075 | 4
York RTU.Cooling Control | Saturated Suction Temperature 1 | SATSUCTMP1 | Saturated Suction Temperature 1 | 2644 | 374 | ADF | 200 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7078 | 4
York RTU.Cooling Control | Saturated Discharge Temperature 1 | SATDISTMP1 | Saturated Discharge Temperature 1 | 2644 | 370 | ADF | 201 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7079 | 4
York RTU.Cooling Control | Saturated Discharge Temperature 2 | SATDISTMP2 | Saturated Discharge Temperature 2 | 2644 | 371 | ADF | 202 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7080 | 4
York RTU.Cooling Control | Saturated Suction Temperature 2 | SATSUCTMP2 | Saturated Suction Temperature 2 | 2644 | 375 | ADF | 203 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7081 | 4
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Discharge Line Pressure | DLP1 | Discharge Line Pressure 1 | 2644 | 378 | AI | 34 | 0 ... 750 psi (0 ... 5172 kPa) |  | FALSE | 4 | 10ths | psi | 507:56 | 0 | 750 |  |  | 1s | kPa | 507:54 | 0 | 5172 |  |  | 7024 | 6
York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics | Discharge Line Temperature | DLT1 | Discharge Line Temperature 1 | 2644 | 380 | AI | 35 | -50 ... 250 deg F (-45.6 ... 121.1 deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 | -50 | 250 |  |  | 10ths | deg C | 507:62 | -45.6 | 121.1 |  |  | 7025 | 6
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Discharge Line Pressure | DLP2 | Discharge Line Pressure 2 | 2644 | 379 | AI | 36 | 0 ... 750 psi (0 ... 5172 kPa) |  | FALSE | 4 | 10ths | psi | 507:56 | 0 | 750 |  |  | 1s | kPa | 507:54 | 0 | 5172 |  |  | 7024 | 8
York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics | Discharge Line Temperature | DLT2 | Discharge Line Temperature 2 | 2644 | 381 | AI | 37 | -50 ... 250 deg F (-45.6 ... 121.1 deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 | -50 | 250 |  |  | 10ths | deg C | 507:62 | -45.6 | 121.1 |  |  | 7025 | 8
York RTU.Cooling Control | Suction Superheat 1 | SUCSUPRHT1 | Suction Superheat 1 | 2644 | 366 | ADF | 204 | deg F (deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 |  |  |  |  | 10ths | deg C | 507:62 |  |  |  |  | 7082 | 4
York RTU.HVAC Zone | Space Temperature Setpoint Offset Range | SSORANGE | SSORange | 1709 | 50 | ADF | 205 | 0 ... 5 delta deg F (0 ... 3 delta deg C) |  | TRUE | 4 | 10ths | delta deg F | 507:120 | 0 | 5 |  |  | 10ths | delta deg C | 507:359 | 0 | 3 |  |  | 7028 | 25
York RTU.Hot Gas Reheat | Operational Evap Temperature Sp | OPREVAPSP | OprEvapTempSp | 1709 | 729 | ADF | 206 | 0 ... 100 deg F (0 ... 100 deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 | 0 | 100 |  |  | 10ths | deg C | 507:62 | 0 | 100 |  |  | 7015 | 20
York RTU.Hot Gas Reheat | Operational HGR Temperature Sp | OPRHGRTPSP | OprHGRTempSp | 1709 | 730 | ADF | 207 | 0 ... 100 deg F (0 ... 100 deg C) |  | FALSE | 4 | 10ths | deg F | 507:64 | 0 | 100 |  |  | 10ths | deg C | 507:62 | 0 | 100 |  |  | 7016 | 20
York RTU.Hot Gas Reheat | Dehum Evap Low Setpoint | DHMEVPLWSP | DehumEvapLowSp | 1709 | 725 | ADF | 208 | 40 ... deg F (4 ... deg C) |  | TRUE | 4 | 10ths | deg F | 507:64 | 40 |  |  | 7017 | 10ths | deg C | 507:62 | 4 |  |  | 7017 | 7018 | 20
York RTU.Hot Gas Reheat | Dehumidify In Satisfied | SATISDEHUM | SatisfiedDehum | 1709 | 726 | ADI | 209 | 0 = False 1 = True |  | TRUE | 9 |  | False/True | 1701 | [5 empty] | False/True | 1701 |  |  |  |  | 7012 | 20
York RTU.Hot Gas Reheat | Modulating HGR Valve Full Open Allowed | HGRFULLOPN | ModHGRFullOpenAllowed | 1709 | 728 | ADI | 210 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7024 | 20
York RTU.Hot Gas Reheat | Condenser Fan 2 OAT Cutout Setpoint | CF2OACUTSP | CondFan2OATCutoutSP | 1709 | 732 | ADF | 211 | 50 ... 80 deg F (10 ... 27 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 50 | 80 |  |  | 1s | deg C | 507:62 | 10 | 27 |  |  | 7023 | 20
York RTU.Cooling Control | Cooling Rapid Start Enable | CLGRPDSRT | Cooling Rapid Start Enable | 1714 | 267 | ADI | 212 | 0 = Disable 1 = Enable |  | TRUE | 9 |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 |  |  |  |  | 7101 | 4
York RTU.Heating Control | Heating Rapid Start Enable | HTGRPDSRT | Heating Rapid Start Enable | 1714 | 268 | ADI | 213 | 0 = Disable 1 = Enable |  | TRUE | 9 |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 |  |  |  |  | 7056 | 13
York RTU.Heating Control | SZ VAV Operating Heating Setpoint | OPHTGDATSP | Operating Heating Discharge Air Temp Setpoint | 2644 | 40 | ADF | 214 | deg F (deg C) |  | FALSE | 4 | 1s | deg F | 507:64 |  |  |  |  | 1s | deg C | 507:62 |  |  |  |  | 7049 | 13
York RTU.Economizer | Mixed Air Temperature Cooling Limit | MATCLGLIM | Mixed Air Temperature Cooling Limit | 2644 | 274 | ADI | 215 | 0 = Disable 1 = Enable |  | TRUE | 9 |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 |  |  |  |  | 7034 | 19
York RTU.Heat Pump Control | OAT Heat Pump Cutout | OAHPCUTOUT | OAT Heat Pump Cutout | 1714 | 273 | ADF | 216 | -20 ... 50 deg F (-29 ... 10 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | -20 | 50 |  |  | 1s | deg C | 507:62 | -29 | 10 |  |  | 7017 | 38
York RTU.Hot Gas Reheat | Use OprST for HGR | USEOPSTHGR | Use OprST for HGR | 1714 | 272 | ADI | 217 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7031 | 20
York RTU.Hot Gas Reheat | Min Heating Setpoint | HGRVLVMIN | HGR Mod Valve Min Setpoint | 1714 | 274 | ADF | 218 | 0 ... 100 % |  | TRUE | 4 | 10ths | % | 507:98 | 0 | 100 |  |  | 10ths | % | 507:98 | 0 | 100 |  |  | 7014 | 20
York RTU.Hot Gas Reheat | Max Heating Setpoint | HGRVLVMAX | HGR Mod Valve Max Setpoint | 1714 | 275 | ADF | 219 | 0 ... 100 % |  | TRUE | 4 | 10ths | % | 507:98 | 0 | 100 |  |  | 10ths | % | 507:98 | 0 | 100 |  |  | 7013 | 20
York RTU.Hot Gas Reheat | HGR Humidity Setpoint Differential | HGRDIFF | HGR Humidity Setpoint Differential | 1675 | 872 | ADF | 220 | 1 ... 10 % |  | TRUE | 4 | 1s | % | 507:98 | 1 | 10 |  |  | 1s | % | 507:98 | 1 | 10 |  |  | 7008 | 20
York RTU.Hot Gas Reheat | Use DFS For Dehum | USEDFSHGR | UseDFSforDehum | 1709 | 721 | ADI | 221 | 0 = No 1 = Yes |  | TRUE | 9 |  | No/Yes | 854 | [5 empty] | No/Yes | 854 |  |  |  |  | 7010 | 20
York RTU.Hot Gas Reheat | Aux Mode | HYBRIDMODE | Hybrid Mode | 1714 | 251 | ADI | 222 | 0 = Off 1 = On |  | TRUE | 9 |  | Off/On | 647 | [5 empty] | Off/On | 647 |  |  |  |  | 7009 | 20
York RTU.Cooling Control | Cooling Rapid Start Time | CLGSTRTIME | Cooling Rapid Start Time | 1714 | 269 | ADF | 223 | 2 ... 30 minutes |  | TRUE | 4 | 1s | minutes | 507:72 | 2 | 30 |  |  | 1s | minutes | 507:72 | 2 | 30 |  |  | 7102 | 4
York RTU.Heating Control | Heating Rapid Start Time | HTGSTRTIME | Heating Rapid Start Time | 1714 | 270 | ADF | 224 | 2 ... 30 minutes |  | TRUE | 4 | 1s | minutes | 507:72 | 2 | 30 |  |  | 1s | minutes | 507:72 | 2 | 30 |  |  | 7057 | 13
York RTU.Cooling Control | A2L Leak Detector Alarm | A2LLEAKALM | A2L Leak Detector Alarm | 1714 | 276 | ADI | 225 | 0 = Normal 1 = Alarm |  | FALSE | 9 |  | Normal/Alarm | 374 | [5 empty] | Normal/Alarm | 374 |  |  |  |  | 7103 | 4
York RTU.Cooling Control | A2L Leak Detector Alarm-Lockout | A2LLEAKLO | A2L Leak Detector Alarm-Lockout | 1714 | 280 | ADI | 226 | 0 = Normal 1 = Lockout |  | FALSE | 9 |  | Normal Lockout | 1604 | [5 empty] | Normal Lockout | 1604 |  |  |  |  | 7106 | 4
York RTU.Cooling Control | Condensate Overflow Switch | COS | Condensate Overflow Switch | 1714 | 277 | ADI | 227 | 0 = Alarm 1 = Normal |  | FALSE | 9 |  | Alarm/Normal | 1696 | [5 empty] | Alarm/Normal | 1696 |  |  |  |  | 7108 | 4
York RTU.Hot Gas Reheat | Neutral Air ModHGR Enable | NEUAIR-EN | Neutral Air ModHGR Enable | 1714 | 281 | ADI | 228 | 0 = Disable 1 = Enable |  | TRUE | 9 |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 |  |  |  |  | 7032 | 20
York RTU.Hot Gas Reheat | Neutral Air ModHGR Offset | NEUAIR-OFF | Neutral Air ModHGR Offset | 1714 | 282 | ADF | 229 | -10 ... 10 delta deg F (-6 ... 6 delta deg C) |  | TRUE | 4 | 1s | delta deg F | 507:120 | -10 | 10 |  |  | 1s | delta deg C | 507:359 | -6 | 6 |  |  | 7033 | 20
York RTU.Heat Pump Control | Dual Fuel OAT HP Cutout | DFOAHPCUT | Dual Fuel OAT HP Cutout | 1714 | 285 | ADF | 230 | 0 ... 65 deg F (-18 ... 18 deg C) |  | TRUE | 4 | 1s | deg F | 507:64 | 0 | 65 |  |  | 1s | deg C | 507:62 | -18 | 18 |  |  | 7019 | 38
York RTU.Cooling Control | Condensate Alarm Enable | COS-EN | COS-En | 1709 | 797 | ADI | 229 | 0 = Disable 1 = Enable |  | TRUE | 9 |  | Disable/Enable | 658 | [5 empty] | Disable/Enable | 658 |  |  |  |  | 7107 | 4

## FactConf
Attribute Fullname | EM Object Id | AttributeId | IP Value | IP Unit | IP Unit Id | SI Value | SI Unit | SI Unit Id

## Events
Type | Event Type | Obj. Instance | MV Instance Active | MV Instance Inactive | Active Set Id | Active Enum Id | Active Text | Inactive Set Id | Inactive Enum Id | Inactive Text | DataSource: Attribute Fullname | DataSource: EM Obj. Id | DataSource: Attr. Id | AlarmStates Ids | AlarmStates Texts | Network Sensor Id | Network Sensor | Auto Clear | Xline
Group | Critical |  | 30000 | 29999 | 1716 |  |  | 1719
Event | Critical | 2 |  |  | 1716 | 104 | C1 Locked Out Due to High Pressure | 1719 | 104 | C1 Locked Out Due to High Pressure | York RTU.Cooling Control.DX Cooling Circuit 1.High Pressure Lockout | 5 | 7010 | 1 | Lockout | 0 | None | FALSE | TRUE
Event | Critical | 24 |  |  | 1716 | 105 | C2 Locked Out Due to High Pressure | 1719 | 105 | C2 Locked Out Due to High Pressure | York RTU.Cooling Control.DX Cooling Circuit 2.High Pressure Lockout | 7 | 7010 | 1 | Lockout | 0 | None | FALSE | TRUE
Event | Critical | 25 |  |  | 1716 | 106 | C3 Locked Out Due to High Pressure | 1719 | 106 | C3 Locked Out Due to High Pressure | York RTU.Cooling Control.DX Cooling Circuit 3.High Pressure Lockout | 9 | 7010 | 1 | Lockout | 0 | None | FALSE | TRUE
Event | Critical | 26 |  |  | 1716 | 107 | C4 Locked Out Due to High Pressure | 1719 | 107 | C4 Locked Out Due to High Pressure | York RTU.Cooling Control.DX Cooling Circuit 4.High Pressure Lockout | 11 | 7010 | 1 | Lockout | 0 | None | FALSE | TRUE
Event | Critical | 31 |  |  | 1716 | 108 | C1 Locked Out Due to Low Pressure | 1719 | 108 | C1 Locked Out Due to Low Pressure | York RTU.Cooling Control.DX Cooling Circuit 1.Low Pressure Lockout | 5 | 7012 | 1 | Lockout | 0 | None | FALSE | TRUE
Event | Critical | 32 |  |  | 1716 | 109 | C2 Locked Out Due to Low Pressure | 1719 | 109 | C2 Locked Out Due to Low Pressure | York RTU.Cooling Control.DX Cooling Circuit 2.Low Pressure Lockout | 7 | 7012 | 1 | Lockout | 0 | None | FALSE | TRUE
Event | Critical | 33 |  |  | 1716 | 110 | C3 Locked Out Due to Low Pressure | 1719 | 110 | C3 Locked Out Due to Low Pressure | York RTU.Cooling Control.DX Cooling Circuit 3.Low Pressure Lockout | 9 | 7012 | 1 | Lockout | 0 | None | FALSE | TRUE
Event | Critical | 34 |  |  | 1716 | 111 | C4 Locked Out Due to Low Pressure | 1719 | 111 | C4 Locked Out Due to Low Pressure | York RTU.Cooling Control.DX Cooling Circuit 4.Low Pressure Lockout | 11 | 7012 | 1 | Lockout | 0 | None | FALSE | TRUE
Event | Critical | 39 |  |  | 1716 | 112 | C1 Locked Out Due to Coil Freeze | 1719 | 112 | C1 Locked Out Due to Coil Freeze | York RTU.Cooling Control.DX Cooling Circuit 1.Freeze Condition Lockout | 5 | 7014 | 1 | Lockout | 0 | None | FALSE | TRUE
Event | Critical | 40 |  |  | 1716 | 113 | C2 Locked Out Due to Coil Freeze | 1719 | 113 | C2 Locked Out Due to Coil Freeze | York RTU.Cooling Control.DX Cooling Circuit 2.Freeze Condition Lockout | 7 | 7014 | 1 | Lockout | 0 | None | FALSE | TRUE
Event | Critical | 41 |  |  | 1716 | 114 | C3 Locked Out Due to Coil Freeze | 1719 | 114 | C3 Locked Out Due to Coil Freeze | York RTU.Cooling Control.DX Cooling Circuit 3.Freeze Condition Lockout | 9 | 7014 | 1 | Lockout | 0 | None | FALSE | TRUE
Event | Critical | 42 |  |  | 1716 | 115 | C4 Locked Out Due to Coil Freeze | 1719 | 115 | C4 Locked Out Due to Coil Freeze | York RTU.Cooling Control.DX Cooling Circuit 4.Freeze Condition Lockout | 11 | 7014 | 1 | Lockout | 0 | None | FALSE | TRUE
Event | Critical | 52 |  |  | 1716 | 116 | Exhaust Fan VFD Failure | 1719 | 116 | Exhaust Fan VFD Failure | York RTU.Exhaust Fan Control.Exhaust Fan VFD Fault | 21 | 7004 | 1 | Alarm | 0 | None | FALSE | TRUE
Event | Critical | 53 |  |  | 1716 | 117 | HS1 Locked Out Due to Limit Switch | 1719 | 117 | HS1 Locked Out Due to Limit Switch | York RTU.Heating Control.Heat Limit1 Switch Lockout | 13 | 7010 | 1 | Lockout | 0 | None | FALSE | TRUE
Event | Critical | 55 |  |  | 1716 | 118 | HS2 Locked Out Due to Limit Switch | 1719 | 118 | HS2 Locked Out Due to Limit Switch | York RTU.Heating Control.Heat Limit2 Switch Lockout | 13 | 7012 | 1 | Lockout | 0 | None | FALSE | TRUE
Event | Critical | 57 |  |  | 1716 | 119 | HS3 Locked Out Due to Limit Switch | 1719 | 119 | HS3 Locked Out Due to Limit Switch | York RTU.Heating Control.Heat Limit3 Switch Lockout | 13 | 7014 | 1 | Lockout | 0 | None | FALSE | TRUE
Event | Critical | 62 |  |  | 1716 | 127 | Unit Shutdown Due to Smoke, etc | 1719 | 127 | Unit Shutdown Due to Smoke, etc | York RTU.Shutdown Input.Shutdown Input/Smoke Detector | 27 | 7004 | 1 | Alarm | 0 | None | FALSE | TRUE
Event | Critical | 65 |  |  | 1716 | 132 | Supply Fan VFD Failure | 1719 | 132 | Supply Fan VFD Failure | York RTU.Fan Control.Fan VFD Fault | 3 | 7002 | 1 | Alarm | 0 | None | FALSE | TRUE
Event | Critical | 66 |  |  | 1716 | 133 | No Heat-Cool Due to Unreliable Space-T | 1719 | 133 | No Heat-Cool Due to Unreliable Space-T | York RTU.HVAC Zone.No Reliable Zone Temp Alarm | 25 | 7070 | 1 | Alarm | 0 | None | FALSE | TRUE
Event | Critical | 67 |  |  | 1716 | 125 | 4-Stage Communication Failure | 1719 | 125 | 4-Stage Communication Failure | York RTU.System Controllers.4 Stage Controller | 29 | 7005 | 1 | Offline | 0 | None | FALSE | TRUE
Event | Critical | 68 |  |  | 1716 | 126 | Economizer Communication Failure | 1719 | 126 | Economizer Communication Failure | York RTU.System Controllers.Econ Controller | 29 | 7004 | 1 | Offline | 0 | None | FALSE | TRUE
Event | Critical | 87 |  |  | 1716 | 120 | Outputs Disabled Due to Low Input V | 1719 | 120 | Outputs Disabled Due to Low Input V | York RTU.Outputs Disabled Due to Low Input Voltage | 1 | 7012 | 1 | Yes | 0 | None | FALSE | TRUE
Event | Critical | 88 |  |  | 1716 | 121 | Outputs Limited Due to Brownout Input V | 1719 | 121 | Outputs Limited Due to Brownout Input V | York RTU.Outputs Limited Due to Low Input Voltage | 1 | 7013 | 1 | Yes | 0 | None | FALSE | TRUE
Event | Critical | 89 |  |  | 1716 | 128 | Unit Locked Out Due to APS | 1719 | 128 | Unit Locked Out Due to APS | York RTU.Fan Control.Unit Locked Out Due to Air Proving Switch | 3 | 7030 | 1 | Alarm | 0 | None | FALSE | TRUE
Event | Critical | 91 |  |  | 1716 | 131 | Unit Locked Out Due to Supply Fan OL | 1719 | 131 | Unit Locked Out Due to Supply Fan OL | York RTU.Fan Control.Unit Locked Out Supply Fan Overload | 3 | 7034 | 1 | Alarm | 0 | None | FALSE | TRUE
Event | Critical | 141 |  |  | 1716 | 130 | Unit Locked Out Due to High Duct-P | 1719 | 130 | Unit Locked Out Due to High Duct-P | York RTU.Fan Control.Unit Shutdown Due High Duct Static Pressure | 3 | 7033 | 1 | Alarm | 0 | None | FALSE | TRUE
Event | Critical | 246 |  |  | 1716 | 198 | Freeze Protect Disabled - Bad Sensor | 1719 | 198 | Freeze Protect Disabled - Bad Sensor | York RTU.Cooling Control.Alarm Reporting | 4 | 7058 | 1 | Alarm | 0 | None | FALSE | TRUE
Event | Critical | 248 |  |  | 1716 | 201 | C1 Locked Out - Exceeded Op Env Limits | 1719 | 201 | C1 Locked Out - Exceeded Op Env Limits | York RTU.Cooling Control.Compressor 1 Lockout | 4 | 7073 | 1 | Lockout | 0 | None | FALSE | TRUE
Event | Critical | 249 |  |  | 1716 | 203 | C1 Locked Out Due to Oil Switch | 1719 | 203 | C1 Locked Out Due to Oil Switch | York RTU.Cooling Control.Compressor Stage 1 Lockout | 4 | 7074 | 1 | Lockout | 0 | None | FALSE | TRUE
Event | Critical | 250 |  |  | 1716 | 202 | C1 Locked Out Due to VFD Failure | 1719 | 202 | C1 Locked Out Due to VFD Failure | York RTU.Cooling Control.Compressor VFD Alarm | 4 | 7075 | 1 | Alarm | 0 | None | FALSE | TRUE
Event | Critical | 252 |  |  | 1716 | 204 | C1 Locked Out - High Discharge Pressure | 1719 | 204 | C1 Locked Out - High Discharge Pressure | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.High Pressure Lockout | 6 | 7027 | 1 | Lockout | 0 | None | FALSE | TRUE
Event | Critical | 254 |  |  | 1716 | 208 | C1 Locked Out - Low Suction Pressure | 1719 | 208 | C1 Locked Out - Low Suction Pressure | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Low Pressure Lockout | 6 | 7029 | 1 | Lockout | 0 | None | FALSE | TRUE
Event | Critical | 257 |  |  | 1716 | 205 | C2 Locked Out - High Discharge Pressure | 1719 | 205 | C2 Locked Out - High Discharge Pressure | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.High Pressure Lockout | 8 | 7027 | 1 | Lockout | 0 | None | FALSE | TRUE
Event | Critical | 258 |  |  | 1716 | 209 | C2 Locked Out - Low Suction Pressure | 1719 | 209 | C2 Locked Out - Low Suction Pressure | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Low Pressure Lockout | 8 | 7029 | 1 | Lockout | 0 | None | FALSE | TRUE
Event | Critical | 269 |  |  | 1716 | 206 | C3 Locked Out - High Discharge Pressure | 1719 | 206 | C3 Locked Out - High Discharge Pressure | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics.High Pressure Lockout | 10 | 7027 | 1 | Lockout | 0 | None | FALSE | TRUE
Event | Critical | 270 |  |  | 1716 | 210 | C3 Locked Out - Low Suction Pressure | 1719 | 210 | C3 Locked Out - Low Suction Pressure | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics.Low Pressure Lockout | 10 | 7029 | 1 | Lockout | 0 | None | FALSE | TRUE
Event | Critical | 273 |  |  | 1716 | 207 | C4 Locked Out - High Discharge Pressure | 1719 | 207 | C4 Locked Out - High Discharge Pressure | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics.High Pressure Lockout | 12 | 7027 | 1 | Lockout | 0 | None | FALSE | TRUE
Event | Critical | 274 |  |  | 1716 | 211 | C4 Locked Out - Low Suction Pressure | 1719 | 211 | C4 Locked Out - Low Suction Pressure | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics.Low Pressure Lockout | 12 | 7029 | 1 | Lockout | 0 | None | FALSE | TRUE
Event | Critical | 275 |  |  | 1716 | 226 | Defrost Disabled - Bad Sensor | 1719 | 226 | Defrost Disabled - Bad Sensor | York RTU.Heat Pump Control.Defrost | 38 | 7016 | 1 | Alarm | 0 | None | FALSE | TRUE
Event | Critical | 276 |  |  | 1716 | 227 | C1 Locked Out - High Discharge Line Temp | 1719 | 227 | C1 Locked Out - High Discharge Line Temp | York RTU.Cooling Control.High Discharge Line Temp Lockout | 4 | 7100 | 1 | Alarm | 0 | None | FALSE | TRUE
Event | Critical | 71 |  |  | 1716 | 230 | A2L Leak Detector Alarm | 1719 | 230 | A2L Leak Detector Alarm | York RTU.Cooling Control.A2L Leak Detector Alarm | 4 | 7103 | 1 | Alarm | 0 | None | FALSE | TRUE
Event | Critical | 73 |  |  | 1716 | 231 | A2L Leak Detector Alarm-Lockout | 1719 | 231 | A2L Leak Detector Alarm-Lockout | York RTU.Cooling Control.A2L Leak Detector Alarm-Lockout | 4 | 7106 | 1 | Lockout | 0 | None | FALSE | TRUE
Event | Critical | 74 |  |  | 1716 | 188 | Cooling Locked Out - Condensate Overflow | 1719 | 188 | Cooling Locked Out - Condensate Overflow | York RTU.Cooling Control.Condensate Overflow Switch | 4 | 7108 | 0 | Alarm | 0 | None | FALSE | TRUE
Group | ServicePriority |  | 29998 | 29997 | 1717 |  |  | 1720
Event | ServicePriority | 1 |  |  | 1717 | 108 | Evaporator Coil Temp 1 Sensor Failure | 1720 | 108 | Evaporator Coil Temp 1 Sensor Failure | York RTU.Cooling Control.DX Cooling Circuit 1.Evaporator Coil Temp Sensor Fault | 5 | 7017 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | ServicePriority | 3 |  |  | 1717 | 109 | Condenser Coil Temp 1 Sensor Failure | 1720 | 109 | Condenser Coil Temp 1 Sensor Failure | York RTU.Cooling Control.DX Cooling Circuit 1.Condenser Coil Temp Sensor Fault | 5 | 7018 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | ServicePriority | 4 |  |  | 1717 | 110 | Evaporator Coil Temp 2 Sensor Failure | 1720 | 110 | Evaporator Coil Temp 2 Sensor Failure | York RTU.Cooling Control.DX Cooling Circuit 2.Evaporator Coil Temp Sensor Fault | 7 | 7017 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | ServicePriority | 5 |  |  | 1717 | 111 | Condenser Coil Temp 2 Sensor Failure | 1720 | 111 | Condenser Coil Temp 2 Sensor Failure | York RTU.Cooling Control.DX Cooling Circuit 2.Condenser Coil Temp Sensor Fault | 7 | 7018 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | ServicePriority | 6 |  |  | 1717 | 112 | Evaporator Coil Temp 3 Sensor Failure | 1720 | 112 | Evaporator Coil Temp 3 Sensor Failure | York RTU.Cooling Control.DX Cooling Circuit 3.Evaporator Coil Temp Sensor Fault | 9 | 7017 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | ServicePriority | 7 |  |  | 1717 | 113 | Condenser Coil Temp 3 Sensor Failure | 1720 | 113 | Condenser Coil Temp 3 Sensor Failure | York RTU.Cooling Control.DX Cooling Circuit 3.Condenser Coil Temp Sensor Fault | 9 | 7018 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | ServicePriority | 8 |  |  | 1717 | 114 | Evaporator Coil Temp 4 Sensor Failure | 1720 | 114 | Evaporator Coil Temp 4 Sensor Failure | York RTU.Cooling Control.DX Cooling Circuit 4.Evaporator Coil Temp Sensor Fault | 11 | 7017 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | ServicePriority | 9 |  |  | 1717 | 115 | Condenser Coil Temp 4 Sensor Failure | 1720 | 115 | Condenser Coil Temp 4 Sensor Failure | York RTU.Cooling Control.DX Cooling Circuit 4.Condenser Coil Temp Sensor Fault | 11 | 7018 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | ServicePriority | 11 |  |  | 1717 | 103 | Building Pressure Sensor Failure | 1720 | 103 | Building Pressure Sensor Failure | York RTU.Exhaust Fan Control.Building Static Pressure Sensor Fault | 21 | 7015 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | ServicePriority | 12 |  |  | 1717 | 104 | Outdoor Air Temperature Sensor Failure | 1720 | 104 | Outdoor Air Temperature Sensor Failure | York RTU.Weather Information.Outdoor Air Temperature Sensor Fault | 26 | 7014 | 1 | Alarm | 1 | Air temperature sensor failure/fault | FALSE | TRUE
Event | ServicePriority | 13 |  |  | 1717 | 105 | Return Air Temperature Sensor Failure | 1720 | 105 | Return Air Temperature Sensor Failure | York RTU.HVAC Zone.Return Air Temperature Sensor Fault | 25 | 7039 | 1 | Alarm | 1 | Air temperature sensor failure/fault | FALSE | TRUE
Event | ServicePriority | 21 |  |  | 1717 | 106 | Supply Air Temperature Sensor Failure | 1720 | 106 | Supply Air Temperature Sensor Failure | York RTU.Fan Control.Supply Air Temperature Sensor Fault | 3 | 7025 | 1 | Alarm | 0 | None | FALSE | TRUE
Event | ServicePriority | 64 |  |  | 1717 | 117 | Unit Shutdown Due to Supply Fan Overload | 1720 | 117 | Unit Shutdown Due to Supply Fan Overload | York RTU.Fan Control.Fan Overload | 3 | 7003 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | ServicePriority | 77 |  |  | 1717 | 118 | Main Controller Calibration Error | 1720 | 118 | Main Controller Calibration Error | York RTU.System Controllers.UCB.Calibration Data Fault | 32 | 7004 | 0 | Yes | 0 | None | FALSE | FALSE
Event | ServicePriority | 78 |  |  | 1717 | 119 | FDDM Controller Calibration Error | 1720 | 119 | FDDM Controller Calibration Error | York RTU.System Controllers.FDD Master.Calibration Data Fault | 35 | 7004 | 0 | Yes | 0 | None | FALSE | FALSE
Event | ServicePriority | 79 |  |  | 1717 | 120 | Econ Controller Calibration Error | 1720 | 120 | Econ Controller Calibration Error | York RTU.System Controllers.Econ.Calibration Data Fault | 33 | 7004 | 0 | Yes | 0 | None | FALSE | FALSE
Event | ServicePriority | 80 |  |  | 1717 | 121 | 4 Stage Controller Calibration Error | 1720 | 121 | 4 Stage Controller Calibration Error | York RTU.System Controllers.4Stage.Calibration Data Fault | 34 | 7004 | 0 | Yes | 0 | None | FALSE | FALSE
Event | ServicePriority | 90 |  |  | 1717 | 116 | Unit Shutdown Due to Air Proving Switch | 1720 | 116 | Unit Shutdown Due to Air Proving Switch | York RTU.Fan Control.Unit Shutdown Due to Air Proving Switch | 3 | 7031 | 4 | Proof Lost Fault | 0 | None | FALSE | FALSE
Event | ServicePriority | 148 |  |  | 1717 | 123 | FDDS Controller Calibration Error | 1720 | 123 | FDDS Controller Calibration Error | York RTU.System Controllers.FDD Slave.Calibration Data Fault | 36 | 7004 | 0 | Yes | 0 | None | FALSE | FALSE
Event | ServicePriority | 245 |  |  | 1717 | 1 | Firmware versions do not match package | 1720 | 1 | Firmware versions do not match package | York RTU.Firmware Status | 1 | 7005 | 1 | Firmware Versions Do Not Match the Package | 0 | None | FALSE | FALSE
Event | ServicePriority | 247 |  |  | 1717 | 161 | C1 Shutdown - Exceeded Op Env Limits | 1720 | 161 | C1 Shutdown - Exceeded Op Env Limits | York RTU.Cooling Control.Alarm Points | 4 | 7072 | 0 | Alarm | 0 | None | FALSE | FALSE
Event | ServicePriority | 251 |  |  | 1717 | 162 | C1 Shutdown - High Discharge Pressure | 1720 | 162 | C1 Shutdown - High Discharge Pressure | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.High Pressure Limit | 6 | 7026 | 0 | Alarm | 0 | None | FALSE | FALSE
Event | ServicePriority | 253 |  |  | 1717 | 166 | C1 Shutdown - Low Suction Pressure | 1720 | 166 | C1 Shutdown - Low Suction Pressure | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Low Pressure Limit | 6 | 7028 | 0 | Alarm | 0 | None | FALSE | FALSE
Event | ServicePriority | 255 |  |  | 1717 | 163 | C2 Shutdown - High Discharge Pressure | 1720 | 163 | C2 Shutdown - High Discharge Pressure | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.High Pressure Limit | 8 | 7026 | 0 | Alarm | 0 | None | FALSE | FALSE
Event | ServicePriority | 256 |  |  | 1717 | 167 | C2 Shutdown - Low Suction Pressure | 1720 | 167 | C2 Shutdown - Low Suction Pressure | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Low Pressure Limit | 8 | 7028 | 0 | Alarm | 0 | None | FALSE | FALSE
Event | ServicePriority | 267 |  |  | 1717 | 164 | C3 Shutdown - High Discharge Pressure | 1720 | 164 | C3 Shutdown - High Discharge Pressure | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics.High Pressure Limit | 10 | 7026 | 0 | Alarm | 0 | None | FALSE | FALSE
Event | ServicePriority | 268 |  |  | 1717 | 168 | C3 Shutdown - Low Suction Pressure | 1720 | 168 | C3 Shutdown - Low Suction Pressure | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics.Low Pressure Limit | 10 | 7028 | 0 | Alarm | 0 | None | FALSE | FALSE
Event | ServicePriority | 271 |  |  | 1717 | 165 | C4 Shutdown - High Discharge Pressure | 1720 | 165 | C4 Shutdown - High Discharge Pressure | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics.High Pressure Limit | 12 | 7026 | 0 | Alarm | 0 | None | FALSE | FALSE
Event | ServicePriority | 272 |  |  | 1717 | 169 | C4 Shutdown - Low Suction Pressure | 1720 | 169 | C4 Shutdown - Low Suction Pressure | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics.Low Pressure Limit | 12 | 7028 | 0 | Alarm | 0 | None | FALSE | FALSE
Group | Service |  | 29996 | 29995 | 1718 |  |  | 1721
Event | Service | 10 |  |  | 1718 | 104 | Duct Pressure Sensor Failure | 1721 | 104 | Duct Pressure Sensor Failure | York RTU.Fan Control.Duct Static Pressure Sensor Fault | 3 | 7026 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | Service | 14 |  |  | 1718 | 105 | Return Air Humidity Sensor Failure | 1721 | 105 | Return Air Humidity Sensor Failure | York RTU.HVAC Zone.Space Humidity Sensor Fault | 25 | 7034 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | Service | 15 |  |  | 1718 | 106 | Outdoor Air Humidity Sensor Failure | 1721 | 106 | Outdoor Air Humidity Sensor Failure | York RTU.Weather Information.Outdoor Air Humidity Sensor Fault | 26 | 7015 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | Service | 16 |  |  | 1718 | 107 | Supply Humidity Sensor Failure | 1721 | 107 | Supply Humidity Sensor Failure | York RTU.Economizer.Supply Air Humidity Sensor Fault | 19 | 7023 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | Service | 17 |  |  | 1718 | 108 | Indoor Air Quality Sensor Failure | 1721 | 108 | Indoor Air Quality Sensor Failure | York RTU.HVAC Zone.Indoor Air Quality Sensor Fault | 25 | 7033 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | Service | 18 |  |  | 1718 | 109 | Outdoor Air Quality Sensor Failure | 1721 | 109 | Outdoor Air Quality Sensor Failure | York RTU.Weather Information.Outdoor Air Quality Sensor Fault | 26 | 7016 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | Service | 19 |  |  | 1718 | 110 | Fresh Air Intake Sensor Failure | 1721 | 110 | Fresh Air Intake Sensor Failure | York RTU.Air Monitor Station.Fresh Air Intake Sensor Fault | 24 | 7003 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | Service | 20 |  |  | 1718 | 111 | Mixed Air Temp Sensor Failure | 1721 | 111 | Mixed Air Temp Sensor Failure | York RTU.Economizer.Mixed Air Temperature Sensor Fault | 19 | 7022 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | Service | 22 |  |  | 1718 | 112 | Space Indoor Temp Sensor Failure | 1721 | 112 | Space Indoor Temp Sensor Failure | York RTU.HVAC Zone.Space Temperature Sensor Fault | 25 | 7031 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | Service | 23 |  |  | 1718 | 113 | Space Offset Sensor Failure | 1721 | 113 | Space Offset Sensor Failure | York RTU.HVAC Zone.Space Temperature Setpoint Offset Fault | 25 | 7032 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | Service | 27 |  |  | 1718 | 132 | C1 Shutdown Due to High Pressure | 1721 | 132 | C1 Shutdown Due to High Pressure | York RTU.Cooling Control.DX Cooling Circuit 1.High Pressure Limit | 5 | 7009 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | Service | 28 |  |  | 1718 | 133 | C2 Shutdown Due to High Pressure | 1721 | 133 | C2 Shutdown Due to High Pressure | York RTU.Cooling Control.DX Cooling Circuit 2.High Pressure Limit | 7 | 7009 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | Service | 29 |  |  | 1718 | 134 | C3 Shutdown Due to High Pressure | 1721 | 134 | C3 Shutdown Due to High Pressure | York RTU.Cooling Control.DX Cooling Circuit 3.High Pressure Limit | 9 | 7009 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | Service | 30 |  |  | 1718 | 135 | C4 Shutdown Due to High Pressure | 1721 | 135 | C4 Shutdown Due to High Pressure | York RTU.Cooling Control.DX Cooling Circuit 4.High Pressure Limit | 11 | 7009 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | Service | 35 |  |  | 1718 | 136 | C1 Shutdown Due to Low Pressure | 1721 | 136 | C1 Shutdown Due to Low Pressure | York RTU.Cooling Control.DX Cooling Circuit 1.Low Pressure Limit | 5 | 7019 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | Service | 36 |  |  | 1718 | 137 | C2 Shutdown Due to Low Pressure | 1721 | 137 | C2 Shutdown Due to Low Pressure | York RTU.Cooling Control.DX Cooling Circuit 2.Low Pressure Limit | 7 | 7019 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | Service | 37 |  |  | 1718 | 138 | C3 Shutdown Due to Low Pressure | 1721 | 138 | C3 Shutdown Due to Low Pressure | York RTU.Cooling Control.DX Cooling Circuit 3.Low Pressure Limit | 9 | 7019 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | Service | 38 |  |  | 1718 | 139 | C4 Shutdown Due to Low Pressure | 1721 | 139 | C4 Shutdown Due to Low Pressure | York RTU.Cooling Control.DX Cooling Circuit 4.Low Pressure Limit | 11 | 7019 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | Service | 43 |  |  | 1718 | 140 | C1 Shutdown Due to Coil Freeze | 1721 | 140 | C1 Shutdown Due to Coil Freeze | York RTU.Cooling Control.DX Cooling Circuit 1.Freeze Condition | 5 | 7013 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | Service | 44 |  |  | 1718 | 141 | C2 Shutdown Due to Coil Freeze | 1721 | 141 | C2 Shutdown Due to Coil Freeze | York RTU.Cooling Control.DX Cooling Circuit 2.Freeze Condition | 7 | 7013 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | Service | 45 |  |  | 1718 | 142 | C3 Shutdown Due to Coil Freeze | 1721 | 142 | C3 Shutdown Due to Coil Freeze | York RTU.Cooling Control.DX Cooling Circuit 3.Freeze Condition | 9 | 7013 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | Service | 46 |  |  | 1718 | 143 | C4 Shutdown Due to Coil Freeze | 1721 | 143 | C4 Shutdown Due to Coil Freeze | York RTU.Cooling Control.DX Cooling Circuit 4.Freeze Condition | 11 | 7013 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | Service | 47 |  |  | 1718 | 145 | Low Outdoor Air Temp Cooling Cutout | 1721 | 145 | Low Outdoor Air Temp Cooling Cutout | York RTU.Cooling Control.Cooling Lockout due to Low Outdoor Air Temp | 4 | 7037 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | Service | 48 |  |  | 1718 | 101 | Econ Economizing When It Should Not | 1721 | 101 | Econ Economizing When It Should Not | York RTU.Economizer.Economizing When Should Not | 19 | 7021 | 1 | Alarm | 3 | Economizing when it should not | FALSE | TRUE
Event | Service | 49 |  |  | 1718 | 100 | Econ Not Economizing When It Should | 1721 | 100 | Econ Not Economizing When It Should | York RTU.Economizer.Not Economizing When Should | 19 | 7019 | 1 | Alarm | 2 | Not economizing when it should | FALSE | TRUE
Event | Service | 50 |  |  | 1718 | 102 | Economizer Damper Not Modulating | 1721 | 102 | Economizer Damper Not Modulating | York RTU.Economizer.Damper Not Modulating | 19 | 7020 | 1 | Alarm | 4 | Damper not modulating | FALSE | TRUE
Event | Service | 51 |  |  | 1718 | 103 | Economizer Letting In Excess Outdoor Air | 1721 | 103 | Economizer Letting In Excess Outdoor Air | York RTU.Economizer.Excess Outdoor Air | 19 | 7018 | 1 | Alarm | 5 | Excess outdoor air | FALSE | TRUE
Event | Service | 54 |  |  | 1718 | 149 | HS1 Shutdown Due to Limit Switch | 1721 | 149 | HS1 Shutdown Due to Limit Switch | York RTU.Heating Control.Heat Limit1 Switch | 13 | 7009 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | Service | 56 |  |  | 1718 | 150 | HS2 Shutdown Due to Limit Switch | 1721 | 150 | HS2 Shutdown Due to Limit Switch | York RTU.Heating Control.Heat Limit2 Switch | 13 | 7011 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | Service | 58 |  |  | 1718 | 151 | HS3 Shutdown Due to Limit Switch | 1721 | 151 | HS3 Shutdown Due to Limit Switch | York RTU.Heating Control.Heat Limit3 Switch | 13 | 7013 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | Service | 59 |  |  | 1718 | 152 | HS1 Off Due to Gas Valve | 1721 | 152 | HS1 Off Due to Gas Valve | York RTU.Heating Control.Main Valve No Proof Fault | 13 | 7026 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | Service | 60 |  |  | 1718 | 153 | HS2 Off Due to Gas Valve | 1721 | 153 | HS2 Off Due to Gas Valve | York RTU.Heating Control.Gas Valve 2 No Proof Fault | 13 | 7027 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | Service | 61 |  |  | 1718 | 154 | HS3 Off Due to Gas Valve | 1721 | 154 | HS3 Off Due to Gas Valve | York RTU.Heating Control.Gas Valve 3 No Proof Fault | 13 | 7028 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | Service | 63 |  |  | 1718 | 167 | Dirty Filter | 1721 | 167 | Dirty Filter | York RTU.Fan Control.DFSInst | 3 | 7041 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | Service | 69 |  |  | 1718 | 162 | FDD 1 Communication Failure | 1721 | 162 | FDD 1 Communication Failure | York RTU.System Controllers.FDD Manager Controller | 29 | 7006 | 1 | Offline | 0 | None | FALSE | FALSE
Event | Service | 70 |  |  | 1718 | 163 | FDD 2 Communication Failure | 1721 | 163 | FDD 2 Communication Failure | York RTU.System Controllers.FDD Subordinate Controller | 29 | 7007 | 1 | Offline | 0 | None | FALSE | FALSE
Event | Service | 72 |  |  | 1718 | 166 | Unit has Received a Purge Request | 1721 | 166 | Unit has Received a Purge Request | York RTU.Shutdown Input.Operating Purge Command | 27 | 7000 | 1 | True | 0 | None | FALSE | FALSE
Event | Service | 81 |  |  | 1718 | 144 | Excessive Supply Air Temp Cooling | 1721 | 144 | Excessive Supply Air Temp Cooling | York RTU.Cooling Control.Excessive Supply Air Cooling Fault | 4 | 7036 | 1¦2 | Drop Stage¦Wait | 0 | None | FALSE | FALSE
Event | Service | 82 |  |  | 1718 | 155 | HS1 Gas Valve Failure | 1721 | 155 | HS1 Gas Valve Failure | York RTU.Heating Control.Main Valve On When Shouldn't Fault | 13 | 7029 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | Service | 83 |  |  | 1718 | 156 | HS2 Gas Valve Failure | 1721 | 156 | HS2 Gas Valve Failure | York RTU.Heating Control.Gas Valve 2 On When Shouldn't Fault | 13 | 7030 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | Service | 84 |  |  | 1718 | 157 | HS3 Gas Valve Failure | 1721 | 157 | HS3 Gas Valve Failure | York RTU.Heating Control.Gas Valve 3 On When Shouldn't Fault | 13 | 7031 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | Service | 85 |  |  | 1718 | 160 | Excessive Supply Air Temp Heating | 1721 | 160 | Excessive Supply Air Temp Heating | York RTU.Heating Control.Excessive Supply Air Heating Fault | 13 | 7033 | 1¦2 | Drop Stage¦Wait | 0 | None | FALSE | FALSE
Event | Service | 86 |  |  | 1718 | 161 | Heating Locked Out Due to OA Temp | 1721 | 161 | Heating Locked Out Due to OA Temp | York RTU.Heating Control.Heating Lockout due to High Outdoor Air Temp | 13 | 7032 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | Service | 92 |  |  | 1718 | 169 | Space Temperature Cooling Alarm | 1721 | 169 | Space Temperature Cooling Alarm | York RTU.HVAC Zone.Space Temperature Cooling Alarm | 25 | 7041 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | Service | 93 |  |  | 1718 | 235 | C1 Refrigerant Low | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Service Alarm | 6 | 7023 | 1 | Chiller 1 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 94 |  |  | 1718 | 236 | C2 Refrigerant Low | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Service Alarm | 8 | 7023 | 1 | Chiller 1 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 95 |  |  | 1718 | 237 | C3 Refrigerant Low | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics.Service Alarm | 10 | 7023 | 1 | Chiller 1 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 96 |  |  | 1718 | 238 | C4 Refrigerant Low | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics.Service Alarm | 12 | 7023 | 1 | Chiller 1 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 97 |  |  | 1718 | 239 | C1 Excessive Refrigerant Flow | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Service Alarm | 6 | 7023 | 2 | Chiller 2 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 98 |  |  | 1718 | 240 | C2 Excessive Refrigerant Flow | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Service Alarm | 8 | 7023 | 2 | Chiller 2 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 99 |  |  | 1718 | 241 | C3 Excessive Refrigerant Flow | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics.Service Alarm | 10 | 7023 | 2 | Chiller 2 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 100 |  |  | 1718 | 242 | C4 Excessive Refrigerant Flow | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics.Service Alarm | 12 | 7023 | 2 | Chiller 2 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 101 |  |  | 1718 | 243 | C1 Inefficient Compressor | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Service Alarm | 6 | 7023 | 3 | Chiller 3 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 102 |  |  | 1718 | 244 | C2 Inefficient Compressor | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Service Alarm | 8 | 7023 | 3 | Chiller 3 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 103 |  |  | 1718 | 245 | C3 Inefficient Compressor | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics.Service Alarm | 10 | 7023 | 3 | Chiller 3 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 104 |  |  | 1718 | 246 | C4 Inefficient Compressor | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics.Service Alarm | 12 | 7023 | 3 | Chiller 3 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 105 |  |  | 1718 | 247 | C1 Refrigerant Flow Restriction | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Service Alarm | 6 | 7023 | 4 | Chiller 4 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 106 |  |  | 1718 | 248 | C2 Refrigerant Flow Restriction | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Service Alarm | 8 | 7023 | 4 | Chiller 4 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 107 |  |  | 1718 | 249 | C3 Refrigerant Flow Restriction | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics.Service Alarm | 10 | 7023 | 4 | Chiller 4 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 108 |  |  | 1718 | 250 | C4 Refrigerant Flow Restriction | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics.Service Alarm | 12 | 7023 | 4 | Chiller 4 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 109 |  |  | 1718 | 251 | C1 High Side Heat Transfer Problem | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Service Alarm | 6 | 7023 | 5 | Chilled Water Pump 1 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 110 |  |  | 1718 | 252 | C2 High Side Heat Transfer Problem | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Service Alarm | 8 | 7023 | 5 | Chilled Water Pump 1 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 111 |  |  | 1718 | 253 | C3 High Side Heat Transfer Problem | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics.Service Alarm | 10 | 7023 | 5 | Chilled Water Pump 1 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 112 |  |  | 1718 | 254 | C4 High Side Heat Transfer Problem | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics.Service Alarm | 12 | 7023 | 5 | Chilled Water Pump 1 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 113 |  |  | 1718 | 255 | C1 Low Side Heat Transfer Problem | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Service Alarm | 6 | 7023 | 6 | Chilled Water Pump 2 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 114 |  |  | 1718 | 256 | C2 Low Side Heat Transfer Problem | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Service Alarm | 8 | 7023 | 6 | Chilled Water Pump 2 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 115 |  |  | 1718 | 257 | C3 Low Side Heat Transfer Problem | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics.Service Alarm | 10 | 7023 | 6 | Chilled Water Pump 2 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 116 |  |  | 1718 | 258 | C4 Low Side Heat Transfer Problem | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics.Service Alarm | 12 | 7023 | 6 | Chilled Water Pump 2 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 117 |  |  | 1718 | 259 | C1 Reduce Evaporator Airflow | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Service Alarm | 6 | 7023 | 7 | Chilled Water Pump 3 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 118 |  |  | 1718 | 260 | C2 Reduce Evaporator Airflow | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Service Alarm | 8 | 7023 | 7 | Chilled Water Pump 3 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 119 |  |  | 1718 | 261 | C3 Reduce Evaporator Airflow | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics.Service Alarm | 10 | 7023 | 7 | Chilled Water Pump 3 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 120 |  |  | 1718 | 262 | C4 Reduce Evaporator Airflow | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics.Service Alarm | 12 | 7023 | 7 | Chilled Water Pump 3 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 121 |  |  | 1718 | 263 | C1 Add Charge | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Service Alarm | 6 | 7023 | 8 | Chilled Water Pump 4 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 122 |  |  | 1718 | 264 | C2 Add Charge | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Service Alarm | 8 | 7023 | 8 | Chilled Water Pump 4 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 123 |  |  | 1718 | 265 | C3 Add Charge | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics.Service Alarm | 10 | 7023 | 8 | Chilled Water Pump 4 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 124 |  |  | 1718 | 266 | C4 Add Charge | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics.Service Alarm | 12 | 7023 | 8 | Chilled Water Pump 4 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 125 |  |  | 1718 | 267 | C1 Insufficient Refrigerant Flow | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Service Alarm | 6 | 7023 | 9 | Cooling Tower 1 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 126 |  |  | 1718 | 268 | C2 Insufficient Refrigerant Flow | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Service Alarm | 8 | 7023 | 9 | Cooling Tower 1 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 127 |  |  | 1718 | 269 | C3 Insufficient Refrigerant Flow | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics.Service Alarm | 10 | 7023 | 9 | Cooling Tower 1 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 128 |  |  | 1718 | 270 | C4 Insufficient Refrigerant Flow | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics.Service Alarm | 12 | 7023 | 9 | Cooling Tower 1 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 129 |  |  | 1718 | 271 | C1 Recover Charge | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Service Alarm | 6 | 7023 | 10 | Cooling Tower 2 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 130 |  |  | 1718 | 272 | C2 Recover Charge | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Service Alarm | 8 | 7023 | 10 | Cooling Tower 2 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 131 |  |  | 1718 | 273 | C3 Recover Charge | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics.Service Alarm | 10 | 7023 | 10 | Cooling Tower 2 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 132 |  |  | 1718 | 274 | C4 Recover Charge | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics.Service Alarm | 12 | 7023 | 10 | Cooling Tower 2 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 133 |  |  | 1718 | 299 | C1 Non-Condensables Present | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Service Alarm | 6 | 7023 | 11 | Cooling Tower 3 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 134 |  |  | 1718 | 300 | C2 Non-Condensables Present | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Service Alarm | 8 | 7023 | 11 | Cooling Tower 3 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 135 |  |  | 1718 | 301 | C3 Non-Condensables Present | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics.Service Alarm | 10 | 7023 | 11 | Cooling Tower 3 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 136 |  |  | 1718 | 302 | C4 Non-Condensables Present | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics.Service Alarm | 12 | 7023 | 11 | Cooling Tower 3 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 137 |  |  | 1718 | 199 | C1 Liquid Temp Greater Than Cond Temp | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Service Alarm | 6 | 7023 | 12 | Cooling Tower 4 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 138 |  |  | 1718 | 200 | C2 Liquid Temp Greater Than Cond Temp | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Service Alarm | 8 | 7023 | 12 | Cooling Tower 4 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 139 |  |  | 1718 | 201 | C3 Liquid Temp Greater Than Cond Temp | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics.Service Alarm | 10 | 7023 | 12 | Cooling Tower 4 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 140 |  |  | 1718 | 202 | C4 Liquid Temp Greater Than Cond Temp | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics.Service Alarm | 12 | 7023 | 12 | Cooling Tower 4 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 142 |  |  | 1718 | 158 | Hot H2o FS Open to Prevent Coil Freeze | 1721 | 158 | Hot H2o FS Open to Prevent Coil Freeze | York RTU.Heating Control.Hydronic Heat Control.Hydronic Heat On due to Freeze Stat | 18 | 7006 | 1 | Yes | 0 | None | FALSE | FALSE
Event | Service | 143 |  |  | 1718 | 159 | Hot H2o FS Opened When It Should Not | 1721 | 159 | Hot H2o FS Opened When It Should Not | York RTU.Heating Control.Hydronic Heat Control.Hot Water Freeze Stat Opened When It Should Not | 18 | 7007 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | Service | 144 |  |  | 1718 | 313 | Space Temperature Heating Alarm | 1721 | 169 | Space Temperature Cooling Alarm | York RTU.HVAC Zone.Space Temperature Heating Alarm | 25 | 7042 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | Service | 145 |  |  | 1718 | 147 | Not Economizing - No Supply Air Sensor | 1721 | 147 | Not Economizing - No Supply Air Sensor | York RTU.Economizer.Not Economizing - No Supply Air Sensor | 19 | 7026 | 1 | Alarm | 1 | Air temperature sensor failure/fault | FALSE | FALSE
Event | Service | 146 |  |  | 1718 | 168 | Using Return Instead of Space Temp | 1721 | 168 | Using Return Instead of Space Temp | York RTU.HVAC Zone.RAT Instead of Space-T | 25 | 7058 | 1 | Yes | 0 | None | FALSE | FALSE
Event | Service | 147 |  |  | 1718 | 424 | Proof Of Air Flow With No Fan Command | 1721 | 424 | Proof Of Air Flow With No Fan Command | York RTU.Fan Control.Air Proving Switch Stuck Closed | 3 | 7036 | 6 | False Proof Fault | 0 | None | FALSE | FALSE
Event | Service | 149 |  |  | 1718 | 171 | C1 Basic Data Not Available | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Service Alarm | 6 | 7023 | 13 | Condenser Water Pump 1 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 150 |  |  | 1718 | 172 | C2 Basic Data Not Available | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Service Alarm | 8 | 7023 | 13 | Condenser Water Pump 1 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 151 |  |  | 1718 | 173 | C3 Basic Data Not Available | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics.Service Alarm | 10 | 7023 | 13 | Condenser Water Pump 1 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 152 |  |  | 1718 | 174 | C4 Basic Data Not Available | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics.Service Alarm | 12 | 7023 | 13 | Condenser Water Pump 1 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 153 |  |  | 1718 | 303 | C1 Unit Off | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Service Alarm | 6 | 7023 | 14 | Condenser Water Pump 2 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 154 |  |  | 1718 | 304 | C2 Unit Off | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Service Alarm | 8 | 7023 | 14 | Condenser Water Pump 2 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 155 |  |  | 1718 | 305 | C3 Unit Off | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics.Service Alarm | 10 | 7023 | 14 | Condenser Water Pump 2 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 156 |  |  | 1718 | 306 | C4 Unit Off | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics.Service Alarm | 12 | 7023 | 14 | Condenser Water Pump 2 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 157 |  |  | 1718 | 175 | C1 Return Air Wet-Bulb Temp Out Of Range | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Service Alarm | 6 | 7023 | 15 | Condenser Water Pump 3 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 158 |  |  | 1718 | 176 | C2 Return Air Wet-Bulb Temp Out Of Range | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Service Alarm | 8 | 7023 | 15 | Condenser Water Pump 3 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 159 |  |  | 1718 | 177 | C3 Return Air Wet-Bulb Temp Out Of Range | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics.Service Alarm | 10 | 7023 | 15 | Condenser Water Pump 3 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 160 |  |  | 1718 | 178 | C4 Return Air Wet-Bulb Temp Out Of Range | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics.Service Alarm | 12 | 7023 | 15 | Condenser Water Pump 3 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 161 |  |  | 1718 | 179 | C1 Ambient Temp Too Low | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Service Alarm | 6 | 7023 | 16 | Condenser Water Pump 4 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 162 |  |  | 1718 | 180 | C2 Ambient Temp Too Low | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Service Alarm | 8 | 7023 | 16 | Condenser Water Pump 4 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 163 |  |  | 1718 | 181 | C3 Ambient Temp Too Low | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics.Service Alarm | 10 | 7023 | 16 | Condenser Water Pump 4 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 164 |  |  | 1718 | 182 | C4 Ambient Temp Too Low | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics.Service Alarm | 12 | 7023 | 16 | Condenser Water Pump 4 Interlock Alarm | 0 | None | FALSE | FALSE
Event | Service | 165 |  |  | 1718 | 183 | C1 Ambient Temp Too High | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Service Alarm | 6 | 7023 | 17 | Chiller 1 Chilled Water DP Failure | 0 | None | FALSE | FALSE
Event | Service | 166 |  |  | 1718 | 184 | C2 Ambient Temp Too High | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Service Alarm | 8 | 7023 | 17 | Chiller 1 Chilled Water DP Failure | 0 | None | FALSE | FALSE
Event | Service | 167 |  |  | 1718 | 185 | C3 Ambient Temp Too High | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics.Service Alarm | 10 | 7023 | 17 | Chiller 1 Chilled Water DP Failure | 0 | None | FALSE | FALSE
Event | Service | 168 |  |  | 1718 | 186 | C4 Ambient Temp Too High | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics.Service Alarm | 12 | 7023 | 17 | Chiller 1 Chilled Water DP Failure | 0 | None | FALSE | FALSE
Event | Service | 169 |  |  | 1718 | 187 | C1 Return Air Wet-Bulb Temp Too Low | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Service Alarm | 6 | 7023 | 18 | Chiller 2 Chilled Water DP Failure | 0 | None | FALSE | FALSE
Event | Service | 170 |  |  | 1718 | 188 | C2 Return Air Wet-Bulb Temp Too Low | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Service Alarm | 8 | 7023 | 18 | Chiller 2 Chilled Water DP Failure | 0 | None | FALSE | FALSE
Event | Service | 171 |  |  | 1718 | 189 | C3 Return Air Wet-Bulb Temp Too Low | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics.Service Alarm | 10 | 7023 | 18 | Chiller 2 Chilled Water DP Failure | 0 | None | FALSE | FALSE
Event | Service | 172 |  |  | 1718 | 190 | C4 Return Air Wet-Bulb Temp Too Low | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics.Service Alarm | 12 | 7023 | 18 | Chiller 2 Chilled Water DP Failure | 0 | None | FALSE | FALSE
Event | Service | 173 |  |  | 1718 | 191 | C1 Return Air Wet-Bulb Temp Too High | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Service Alarm | 6 | 7023 | 19 | Chiller 3 Chilled Water DP Failure | 0 | None | FALSE | FALSE
Event | Service | 174 |  |  | 1718 | 192 | C2 Return Air Wet-Bulb Temp Too High | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Service Alarm | 8 | 7023 | 19 | Chiller 3 Chilled Water DP Failure | 0 | None | FALSE | FALSE
Event | Service | 175 |  |  | 1718 | 193 | C3 Return Air Wet-Bulb Temp Too High | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics.Service Alarm | 10 | 7023 | 19 | Chiller 3 Chilled Water DP Failure | 0 | None | FALSE | FALSE
Event | Service | 176 |  |  | 1718 | 194 | C4 Return Air Wet-Bulb Temp Too High | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics.Service Alarm | 12 | 7023 | 19 | Chiller 3 Chilled Water DP Failure | 0 | None | FALSE | FALSE
Event | Service | 177 |  |  | 1718 | 195 | C1 Condensing Temp Less Than Ambient | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Service Alarm | 6 | 7023 | 20 | Chiller 4 Chilled Water DP Failure | 0 | None | FALSE | FALSE
Event | Service | 178 |  |  | 1718 | 196 | C2 Condensing Temp Less Than Ambient | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Service Alarm | 8 | 7023 | 20 | Chiller 4 Chilled Water DP Failure | 0 | None | FALSE | FALSE
Event | Service | 179 |  |  | 1718 | 197 | C3 Condensing Temp Less Than Ambient | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics.Service Alarm | 10 | 7023 | 20 | Chiller 4 Chilled Water DP Failure | 0 | None | FALSE | FALSE
Event | Service | 180 |  |  | 1718 | 198 | C4 Condensing Temp Less Than Ambient | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics.Service Alarm | 12 | 7023 | 20 | Chiller 4 Chilled Water DP Failure | 0 | None | FALSE | FALSE
Event | Service | 181 |  |  | 1718 | 203 | C1 Suction Temp Less Than Evap Temp | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Service Alarm | 6 | 7023 | 21 | Building Chilled Water DP Failure | 0 | None | FALSE | FALSE
Event | Service | 182 |  |  | 1718 | 204 | C2 Suction Temp Less Than Evap Temp | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Service Alarm | 8 | 7023 | 21 | Building Chilled Water DP Failure | 0 | None | FALSE | FALSE
Event | Service | 183 |  |  | 1718 | 205 | C3 Suction Temp Less Than Evap Temp | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics.Service Alarm | 10 | 7023 | 21 | Building Chilled Water DP Failure | 0 | None | FALSE | FALSE
Event | Service | 184 |  |  | 1718 | 206 | C4 Suction Temp Less Than Evap Temp | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics.Service Alarm | 12 | 7023 | 21 | Building Chilled Water DP Failure | 0 | None | FALSE | FALSE
Event | Service | 185 |  |  | 1718 | 207 | C1 Evap Temp Greater Than Ambient Temp | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Service Alarm | 6 | 7023 | 22 | Primary Chilled Water Flow Failure | 0 | None | FALSE | FALSE
Event | Service | 186 |  |  | 1718 | 208 | C2 Evap Temp Greater Than Ambient Temp | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Service Alarm | 8 | 7023 | 22 | Primary Chilled Water Flow Failure | 0 | None | FALSE | FALSE
Event | Service | 187 |  |  | 1718 | 209 | C3 Evap Temp Greater Than Ambient Temp | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics.Service Alarm | 10 | 7023 | 22 | Primary Chilled Water Flow Failure | 0 | None | FALSE | FALSE
Event | Service | 188 |  |  | 1718 | 210 | C4 Evap Temp Greater Than Ambient Temp | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics.Service Alarm | 12 | 7023 | 22 | Primary Chilled Water Flow Failure | 0 | None | FALSE | FALSE
Event | Service | 189 |  |  | 1718 | 211 | C1 Liquid Temp Less Than Ambient Temp | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Service Alarm | 6 | 7023 | 23 | Chiller 1 Chilled Water Supply Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 190 |  |  | 1718 | 212 | C2 Liquid Temp Less Than Ambient Temp | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Service Alarm | 8 | 7023 | 23 | Chiller 1 Chilled Water Supply Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 191 |  |  | 1718 | 213 | C3 Liquid Temp Less Than Ambient Temp | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics.Service Alarm | 10 | 7023 | 23 | Chiller 1 Chilled Water Supply Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 192 |  |  | 1718 | 214 | C4 Liquid Temp Less Than Ambient Temp | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics.Service Alarm | 12 | 7023 | 23 | Chiller 1 Chilled Water Supply Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 193 |  |  | 1718 | 215 | C1 Invalid Suction or Ambient Temp | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Service Alarm | 6 | 7023 | 24 | Chiller 2 Chilled Water Supply Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 194 |  |  | 1718 | 216 | C2 Invalid Suction or Ambient Temp | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Service Alarm | 8 | 7023 | 24 | Chiller 2 Chilled Water Supply Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 195 |  |  | 1718 | 217 | C3 Invalid Suction or Ambient Temp | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics.Service Alarm | 10 | 7023 | 24 | Chiller 2 Chilled Water Supply Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 196 |  |  | 1718 | 218 | C4 Invalid Suction or Ambient Temp | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics.Service Alarm | 12 | 7023 | 24 | Chiller 2 Chilled Water Supply Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 197 |  |  | 1718 | 219 | C1 Invalid RA Dry-Bulb or Wet-Bulb Temp | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Service Alarm | 6 | 7023 | 25 | Chiller 3 Chilled Water Supply Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 198 |  |  | 1718 | 220 | C2 Invalid RA Dry-Bulb or Wet-Bulb Temp | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Service Alarm | 8 | 7023 | 25 | Chiller 3 Chilled Water Supply Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 199 |  |  | 1718 | 221 | C3 Invalid RA Dry-Bulb or Wet-Bulb Temp | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics.Service Alarm | 10 | 7023 | 25 | Chiller 3 Chilled Water Supply Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 200 |  |  | 1718 | 222 | C4 Invalid RA Dry-Bulb or Wet-Bulb Temp | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics.Service Alarm | 12 | 7023 | 25 | Chiller 3 Chilled Water Supply Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 201 |  |  | 1718 | 223 | C1 Invalid Liquid and Suction Pressure | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Service Alarm | 6 | 7023 | 26 | Chiller 4 Chilled Water Supply Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 202 |  |  | 1718 | 224 | C2 Invalid Liquid and Suction Pressure | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Service Alarm | 8 | 7023 | 26 | Chiller 4 Chilled Water Supply Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 203 |  |  | 1718 | 225 | C3 Invalid Liquid and Suction Pressure | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics.Service Alarm | 10 | 7023 | 26 | Chiller 4 Chilled Water Supply Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 204 |  |  | 1718 | 226 | C4 Invalid Liquid and Suction Pressure | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics.Service Alarm | 12 | 7023 | 26 | Chiller 4 Chilled Water Supply Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 205 |  |  | 1718 | 227 | C1 Invalid Suction Temp | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Service Alarm | 6 | 7023 | 27 | Chiller 1 Chilled Water Return Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 206 |  |  | 1718 | 228 | C2 Invalid Suction Temp | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Service Alarm | 8 | 7023 | 27 | Chiller 1 Chilled Water Return Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 207 |  |  | 1718 | 229 | C3 Invalid Suction Temp | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics.Service Alarm | 10 | 7023 | 27 | Chiller 1 Chilled Water Return Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 208 |  |  | 1718 | 230 | C4 Invalid Suction Temp | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics.Service Alarm | 12 | 7023 | 27 | Chiller 1 Chilled Water Return Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 209 |  |  | 1718 | 231 | C1 Invalid Liquid and Suction Temp | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Service Alarm | 6 | 7023 | 28 | Chiller 2 Chilled Water Return Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 210 |  |  | 1718 | 232 | C2 Invalid Liquid and Suction Temp | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Service Alarm | 8 | 7023 | 28 | Chiller 2 Chilled Water Return Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 211 |  |  | 1718 | 233 | C3 Invalid Liquid and Suction Temp | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics.Service Alarm | 10 | 7023 | 28 | Chiller 2 Chilled Water Return Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 212 |  |  | 1718 | 234 | C4 Invalid Liquid and Suction Temp | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics.Service Alarm | 12 | 7023 | 28 | Chiller 2 Chilled Water Return Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 213 |  |  | 1718 | 279 | C1 Return Air Dry-Bulb Temp Too Low | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Service Alarm | 6 | 7023 | 29 | Chiller 3 Chilled Water Return Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 214 |  |  | 1718 | 280 | C2 Return Air Dry-Bulb Temp Too Low | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Service Alarm | 8 | 7023 | 29 | Chiller 3 Chilled Water Return Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 215 |  |  | 1718 | 281 | C3 Return Air Dry-Bulb Temp Too Low | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics.Service Alarm | 10 | 7023 | 29 | Chiller 3 Chilled Water Return Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 216 |  |  | 1718 | 282 | C4 Return Air Dry-Bulb Temp Too Low | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics.Service Alarm | 12 | 7023 | 29 | Chiller 3 Chilled Water Return Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 217 |  |  | 1718 | 283 | C1 Return Air Dry-Bulb Temp Too High | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Service Alarm | 6 | 7023 | 30 | Chiller 4 Chilled Water Return Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 218 |  |  | 1718 | 284 | C2 Return Air Dry-Bulb Temp Too High | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Service Alarm | 8 | 7023 | 30 | Chiller 4 Chilled Water Return Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 219 |  |  | 1718 | 285 | C3 Return Air Dry-Bulb Temp Too High | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics.Service Alarm | 10 | 7023 | 30 | Chiller 4 Chilled Water Return Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 220 |  |  | 1718 | 286 | C4 Return Air Dry-Bulb Temp Too High | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics.Service Alarm | 12 | 7023 | 30 | Chiller 4 Chilled Water Return Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 221 |  |  | 1718 | 314 | C1 EI Below 75% Expected Performance | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Service Alarm | 6 | 7023 | 31 | Chiller 1 Cond Water Supply Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 222 |  |  | 1718 | 315 | C2 EI Below 75% Expected Performance | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Service Alarm | 8 | 7023 | 31 | Chiller 1 Cond Water Supply Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 223 |  |  | 1718 | 316 | C3 EI Below 75% Expected Performance | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics.Service Alarm | 10 | 7023 | 31 | Chiller 1 Cond Water Supply Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 224 |  |  | 1718 | 317 | C4 EI Below 75% Expected Performance | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics.Service Alarm | 12 | 7023 | 31 | Chiller 1 Cond Water Supply Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 225 |  |  | 1718 | 318 | C1 CI Below 75% Expected Performance | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Service Alarm | 6 | 7023 | 32 | Chiller 2 Cond Water Supply Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 226 |  |  | 1718 | 319 | C2 CI Below 75% Expected Performance | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Service Alarm | 8 | 7023 | 32 | Chiller 2 Cond Water Supply Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 227 |  |  | 1718 | 320 | C3 CI Below 75% Expected Performance | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics.Service Alarm | 10 | 7023 | 32 | Chiller 2 Cond Water Supply Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 228 |  |  | 1718 | 321 | C4 CI Below 75% Expected Performance | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics.Service Alarm | 12 | 7023 | 32 | Chiller 2 Cond Water Supply Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 229 |  |  | 1718 | 322 | C1 EI+CI Below 75% Expected Performance | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Service Alarm | 6 | 7023 | 33 | Chiller 3 Cond Water Supply Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 230 |  |  | 1718 | 323 | C2 EI+CI Below 75% Expected Performance | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Service Alarm | 8 | 7023 | 33 | Chiller 3 Cond Water Supply Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 231 |  |  | 1718 | 324 | C3 EI+CI Below 75% Expected Performance | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics.Service Alarm | 10 | 7023 | 33 | Chiller 3 Cond Water Supply Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 232 |  |  | 1718 | 325 | C4 EI+CI Below 75% Expected Performance | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics.Service Alarm | 12 | 7023 | 33 | Chiller 3 Cond Water Supply Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 233 |  |  | 1718 | 287 | C1 FDD Not Functioning Sensor Unreliable | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Service Alarm | 6 | 7023 | 34 | Chiller 4 Cond Water Supply Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 234 |  |  | 1718 | 288 | C2 FDD Not Functioning Sensor Unreliable | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Service Alarm | 8 | 7023 | 34 | Chiller 4 Cond Water Supply Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 235 |  |  | 1718 | 289 | C3 FDD Not Functioning Sensor Unreliable | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics.Service Alarm | 10 | 7023 | 34 | Chiller 4 Cond Water Supply Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 236 |  |  | 1718 | 290 | C4 FDD Not Monitoring Sensor Unreliable | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics.Service Alarm | 12 | 7023 | 34 | Chiller 4 Cond Water Supply Temp Fail | 0 | None | FALSE | FALSE
Event | Service | 237 |  |  | 1718 | 291 | C1 FDD Not Monitoring Conditions | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Service Alarm | 6 | 7023 | 35 | Outside Air Temperature Failure | 0 | None | FALSE | FALSE
Event | Service | 238 |  |  | 1718 | 292 | C2 FDD Not Monitoring Conditions | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Service Alarm | 8 | 7023 | 35 | Outside Air Temperature Failure | 0 | None | FALSE | FALSE
Event | Service | 239 |  |  | 1718 | 293 | C3 FDD Not Monitoring Conditions | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics.Service Alarm | 10 | 7023 | 35 | Outside Air Temperature Failure | 0 | None | FALSE | FALSE
Event | Service | 240 |  |  | 1718 | 294 | C4 FDD Not Monitoring Conditions | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics.Service Alarm | 12 | 7023 | 35 | Outside Air Temperature Failure | 0 | None | FALSE | FALSE
Event | Service | 241 |  |  | 1718 | 295 | C1 FDD Not Monitoring Equipment Data | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Service Alarm | 6 | 7023 | 36 | Outside Air Humidity Failure | 0 | None | FALSE | FALSE
Event | Service | 242 |  |  | 1718 | 296 | C2 FDD Not Monitoring Equipment Data | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Service Alarm | 8 | 7023 | 36 | Outside Air Humidity Failure | 0 | None | FALSE | FALSE
Event | Service | 243 |  |  | 1718 | 297 | C3 FDD Not Monitoring Equipment Data | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 3.Cooling Circuit Diagnostics.Service Alarm | 10 | 7023 | 36 | Outside Air Humidity Failure | 0 | None | FALSE | FALSE
Event | Service | 244 |  |  | 1718 | 298 | C4 FDD Not Monitoring Equipment Data | 1721 | 0 | None | York RTU.Cooling Control.DX Cooling Circuit 4.Cooling Circuit Diagnostics.Service Alarm | 12 | 7023 | 36 | Outside Air Humidity Failure | 0 | None | FALSE | FALSE
Event | Service | 259 |  |  | 1718 | 115 | C1 Suction Pressure Sensor Failure | 1721 | 115 | C1 Suction Pressure Sensor Failure | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Suction Pressure Sensor Fault | 6 | 7010 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | Service | 260 |  |  | 1718 | 407 | C1 Suction Temperature Sensor Failure | 1721 | 407 | C1 Suction Temperature Sensor Failure | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Suction Temperature Sensor Fault | 6 | 7011 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | Service | 261 |  |  | 1718 | 409 | C1 Discharge Pressure Sensor Failure | 1721 | 409 | C1 Discharge Pressure Sensor Failure | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Discharge Pressure Sensor Fault | 6 | 7012 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | Service | 262 |  |  | 1718 | 411 | C1 Discharge Temperature Sensor Failure | 1721 | 411 | C1 Discharge Temperature Sensor Failure | York RTU.Cooling Control.DX Cooling Circuit 1.Cooling Circuit Diagnostics.Discharge Temperature Sensor Fault | 6 | 7013 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | Service | 263 |  |  | 1718 | 119 | C2 Suction Pressure Sensor Failure | 1721 | 119 | C2 Suction Pressure Sensor Failure | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Suction Pressure Sensor Fault | 8 | 7010 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | Service | 264 |  |  | 1718 | 408 | C2 Suction Temperature Sensor Failure | 1721 | 408 | C2 Suction Temperature Sensor Failure | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Suction Temperature Sensor Fault | 8 | 7011 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | Service | 265 |  |  | 1718 | 410 | C2 Discharge Pressure Sensor Failure | 1721 | 410 | C2 Discharge Pressure Sensor Failure | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Discharge Pressure Sensor Fault | 8 | 7012 | 1 | Alarm | 0 | None | FALSE | FALSE
Event | Service | 266 |  |  | 1718 | 412 | C2 Discharge Temperature Sensor Failure | 1721 | 412 | C2 Discharge Temperature Sensor Failure | York RTU.Cooling Control.DX Cooling Circuit 2.Cooling Circuit Diagnostics.Discharge Temperature Sensor Fault | 8 | 7013 | 1 | Alarm | 0 | None | FALSE | FALSE

## Dictionary
SetId | EnumId | Text
90 | 0 | False
90 | 1 | True
90 | 2 | Hold
121 | 0 | 9600
121 | 1 | 19200
121 | 2 | 38400
121 | 3 | 57600
121 | 4 | 115200
124 | 0 | 1
124 | 1 | 1.5
124 | 2 | 2
137 | 1 | Monday
137 | 2 | Tuesday
137 | 3 | Wednesday
137 | 4 | Thursday
137 | 5 | Friday
137 | 6 | Saturday
137 | 7 | Sunday
137 | 255 | Any day of week
300 | 0 | Auto
300 | 1 | 1200
300 | 2 | 9600
300 | 3 | 19200
300 | 4 | 38400
300 | 5 | 76800
302 | 0 | Not Configured
302 | 1 | Active
302 | 2 | Waiting For Poll For Manager
302 | 3 | Not Received Token For Long
302 | 4 | Duplicate MAC Address
302 | 5 | Forcing BAUD
302 | 6 | Remote Trunk
343 | 0 | Occupied
343 | 1 | UnOccupied
343 | 2 | Standby
343 | 3 | Not Set
344 | 0 | Occupied
344 | 1 | UnOccupied
344 | 2 | Not Set
345 | 0 | Occupied
345 | 1 | UnOccupied
345 | 2 | Bypass
345 | 3 | Standby
349 | 0 | Shutdown
349 | 1 | Enable
350 | 0 | Heating
350 | 1 | Cooling
366 | 0 | Normal
366 | 1 | Warmup
366 | 2 | Cooldown
366 | 3 | Coast
374 | 0 | Normal
374 | 1 | Alarm
430 | 0 | None
430 | 1 | Odd
430 | 2 | Even
430 | 3 | Mark
430 | 4 | Space
503 | 0 | Reliable
503 | 1 | No Input
503 | 2 | Out of range high
503 | 3 | Out of range low
503 | 4 | Open
503 | 5 | Shorted
503 | 6 | No Output
503 | 7 | Unreliable
503 | 8 | Process Error
503 | 9 | Multi-State Fault
503 | 10 | Configuration Error
503 | 12 | Communications failure
503 | 13 | Member fault
503 | 14 | Monitored Object fault
503 | 15 | Tripped
503 | 16 | Lamp Failure
503 | 17 | Activation Failure
503 | 18 | Renew DHCP Failure
503 | 19 | Renew F. D. Registration Failure
503 | 20 | Restart Auto-negotiation Failure
503 | 21 | Restart Failure
503 | 22 | Proprietary Command Failure
503 | 23 | Faults Listed Failure
503 | 24 | Referenced Object Fault
503 | 64 | Unreliable rate
503 | 65 | Math error
503 | 66 | Math overflow
503 | 67 | Math underflow
503 | 68 | String overflow
503 | 69 | Divide by zero
503 | 70 | Comm loss
503 | 71 | Memory overflow
503 | 72 | Device error
503 | 73 | Not a number
503 | 74 | Input out of range
503 | 75 | Inconsistent inputs
503 | 76 | Data Convert Error
503 | 77 | Convert Overflow
503 | 78 | Read Error
503 | 79 | Write Error
503 | 80 | Execute Error
503 | 81 | Pcode Error
503 | 82 | Stall During Post
503 | 83 | Did Not Stall
503 | 84 | Cal Stroke too Big
503 | 85 | Cal Stroke too Small
503 | 86 | Not Calibrated
503 | 87 | Connections Failed
503 | 88 | Initialization Error
503 | 89 | Attr Init Error
503 | 90 | No Object Name
503 | 91 | Invalid Lin Table
503 | 92 | Null Data Returned
503 | 93 | Input Unreliable
503 | 94 | Disabled
503 | 95 | Inputs cannot be equal
503 | 96 | Setpoint Unreliable
503 | 97 | Command Unreliable
503 | 98 | Required Input Unavailable
503 | 99 | Failed to Synchronize
503 | 100 | Invalid Input
503 | 101 | Output cannot be determined
503 | 102 | Internal Error
503 | 103 | Destinations Unavailable
503 | 104 | Write Failed
503 | 105 | Data Type Mismatch
503 | 106 | Source Unavailable
503 | 107 | Round Off Error
503 | 108 | Clamped Low
503 | 109 | Clamped High
503 | 110 | Value Timed Out
503 | 111 | Data Model Template Not Found
503 | 112 | Not Present
503 | 113 | Output out of range
503 | 114 | Value Not Set
503 | 115 | Invalid Value For Application
505 | 0 | Normal
505 | 1 | Inactive
505 | 2 | Monitor Only Mode Active
505 | 5 | Battery Alarm
505 | 7 | Below Setpoint
505 | 8 | Above Setpoint
505 | 10 | Low Warning
505 | 15 | High Warning
505 | 17 | Unoccupied
505 | 20 | Trouble
505 | 25 | SAB Device Warning
505 | 30 | Low Alarm
505 | 34 | High Alarm
505 | 38 | Alarm
505 | 50 | Using Startup Value
505 | 51 | Using Default Value
505 | 55 | Output Clipped
505 | 60 | HW Value Overwritten
505 | 65 | OS Suspended
505 | 70 | Unreliable
505 | 73 | SAB Device Alarm
505 | 75 | Disconnected
505 | 80 | Overridden
505 | 86 | Operator Override
505 | 87 | In Test
505 | 88 | Heavy Equip Delay
505 | 90 | Min On Min Off
505 | 91 | Critical Resource Missing
505 | 92 | DNS Server Not Defined
505 | 93 | WebSocket Server Task Not Running
505 | 94 | Invalid Security Credentials
505 | 95 | Changes Pending
505 | 99 | High Priority
505 | 100 | Insufficient Capacity
505 | 102 | Disabled
505 | 108 | Out of Service
505 | 110 | HW Override
505 | 112 | Offline
505 | 115 | Shutdown
505 | 120 | Max
505 | 555 | Device pairing failed
505 | 556 | Device Unauthenticated
507 | 5 | V
507 | 24 | Btu/lb dry air
507 | 29 | %RH
507 | 31 | m
507 | 33 | ft
507 | 48 | kW
507 | 52 | tons refr
507 | 53 | Pa
507 | 54 | kPa
507 | 56 | psi
507 | 58 | in wc
507 | 62 | deg C
507 | 64 | deg F
507 | 71 | hours
507 | 72 | minutes
507 | 73 | seconds
507 | 84 | cfm
507 | 87 | L/s
507 | 92 | deg C/min
507 | 94 | deg F/min
507 | 95
507 | 96 | ppm
507 | 98 | %
507 | 117 | Btu/lb
507 | 120 | delta deg F
507 | 125 | kJ/kg
507 | 264 | % open
507 | 272 | Custom
507 | 359 | delta deg C
575 | 0 | ISO 10646 (UCS-2)
575 | 1 | ANSI X3.4 (US-ASCII)
575 | 2 | Microsoft DBCS code page 932 (Japanese Shift JIS)
575 | 3 | ISO 10646 (UTF-8)
647 | 0 | Off
647 | 1 | On
658 | 0 | Disable
658 | 1 | Enable
854 | 0 | No
854 | 1 | Yes
869 | 0 | IP
869 | 1 | SI
939 | 0 | Close
939 | 1 | Open
1222 | 0 | Wired Field Bus
1222 | 1 | Wireless Field Bus
1222 | 2 | N2 Subordinate Field Bus
1222 | 3 | Modbus Field Bus
1222 | 4 | Ethernet Field Bus
1222 | 255 | Indeterminate FC Bus Mode
1223 | 0 | None
1223 | 1 | Weak
1223 | 2 | Average
1223 | 3 | Strong
1236 | 0 | Offline
1236 | 1 | Not Associated
1236 | 2 | Online
1236 | 3 | Radio Processor Fault
1241 | 0 | Heat
1241 | 1 | Cool
1241 | 2 | Fan Only
1241 | 3 | Auto
1241 | 4 | Off
1243 | 0 | Heat
1243 | 1 | Cool
1243 | 2 | Fan Only
1243 | 3 | Balancing
1243 | 4 | Satisfied
1243 | 5 | Off
1244 | 0 | Changeover Bypass
1244 | 1 | VAV
1244 | 2 | Constant Volume
1244 | 3 | TEC
1368 | 0 | Unknown
1368 | 1 | RTU
1368 | 2 | Split
1368 | 3 | HeatPump
1392 | 0 | 0.0001
1392 | 1 | 0.001
1392 | 2 | 0.01
1392 | 3 | 0.1
1392 | 4 | 1
1392 | 5 | 10
1392 | 6 | 100
1392 | 7 | 1000
1604 | 0 | Normal
1604 | 1 | Lockout
1608 | 0 | Staged
1608 | 1 | Proportional
1619 | 0 | Single Speed
1619 | 1 | Not Used
1619 | 2 | Fixed Variable
1619 | 3 | Variable Speed
1621 | 0 | Normal Off
1621 | 1 | Startup
1621 | 2 | Normal On
1621 | 3 | Proof Lost OK
1621 | 4 | Proof Lost Fault
1621 | 5 | False Proof Off
1621 | 6 | False Proof Fault
1622 | 0 | Constant Volume
1622 | 1 | Variable Volume
1622 | 2 | None
1639 | 0 | None
1639 | 1 | Non-Modulating
1639 | 2 | Modulating Damper
1639 | 3 | Variable Frequency Fan
1644 | 0 | Normal
1644 | 1 | Drop Stage
1644 | 2 | Wait
1644 | 3 | SAT Unreliable
1645 | 0 | Defrost Off
1645 | 1 | Normal Defrost
1645 | 2 | Test Defrost
1645 | 3 | Comp Delay Exit Defrost
1645 | 4 | Comp Delay Enter Defrost
1645 | 5 | Rev Valve Off Delay
1645 | 6 | Rev Valve On Delay
1658 | 0 | Occupied
1658 | 1 | Unoccupied
1662 | 0 | Not Present
1662 | 1 | Offline
1662 | 2 | Online
1665 | 0 | Curve 1
1665 | 1 | Curve 2
1665 | 2 | Curve 3
1665 | 3 | Curve 4
1665 | 4 | Curve 5
1665 | 5 | Curve 6
1667 | 2 | Occupancy Schedule
1668 | 0 | Local Input
1668 | 1 | Local Network Sensor
1668 | 2 | BAS Network Request
1668 | 3 | Local Schedule
1668 | 4 | Temporary Occupancy
1671 | 0 | Equipment
1672 | 0 | York RTU
1672 | 1 | HVAC Zone
1675 | 0 | Unit Status
1675 | 1 | Unit Name
1675 | 2 | Description
1675 | 3 | Unit Model Number
1675 | 4 | Unit Serial Number
1675 | 5 | Firmware Version
1675 | 9 | Occupancy Input Source
1675 | 10 | Operational Occupancy
1675 | 12 | Network Temporary Occupancy Request
1675 | 13 | Network Occupancy Request
1675 | 14 | Temporary Occupancy Timeout
1675 | 15 | Operational Space Temperature
1675 | 16 | Space Temperature Source
1675 | 18 | Network Override Space Temperature
1675 | 19 | Indoor Air Quality
1675 | 20 | Indoor Air Quality Source
1675 | 22 | Network Override Indoor Air Quality
1675 | 23 | Operational Space Humidity
1675 | 24 | Space Humidity Source
1675 | 25 | Space Humidity RAH Input
1675 | 26 | Network Override Zone Humidity
1675 | 27 | Operating Fan Request
1675 | 28 | Fan Request Source
1675 | 29 | Network Override Fan Request
1675 | 30 | Operational Space Temperature Setpoint Offset
1675 | 31 | Space Temperature Setpoint Offset Source
1675 | 32 | Space Temp Setpoint Offset Input
1675 | 33 | Network Override Space Setpoint Offset
1675 | 34 | Space Temperature Setpoint Offset Range
1675 | 35 | Number of Network Sensors Online
1675 | 36 | Operational Outdoor Air Temperature
1675 | 37 | Outdoor Air Temperature Source
1675 | 38 | Outdoor Air Temperature Input
1675 | 39 | Network Override Outdoor Air Temperature
1675 | 40 | Operational Outdoor Air Humidity
1675 | 41 | Outdoor Air Enthalpy
1675 | 42 | Outdoor Air Humidity Source
1675 | 43 | Outdoor Air Humidity Input
1675 | 44 | Network Override Outdoor Air Humidity
1675 | 45 | Operational Outdoor Air Quality
1675 | 46 | Outdoor Air Quality Source
1675 | 47 | Outdoor Air Quality Input
1675 | 48 | Outdoor Air Quality Sensor Range
1675 | 49 | Network Override Outdoor Air Quality
1675 | 50 | Economizer Enabled For Operation
1675 | 51 | Economizer Damper % Command
1675 | 52 | Econ Free Cooling Available
1675 | 53 | Economizer Status
1675 | 54 | Free Cooling Current Mode
1675 | 55 | Free Cooling Selection
1675 | 56 | Economizer Outdoor Air Temp Enable Setpoint
1675 | 57 | Economizer Outdoor Air Enthalpy Setpoint
1675 | 58 | Low Ambient Economizer Setpoint
1675 | 59 | Low Ambient Economizer Minimum Position
1675 | 62 | Mixed Air Temperature
1675 | 63 | Return Air Humidity
1675 | 64 | Return Air Enthalpy
1675 | 65 | Return Air Temperature
1675 | 66 | Cooling Mode Enabled For Operation
1675 | 67 | Number of Cooling Stages Installed
1675 | 68 | Cooling Stages Available
1675 | 69 | Cooling Status
1675 | 71 | Minimum Runtime for a Cooling Stage
1675 | 72 | Lead/Lag Equalize Cooling Stage Runtime Enabled
1675 | 73 | Low Ambient Fan Pre-run Time For Cooling
1675 | 74 | OAT Cooling Cutout
1675 | 75 | SAT Limit for Cooling Setpoint
1675 | 76 | Economizer Loading Enabled
1675 | 77 | All Compressors Off in Free Cooling
1675 | 78 | Low Ambient Cooling Stages 10 on 5 off Setpoint
1675 | 79 | Temperature/Humidity (Return) Control Enable
1675 | 80 | Temperature/Humidity Setpoint
1675 | 81 | Maximum Temperature / Humidity Setpoint Offset
1675 | 82 | Temperature / Humidity Value per Degree Offset
1675 | 83 | Compressor Stage Number
1675 | 84 | Compressor Stage Command
1675 | 85 | Compressor Stage Status
1675 | 86 | Compressor Stage Enabled
1675 | 89 | Hot Gas Bypass Present
1675 | 90 | Compressor Stage Accumulated Runtime
1675 | 91 | Compressor Stage Number Times On
1675 | 92 | Min On Time Remaining
1675 | 93 | High Pressure Limit
1675 | 94 | High Pressure Lockout
1675 | 95 | Low Pressure Limit
1675 | 96 | Low Pressure Lockout
1675 | 97 | Freeze Condition
1675 | 98 | Freeze Condition Lockout
1675 | 99 | Freeze Condition Setpoint
1675 | 100 | Evaporator Coil Temp
1675 | 101 | Evaporator Coil Type
1675 | 102 | Condenser Coil Temp
1675 | 103 | Condenser Coil Type
1675 | 105 | Heating Mode Enabled For Operation
1675 | 106 | Heating Status
1675 | 107 | Heating Control Type
1675 | 108 | SAT Air Temp Limit for Heating Enabled
1675 | 109 | SAT Air Temp Limit For Heating Setpoint
1675 | 110 | Outdoor Air Temp Heating Cutout Setpoint
1675 | 111 | Heat Stage Command
1675 | 112 | Heat Stage Status
1675 | 116 | Heat Stage Accumulated Runtime
1675 | 117 | Heat Stage Number of Times On
1675 | 118 | Gas Valve1 Input
1675 | 119 | Gas Valve2 Input
1675 | 120 | Gas Valve3 Input
1675 | 121 | Heat Limit1 Switch
1675 | 122 | Heat Limit1 Switch Lockout
1675 | 123 | Heat Limit2 Switch
1675 | 124 | Heat Limit2 Switch Lockout
1675 | 125 | Heat Limit3 Switch
1675 | 126 | Heat Limit3 Switch Lockout
1675 | 127 | OAT Cooling Cutout Enabled
1675 | 128 | Condenser Fan 1
1675 | 129 | Condenser Fan 2
1675 | 130 | Unit Type
1675 | 131 | EER
1675 | 132 | Subcooling Goal
1675 | 133 | Refrigerant Type
1675 | 134 | High Side Port Location
1675 | 135 | Indoor Metering Device Type
1675 | 136 | Outdoor Metering Device Type
1675 | 137 | VAV Cooling Supply Air Temp Upper Setpoint
1675 | 138 | VAV Cooling Supply Air Temp Lower Setpoint
1675 | 139 | VAV Supply Air Temp Reset Setpoint
1675 | 140 | VAV Operating Cooling Supply Air Temp Setpoint
1675 | 141 | CV Occupied Cooling Setpoint
1675 | 142 | CV Unoccupied Cooling Setpoint
1675 | 143 | SAT Limit for Cooling Enable
1675 | 144 | CV Operating Cooling Setpoint
1675 | 145 | Anti-Short Cycle Delay Time Remaining
1675 | 146 | Firmware Status
1675 | 147 | Exhaust Type
1675 | 148 | UCB 24VAC Input
1675 | 150 | Y1 - Thermostat
1675 | 151 | Y2 - Thermostat
1675 | 152 | Y3 - Thermostat
1675 | 153 | Y4 - Thermostat
1675 | 154 | W1 - Thermostat
1675 | 155 | W2 - Thermostat
1675 | 156 | W3 - Thermostat
1675 | 157 | G - Thermostat
1675 | 158 | Local Occupancy Input - Thermostat
1675 | 159 | X-OUT
1675 | 160 | Thermostat Only Control Enabled
1675 | 161 | Occupancy Mode
1675 | 162 | Space Temperature Alarm Setpoint Offset
1675 | 163 | Space Temperature Alarm Time Delay
1675 | 164 | Space Temperature Input
1675 | 165 | Operational Indoor Air Quality
1675 | 166 | Indoor Air Quality Sensor Range
1675 | 168 | Fan Status
1675 | 169 | Fan % Command
1675 | 170 | Fan VFD Fault
1675 | 171 | Fan Overload
1675 | 172 | Fan Accumulated Runtime
1675 | 173 | Fan Control Type
1675 | 174 | Air Proving Switch Setup
1675 | 175 | Air Proving Switch
1675 | 176 | Fan On Delay for Cool
1675 | 177 | Fan Off Delay for Cool
1675 | 178 | Fan On Delay for Heat
1675 | 179 | Fan Off Delay for Heat
1675 | 180 | Dirty Filter Switch
1675 | 181 | Fan Command
1675 | 182 | Supply Air Temperature
1675 | 183 | Duct Static Pressure
1675 | 184 | Duct Pressure Setpoint
1675 | 185 | Duct Pressure Shutdown Setpoint
1675 | 186 | Continuous Fan Operation in Occupied Mode
1675 | 187 | Turn Off Continuous Fan Operation When Starting Heat
1675 | 188 | Occupied: No Heat or Cool % Command
1675 | 189 | Occupied: One Stage of Cool % Command
1675 | 190 | Occupied: Two Stage of Cool % Command
1675 | 191 | Occupied: One Stage of Heat % Command
1675 | 192 | Occupied: Two Stage of Heat % Command
1675 | 193 | Cooling Circuit Test Status
1675 | 194 | Suction Pressure
1675 | 195 | Liquid Pressure
1675 | 196 | Suction Temperature
1675 | 197 | Liquid Temperature
1675 | 198 | Superheat
1675 | 199 | Subcooling
1675 | 200 | Condensing Temperature over Ambient
1675 | 201 | Efficiency Index
1675 | 202 | Capacity Index
1675 | 203 | Hot Water Freeze Stat
1675 | 204 | VAV Occupied Heating Enabled
1675 | 205 | VAV Occupied Heating Setpoint
1675 | 206 | Unoccupied Heating Enabled
1675 | 207 | VAV Unoccupied Heating Setpoint
1675 | 208 | VAV Operating Heating Setpoint
1675 | 209 | Morning Warmup Enabled
1675 | 210 | Morning Warmup/Return Air Temp Setpoint
1675 | 211 | VAV Box Heat Command
1675 | 212 | CV Occupied Heating Setpoint
1675 | 213 | CV Unoccupied Heating Setpoint
1675 | 214 | CV Operating Heating Setpoint
1675 | 215 | Number of Heating Stages Installed
1675 | 216 | Heating Stage Min On Time Remaining
1675 | 217 | Heating Stage Anti-Short Cycle Delay Time Remaining
1675 | 218 | Hydronic Heat Valve % Command
1675 | 219 | Hydronic Heat Valve Reverse Acting
1675 | 220 | Hydronic Heating Stage #1 Supply Air Setpoint
1675 | 221 | Hydronic Heating Stage #2 Supply Air Setpoint
1675 | 222 | Hydronic Heat SAT Tempering Enabled
1675 | 223 | Hydronic Heat SAT Tempering Setpoint
1675 | 224 | Supply Air Humidity
1675 | 225 | Demand Ventilation Mode of Operation
1675 | 226 | Demand Ventilation Maximum Economizer Position
1675 | 227 | Demand Ventilation Indoor Air Quality Setpoint
1675 | 228 | Demand Ventilation Differential Setpoint
1675 | 235 | Exhaust Fan Command
1675 | 236 | Exhaust Fan VFD % Command
1675 | 237 | Exhaust Fan Status
1675 | 238 | Exhaust Fan VFD Fault
1675 | 239 | Exhaust Fan Accumulated Runtime
1675 | 240 | Building Pressure Setpoint
1675 | 241 | Building Static Pressure
1675 | 242 | Exhaust Damper % Command
1675 | 243 | Exhaust Damper Position for Exhaust Fan to Turn On
1675 | 244 | Exhaust Damper Position for Exhaust Fan to Turn Off
1675 | 245 | Economizer Damper Position for Exhaust Fan to Turn On
1675 | 246 | Economizer Damper Position for Exhaust Fan to Turn Off
1675 | 247 | ERV Enabled
1675 | 248 | ERV Unoccupied Fan Enabled
1675 | 249 | Hot Gas Reheat Enabled For Operation
1675 | 250 | Hot Gas Reheat Command
1675 | 251 | Hot Gas Reheat Status
1675 | 252 | Hot Gas Reheat Humidity Setpoint
1675 | 253 | Hot Gas Reheat Alternate Operation Enabled
1675 | 254 | Hot Gas Reheat Alternate Operation Writeable
1675 | 255 | Fresh Air Intake Setpoint
1675 | 256 | Fresh Air Intake Value
1675 | 257 | Fresh Air Intake Max Sensor Range
1675 | 258 | Operating Purge Command
1675 | 259 | Purge Command Source
1675 | 260 | Local Purge Command Input
1675 | 261 | Network Override Purge Command
1675 | 262 | Shutdown Input/Smoke Detector
1675 | 267 | Language
1675 | 268 | Units
1675 | 269 | Relearn System
1675 | 270 | BAS Communication
1675 | 271 | Time
1675 | 272 | Date
1675 | 278 | Time Zone
1675 | 281 | Communication Status
1675 | 282 | Address
1675 | 283 | Device OID
1675 | 284 | Operating Baud Rate
1675 | 285 | Baud Rate
1675 | 287 | Firmware Main Version
1675 | 288 | Application Version
1675 | 289 | Board Communication Status
1675 | 290 | Hardware Version
1675 | 291 | Occupancy Input
1675 | 292 | Economizer Minimum Position Setpoint
1675 | 293 | Excess Outdoor Air
1675 | 294 | Not Economizing When Should
1675 | 295 | Damper Not Modulating
1675 | 296 | Economizing When Should Not
1675 | 299 | Space Temperature Sensor Fault
1675 | 300 | Space Temperature Setpoint Offset Fault
1675 | 301 | Indoor Air Quality Sensor Fault
1675 | 302 | Space Humidity Sensor Fault
1675 | 303 | Outdoor Air Temperature Sensor Fault
1675 | 304 | Outdoor Air Humidity Sensor Fault
1675 | 305 | Outdoor Air Quality Sensor Fault
1675 | 306 | Supply Air Temperature Sensor Fault
1675 | 307 | Duct Static Pressure Sensor Fault
1675 | 308 | Evaporator Coil Temp Sensor Fault
1675 | 309 | Condenser Coil Temp Sensor Fault
1675 | 310 | Mixed Air Temperature Sensor Fault
1675 | 311 | Supply Air Humidity Sensor Fault
1675 | 312 | Return Air Temperature Sensor Fault
1675 | 313 | Building Static Pressure Sensor Fault
1675 | 314 | Fresh Air Intake Sensor Fault
1675 | 315 | Econ Controller
1675 | 316 | 4 Stage Controller
1675 | 317 | FDD Manager Controller
1675 | 318 | FDD Subordinate Controller
1675 | 320 | Occupied: Three Stage of Cool % Command
1675 | 321 | Occupied: Four Stage of Cool % Command
1675 | 322 | Occupied: Three Stage of Heat % Command
1675 | 323 | Netsensor Battery Fault
1675 | 324 | Netsensor Signal Strength Fault
1675 | 325 | Scheduled Occupancy
1675 | 326 | Device Name
1675 | 327 | Economizer Damper Minimum Position Low Speed Fan
1675 | 328 | Calibration Data Fault
1675 | 329 | Temporary Occupancy Input
1675 | 330 | Space Temperature Cooling Alarm
1675 | 331 | Suction Pressure Sensor Fault
1675 | 332 | Suction Temperature Sensor Fault
1675 | 335 | Economizer Damper Position
1675 | 336 | Cancel ASCD Timers
1675 | 337 | Reset Lockouts
1675 | 338 | Outputs Disabled Due to Low Input Voltage
1675 | 339 | Outputs Limited Due to Low Input Voltage
1675 | 340 | Unit Locked Out Due to Air Proving Switch
1675 | 341 | Unit Shutdown Due to Air Proving Switch
1675 | 343 | Unit Shutdown Due High Duct Static Pressure
1675 | 344 | Unit Locked Out Supply Fan Overload
1675 | 345 | Excessive Supply Air Cooling Fault
1675 | 346 | Cooling Lockout due to Low Outdoor Air Temp
1675 | 347 | Main Valve No Proof Fault
1675 | 348 | Gas Valve 2 No Proof Fault
1675 | 349 | Gas Valve 3 No Proof Fault
1675 | 350 | Main Valve On When Shouldn't Fault
1675 | 351 | Gas Valve 2 On When Shouldn't Fault
1675 | 352 | Gas Valve 3 On When Shouldn't Fault
1675 | 353 | Heating Lockout due to High Outdoor Air Temp
1675 | 354 | Hydronic Heat On due to Freeze Stat
1675 | 355 | Excessive Supply Air Heating Fault
1675 | 359 | Space Temperature Heating Alarm
1675 | 361 | Hot Water Freeze Stat Opened When It Should Not
1675 | 362 | Not Economizing - No Supply Air Sensor
1675 | 364 | Dirty Filter Switch Installed
1675 | 365 | Air Proving Switch Stuck Closed
1675 | 371 | Unit Capacity
1675 | 372 | Fan Power
1675 | 373 | Super Heat Goal
1675 | 374 | Altitude
1675 | 375 | Morning Cooldown Enabled
1675 | 376 | Morning Cooldown/Return Air Temp Setpoint
1675 | 377 | Optimal Start Enabled
1675 | 378 | Occupancy BI Enabled
1675 | 379 | Early Start Period
1675 | 380 | Number of Heat Pump Stages Installed
1675 | 382 | Test Defrost Enable
1675 | 383 | Compressor Delay Enable
1675 | 384 | Defrost Curve Selection
1675 | 385 | Defrost State
1675 | 386 | Defrost Terminate Curve 6
1675 | 387 | Initiate Curve 6
1675 | 388 | Initiate Curve Intercept 6
1675 | 389 | Defrost Inhibit Time 6
1675 | 390 | Max Defrost Cycle Time 6
1675 | 421 | Load Shed Active
1675 | 422 | Load Shed Rate Limit
1675 | 423 | Load Shed Adjust
1675 | 424 | Evaporating Temp Value
1675 | 425 | Time to Next Occupancy Period
1675 | 426 | Operating Mode
1675 | 439 | Number of Gas Valves Installed
1675 | 440 | Condenser Temperature Over Ambient High
1675 | 441 | Condenser Temperature Over Ambient Low
1675 | 442 | Superheat High
1675 | 443 | Superheat Low
1675 | 444 | Subcool High
1675 | 445 | Subcool Low
1675 | 446 | Evaporating Temperature High
1675 | 447 | Evaporating Temperature Low
1675 | 448 | Model Name
1675 | 456 | RAT Instead of Space-T
1675 | 457 | Warmer/Cooler Adjust Enable
1675 | 458 | Heat Cool Mode
1675 | 459 | Operating State
1675 | 460 | Effective Y4 Call
1675 | 461 | Effective W3 Call
1675 | 462 | Unit Enable
1675 | 463 | Emergency Heat Only
1675 | 464 | Active Mode
1675 | 465 | Control Mode
1675 | 466 | Rooftop Controller Type
1675 | 467 | Rooftop Equipment Type
1675 | 468 | Standby Cooling Setpoint
1675 | 469 | Standby Heating Setpoint
1675 | 470 | CCS Temp Occ Status
1675 | 471 | Fan Speed High
1675 | 472 | Fan Speed Low
1675 | 473 | Power Fail Restart Enable
1675 | 474 | VFD Econ Min Pos Reset
1675 | 475 | Plug and Play Occupancy Request
1675 | 476 | CCS Fan Request
1675 | 477 | CCS Online
1675 | 478 | Cooling Manual Tuning
1675 | 479 | Heating Manual Tuning
1675 | 482 | Reversing Valve
1675 | 483 | Auxiliary Heat
1675 | 484 | Mode
1675 | 485 | Heating Adaptive Tuning Enable
1675 | 486 | Cooling Adaptive Tuning Enable
1675 | 490 | Number of Limit Switches
1675 | 491 | SZ VAV Enabled
1675 | 492 | DAT Max Heating SP
1675 | 493 | DAT Satisfied SP
1675 | 494 | DAT Cooling Min SP
1675 | 495 | Number of Refrig Systems Installed
1675 | 496 | FC Comm Mode
1675 | 497 | Direct Loadshed
1675 | 498 | EconMech Setup
1675 | 499 | Hardware Reset
1675 | 500 | Redline
1675 | 501 | Off During Unoccupied
1675 | 514 | Max Heating Setpoint
1675 | 515 | Min Cooling Setpoint
1675 | 562 | Occupied Cooling Setpoint
1675 | 588 | Service Alarm
1675 | 601 | COBP Supply Air Temperature Setpoint
1675 | 602 | HGR Unoccupied Humidity Setpoint
1675 | 603 | HGR Enabled for Unoccupied Operation
1675 | 619 | Pump Out Enable
1675 | 626 | Economizer Fault Detection Enable
1675 | 627 | SZ VAV Minimum Fan Speed
1675 | 628 | Staged Cooling Command
1675 | 629 | Staged Heating Command
1675 | 630 | Proportional Heating Command
1675 | 631 | PID Tuning Reset
1675 | 632 | Adaptive Tuning Enable
1675 | 633 | FDD Economizer Alarm Delay
1675 | 634 | FDD Economizer Damper Allowed Error
1675 | 635 | FDD Damper Min Position Tolerance
1675 | 641 | Brightness Setting
1675 | 643 | SZ VAV Occupied Heating Setpoint
1675 | 644 | SZ VAV Occupied Cooling Setpoint
1675 | 645 | SZ VAV Unoccupied Heating Setpoint
1675 | 646 | SZ VAV Unoccupied Cooling Setpoint
1675 | 647 | SZ VAV Operating Heating Setpoint
1675 | 648 | SZ VAV Operating Cooling Setpoint
1675 | 649 | Low Ambient Enabled
1675 | 688 | Temperature Sensor 1
1675 | 689 | Temperature Sensor 2
1675 | 690 | Temperature Sensor 3
1675 | 691 | Temperature Sensor 4
1675 | 692 | Temperature Sensor 5
1675 | 693 | Temperature Sensor 6
1675 | 694 | Temperature Sensor 7
1675 | 695 | Temperature Sensor 8
1675 | 696 | Temperature Sensor 9
1675 | 697 | Temperature Sensor 10
1675 | 698 | Temperature Sensor 11
1675 | 699 | Temperature Sensor 12
1675 | 700 | Temperature Sensor 13
1675 | 701 | Temperature Sensor 14
1675 | 702 | Temperature Sensor 15
1675 | 703 | Temperature Sensor 16
1675 | 704 | Temperature Sensor 17
1675 | 705 | Temperature Sensor 18
1675 | 706 | Temperature Sensor 19
1675 | 707 | Temperature Sensor 20
1675 | 708 | Temperature Sensor 21
1675 | 709 | Temperature Sensor 22
1675 | 710 | Temperature Sensor 23
1675 | 711 | Temperature Sensor 24
1675 | 712 | Temperature Sensor 25
1675 | 713 | Temperature Sensor 26
1675 | 740 | VAV Unoccupied Cooling Setpoint
1675 | 741 | Fresh Air Intake Enable
1675 | 742 | Software Version
1675 | 744 | SZ VAV Cooling Load
1675 | 745 | SZ VAV Heating Load
1675 | 757 | Occupancy Status
1675 | 791 | Aux Mode
1675 | 824 | Event 1 Set
1675 | 825 | Event 1 Value
1675 | 826 | Event 2 Set
1675 | 827 | Event 2 Value
1675 | 828 | Event 3 Set
1675 | 829 | Event 3 Value
1675 | 830 | Event 4 Set
1675 | 831 | Event 4 Value
1675 | 832 | Event 5 Set
1675 | 833 | Event 5 Value
1675 | 847 | BACnet Encoding Type
1675 | 855 | Operational Mode
1675 | 872 | HGR Humidity Setpoint Differential
1675 | 973 | Compressor 1 Lockout
1675 | 1016 | ERV
1675 | 1024 | Economizer
1675 | 1038 | Fresh Air Range
1675 | 1076 | Operational Error Sigma
1675 | 1175 | Operating Heating Setpoint
1675 | 1176 | Operating Cooling Setpoint
1675 | 1244 | Commissioning Mode
1675 | 1282 | Compressor Stage 1 Lockout
1675 | 1319 | HVAC Space
1675 | 1369 | Alarm Reporting
1675 | 1405 | Low Limit Enable
1675 | 1406 | Low Limit Upper SAT Setpoint
1675 | 1407 | Low Limit Lower SAT Setpoint
1675 | 1448 | Min Heating Setpoint
1675 | 1454 | 4 Pipe Split Enable
1675 | 1455 | Pre Occupancy Purge Enable
1675 | 1456 | COBP Occupied Heating Enabled
1675 | 1457 | Low Ambient Start
1675 | 1458 | Pre Occupancy Purge Time
1675 | 1459 | Pre Occupancy Purge Upper SAT Setpoint
1675 | 1460 | Pre Occupancy Purge Lower SAT Setpoint
1675 | 1461 | Alarm Delay
1675 | 1469 | Auto Changeover
1675 | 1494 | Setpoint Lower Limit
1675 | 1519 | High Alarm Text
1675 | 1520 | Low Alarm Text
1675 | 1521 | Unreliable Sensor Text
1675 | 1529 | Defrost
1675 | 1567 | Unique Equipment Identifier
1675 | 1594 | Parity
1675 | 1595 | Stop Bits
1675 | 1596 | No Reliable Zone Temp Alarm
1675 | 1597 | Network Occupancy Timeout Enable
1675 | 1598 | Network Occupancy Timeout Time
1675 | 1599 | Network Occupancy Request Time
1675 | 1605 | Econ Sensor Fault Indications
1675 | 1679 | VAV Operating Cooling Setpoint
1675 | 1680 | Serial Flash Size
1675 | 1681 | Discharge Pressure Sensor Fault
1675 | 1682 | Discharge Temperature Sensor Fault
1675 | 1683 | BLE Connection Status
1675 | 1684 | Initiate Connection
1675 | 1685 | PIN
1675 | 1686 | BLE Device Name
1675 | 1687 | Bluetooth Firmware Version
1675 | 1688 | Status
1675 | 1689 | VZC Online
1675 | 1690 | Verasys
1675 | 1691 | Bluetooth Enabled
1675 | 1692 | Clear Bluetooth Connections
1681 | 0 | Liquid
1681 | 1 | Discharge
1682 | 0 | R22
1682 | 1 | R12
1682 | 2 | R500
1682 | 3 | R134A
1682 | 4 | R410A
1682 | 5 | R502
1682 | 6 | R409A
1682 | 7 | 404A
1682 | 8 | 507A
1682 | 9 | R407C
1682 | 10 | n
1682 | 11 | R454B
1684 | 0 | TxV
1684 | 1 | FO
1684 | 2 | TxV Or FO
1684 | 3 | n
1685 | 0 | Not Used
1685 | 1 | Package Cool
1685 | 2 | Package HP
1685 | 3 | Split Cool
1685 | 4 | Split HP
1685 | 5 | Water Source Package HP
1685 | 6 | Water Source Split HP
1685 | 7 | Water Cooled Package Cool
1685 | 8 | Water Cooled Split Cool
1685 | 9 | Walk In Cooler
1685 | 10 | Walk In Freezer
1685 | 11 | n
1686 | 0 | On
1686 | 1 | Off
1694 | 0 | Unknown Status
1694 | 1 | Basic Data Not Available Manual Entry
1694 | 2 | Basic Data Not Available
1694 | 3 | Return Wet Bulb Temp Not Available
1694 | 4 | Return Air Temp And Humidity Not Available
1694 | 5 | Return Air Temp Not Available
1694 | 6 | Sensor Not Attached To Tool
1694 | 7 | Tool Not Connected To Unit
1694 | 8 | Unit is Off
1694 | 9 | Ambient Temp Out Of Range
1694 | 10 | Return Air Wet-Bulb Temp Out Of Range
1694 | 11 | Ambient And Return Air Wet-Bulb Temp Out Of Range
1694 | 12 | Ambient Temp Too Low
1694 | 13 | Ambient Temp Too High
1694 | 14 | Return Air Wet-Bulb Temp Too Low
1694 | 15 | Return Air Wet-Bulb Temp Too High
1694 | 16 | Invalid Discharge Pressure or Ambient
1694 | 17 | Invalid Liquid Temp Greater Than Condensing Temp
1694 | 18 | Invalid Suction Temp or Suction Pressure
1694 | 19 | Invalid Suction Pressure or Ambient
1694 | 20 | Invalid Liquid Temp or Ambient
1694 | 21 | Invalid Suction Pressure or Return Air Temp
1694 | 22 | Invalid Liquid Temp or Return Air Temp
1694 | 23 | Invalid Liquid Pressure or Ambient
1694 | 24 | Invalid Suction Temp or Ambient
1694 | 25 | Invalid Return Air Temp or Supply Air Temp
1694 | 26 | Invalid Supply Air Temp or Suction Pressure
1694 | 27 | Invalid Return Air Dry-Bulb or Return Air Wet-Bulb
1694 | 28 | Invalid Supply Air or Supply Air Wet-Bulb
1694 | 29 | Invalid Return Air Wet-Bulb or Supply Air Wet-Bulb
1694 | 30 | Invalid Liquid Pressure and Suction Pressure
1694 | 31 | Invalid Suction Temp
1694 | 32 | Invalid Liquid Temp And Suction Temp
1694 | 33 | Unfavorable Test Condition Retest At Another Time
1694 | 34 | Refrigerant Flow Restriction
1694 | 35 | Excessive Refrigerant Flow
1694 | 36 | Inefficient Compressor
1694 | 37 | Non-Condensables
1694 | 38 | Flow Restriction Caused By Non-Condensables
1694 | 39 | High Side Heat Transfer Problem
1694 | 40 | High Side Heat Transfer Problem
1694 | 41 | High Side Heat Transfer Problem
1694 | 42 | Low Side Heat Transfer Problem
1694 | 43 | Low Side Heat Transfer Problem
1694 | 44 | Low Side Heat Transfer Problem
1694 | 45 | Low Side Heat Transfer Problem
1694 | 46 | Low Side Heat Transfer Problem
1694 | 47 | Low Side Heat Transfer Problem
1694 | 48 | Low Side Heat Transfer Problem
1694 | 49 | Reduce Evaporator Airflow
1694 | 50 | Add Charge
1694 | 51 | Add Charge
1694 | 52 | Add Charge
1694 | 53 | Add Charge
1694 | 54 | Add Charge or Refrigerant Flow Restriction
1694 | 55 | Recover Charge
1694 | 56 | Recover Charge
1694 | 57 | Recover Charge
1694 | 58 | Add Charge
1694 | 59 | Add Charge
1694 | 60 | Low Side Heat Transfer Problem
1694 | 61 | Low Side Heat Transfer Problem
1694 | 62 | Recover Charge
1694 | 63 | Recover Charge
1694 | 64 | Recover Charge
1694 | 65 | Refrigerant Flow Restriction
1694 | 66 | Excessive Refrigerant Flow
1694 | 67 | Low Side Heat Transfer Problem
1694 | 68 | Safe And Reasonable Performance
1694 | 69 | Return Air Dry-Bulb Temp Too Low
1694 | 70 | Return Air Dry-Bulb Temp Too High
1694 | 71 | Unit Energy Efficiency Ratio Too Low
1694 | 72 | Unit Energy Efficiency Ratio Too High
1694 | 73 | Unit EI below 75% expected performance
1694 | 74 | Unit CI below 75% expected performance
1694 | 75 | Unit EI & CI below 75% expected performance
1694 | 1000 | FDD Sensor Unreliable
1694 | 1001 | Driving Conditions Unreliable
1694 | 1002 | Equipment Info Unreliable
1694 | 1003 | Initialized Awaiting Steady State
1694 | 1004 | Heat Pump Active Diagnostics Not Available
1696 | 0 | Alarm
1696 | 1 | Normal
1698 | 0 | Yes
1698 | 1 | No
1701 | 0 | False
1701 | 1 | True
1708 | 0 | Firmware Error
1708 | 1 | Reload
1708 | 2 | USB Flash
1708 | 3 | Inserted
1708 | 4 | View Version
1708 | 5 | Load Firmware
1708 | 6 | Restore
1708 | 7 | Full Clone
1708 | 8 | Partial Clone
1708 | 9 | Backup
1708 | 10 | Setup Done?
1708 | 11 | Settings
1708 | 12 | No Factory
1708 | 13 | Factory Defaults
1708 | 14 | Remain
1708 | 15 | Start
1708 | 16 | No Load
1708 | 17 | Files
1708 | 18 | USB Fail
1708 | 19 | Current Version
1708 | 20 | Corrupt
1708 | 21 | Load Fail
1708 | 22 | Error
1708 | 23 | Done
1708 | 24 | Fail
1708 | 25 | Status
1708 | 26 | Alarms
1708 | 27 | Summary
1708 | 28 | Commission
1708 | 29 | Controller
1708 | 30 | Update
1708 | 31 | Details
1708 | 32 | Active
1708 | 33 | History
1708 | 34 | Soft Reset
1708 | 35 | Clear History
1708 | 36 | Confirm
1708 | 37 | Reset System
1708 | 38 | ?Shorted
1708 | 39 | ?Open
1708 | 40 | ?OutRnge
1708 | 41 | ?Unrel
1708 | 42 | ?Unavail
1708 | 43 | ?Unknown
1708 | 44 | Firmware OK
1708 | 45 | Firmware versions do not match pkg
1708 | 46 | UP
1708 | 47 | Backing
1708 | 48 | Timers
1708 | 49 | Cancel
1708 | 50 | No Events
1708 | 51 | No clone Package Present
1708 | 52 | No Restore Package Present
1708 | 53 | No Package Present
1708 | 54 | Year
1708 | 55 | Month
1708 | 56 | Day
1708 | 57 | Minute
1708 | 58 | Hour
1708 | 59 | Error No Group
1708 | 60 | Write
1708 | 61 | Error on Unit Status read
1708 | 62 | Too many files to list
1708 | 63 | Too many packages to list
1708 | 64 | Self Test
1708 | 65 | Export
1708 | 66 | Exporting
1708 | 67 | Trend
1708 | 68 | No
1708 | 69 | USB
1708 | 70 | Missing
1708 | 71 | Write Fail
1708 | 72 | Pause
1708 | 73 | Test Status
1708 | 74 | Export Trend
1708 | 75 | Board will reset
1708 | 76 | View Results
1708 | 77 | Fan Running?
1708 | 78 | Econ Open?
1708 | 79 | Yes(Enter) No(Cancel)
1708 | 80 | SelftestReport
1708 | 81 | Unit Name
1708 | 82 | Unit Model
1708 | 83 | Unit Firmware
1708 | 84 | Unit Serial
1708 | 85 | Time
1708 | 86 | Date
1708 | 87 | Timezone
1708 | 88 | Operational Space Temperature
1708 | 89 | Operational Space Humidity
1708 | 90 | Outdoor Air Temperature
1708 | 91 | Outdoor Air Humidity
1708 | 92 | Supply Air Temperature
1708 | 93 | Suction Pressure
1708 | 94 | Fan Test
1708 | 95 | Compressor 1 Test
1708 | 96 | Compressor 2 Test
1708 | 97 | Compressor 3 Test
1708 | 98 | Compressor 4 Test
1708 | 99 | Heating 1 Test
1708 | 100 | Heating 2 Test
1708 | 101 | Heating 3 Test
1708 | 102 | Econ Test
1708 | 103 | Exhaust Test
1708 | 104 | Board may reset
1708 | 105 | Minutes
1708 | 106 | Attempting to access USB
1708 | 107 | Start commissioning mode?
1708 | 108 | Control will be disabled
1708 | 109 | View Today's Schedule
1708 | 110 | View Weekly Schedule
1708 | 111 | Edit Weekly Schedule
1708 | 112 | Add Event
1708 | 113 | Remove Event
1708 | 114 | Select Weekday
1708 | 115 | Maximum Events Reached
1708 | 116 | No Scheduled Events
1708 | 117 | List Too Long
1708 | 118 | Password Enabled
1708 | 119 | Set Password
1708 | 120 | Confirm Password
1708 | 121 | Enter Password
1708 | 122 | Incorrect Password Entered
1708 | 123 | Password Entries Don't Match
1708 | 124 | Password Settings Updated
1708 | 125 | Binary Input 1
1708 | 126 | Binary Input 2
1708 | 127 | Binary Input 3
1708 | 128 | Binary Input 4
1708 | 129 | Analog Input 5
1708 | 130 | Analog Input 6
1708 | 131 | Analog Input 7
1708 | 132 | Analog Input 8
1708 | 133 | Analog Input 9
1708 | 134 | Alarm Log
1708 | 135 | Setup
1708 | 136 | Advanced Setup
1708 | 137 | Advanced Status
1708 | 138 | Board may restart several times
1708 | 139 | FWU Complete
1708 | 140 | System
1708 | 141 | Load Remote Pkg
1708 | 142 | Transfer Over FC Bus
1708 | 143 | Binary Input 5
1708 | 144 | Binary Input 6
1708 | 145 | Binary Input 7
1708 | 146 | Binary Input 8
1708 | 147 | Binary Input 9
1708 | 148 | Binary Input 10
1708 | 149 | Binary Input 11
1708 | 150 | Binary Input 12
1708 | 151 | Analog Input 13
1708 | 152 | Analog Input 14
1708 | 153 | Analog Input 15
1708 | 154 | Analog Input 16
1708 | 155 | Analog Input 17
1708 | 156 | Analog Input 18
1709 | 0 | Unit-S
1709 | 1 | Name
1709 | 2 | Model#
1709 | 3 | Serial#
1709 | 4 | FirmVer
1709 | 5 | Firm-S
1709 | 6 | Htg-Type
1709 | 7 | HGR-Inst
1709 | 8 | ExFType
1709 | 9 | UCB24VForOutp
1709 | 11 | Y1-Tstat
1709 | 12 | Y2-Tstat
1709 | 13 | Y3-Tstat
1709 | 14 | Y4-Tstat
1709 | 15 | W1-Tstat
1709 | 16 | W2-Tstat
1709 | 17 | W3-Tstat
1709 | 18 | G-Tstat
1709 | 19 | Occ-Tstat
1709 | 20 | X-Out
1709 | 21 | Tstat-Only
1709 | 22 | OccSrc
1709 | 23 | OprOcc
1709 | 24 | OccMode
1709 | 25 | NetTempOcc
1709 | 26 | NetOcc
1709 | 27 | TempOccTimeout
1709 | 28 | OprST
1709 | 29 | STSrc
1709 | 30 | STAlarmOffset
1709 | 31 | STAlarmDelay
1709 | 32 | ST
1709 | 33 | NetST
1709 | 34 | OprIAQ
1709 | 35 | IAQSrc
1709 | 36 | IAQ
1709 | 37 | IAQRange
1709 | 38 | NetIAQ
1709 | 39 | OprSH
1709 | 40 | SHSrc
1709 | 41 | RAH
1709 | 42 | NetSH
1709 | 43 | OprFanReq
1709 | 44 | FanReqSrc
1709 | 45 | NetFanReq
1709 | 46 | OprSSO
1709 | 47 | SSOSrc
1709 | 48 | SSO
1709 | 49 | NetSSO
1709 | 50 | SSORange
1709 | 51 | #NetSensors
1709 | 52 | OprOAT
1709 | 53 | OATSrc
1709 | 54 | OAT
1709 | 55 | NetOAT
1709 | 56 | OprOAH
1709 | 57 | OA-Enth
1709 | 58 | OAHSrc
1709 | 59 | OAH
1709 | 60 | NetOAH
1709 | 61 | OprOAQ
1709 | 62 | OAQSrc
1709 | 63 | OAQ
1709 | 64 | OAQRange
1709 | 65 | NetOAQ
1709 | 66 | Fan-S
1709 | 67 | FanVFD
1709 | 68 | FanVFDFlt
1709 | 69 | FanOvrload
1709 | 70 | Fan-RT
1709 | 71 | FanCtl-Type
1709 | 72 | APSSetup
1709 | 73 | APS
1709 | 74 | FanOnDlyCool
1709 | 75 | FanOffDlyCool
1709 | 76 | FanOnDlyHeat
1709 | 77 | FanOffDlyHeat
1709 | 78 | DFS
1709 | 79 | Fan
1709 | 80 | SAT
1709 | 81 | DctPrs
1709 | 82 | DctPrs-Sp
1709 | 83 | DctShutdownSp
1709 | 84 | FanOnOcc
1709 | 85 | FanOffStartHeat
1709 | 86 | FanOnly-%Cmd
1709 | 87 | 1ClgStg-%Cmd
1709 | 88 | 2ClgStg-%Cmd
1709 | 89 | 1HtgStg-%Cmd
1709 | 90 | 2HtgStg-%Cmd
1709 | 91 | Clg-En
1709 | 92 | #ClgStgs
1709 | 93 | Clg-S
1709 | 94 | MinRtCoolStg
1709 | 95 | LeadLag-En
1709 | 96 | LowAmbFanPrerunCool
1709 | 97 | ClgOATCutout-En
1709 | 98 | ClgOATCutout
1709 | 99 | EconLoad-En
1709 | 100 | AllCompOff-Econ
1709 | 101 | LowAmb10On5OffSp
1709 | 102 | TempHumCtrl-En
1709 | 103 | TempHum-Sp
1709 | 104 | MaxTempHumSpOff
1709 | 105 | TempHumValPerDegOff
1709 | 106 | SATCoolLimit-En
1709 | 107 | SATCoolLimit-Sp
1709 | 108 | Freeze-Sp
1709 | 109 | CN-Fan
1709 | 110 | CF2
1709 | 111 | UnitType
1709 | 112 | EER
1709 | 113 | SubcoolGoal
1709 | 114 | RefrigType
1709 | 115 | HiSidePortLoc
1709 | 116 | EvapCoil-Type
1709 | 117 | CondCoil-Type
1709 | 118 | InMeterDev-Type
1709 | 119 | SATUp-Sp
1709 | 120 | SATLo-Sp
1709 | 121 | SATRst-Sp
1709 | 122 | OprVAVClg-Sp
1709 | 123 | ClgOcc-Sp
1709 | 124 | ClgUnocc-Sp
1709 | 125 | OprCVClg-Sp
1709 | 127 | C1
1709 | 128 | C2
1709 | 129 | C3
1709 | 130 | C4
1709 | 131 | C1-S
1709 | 132 | C2-S
1709 | 133 | C3-S
1709 | 134 | C4-S
1709 | 135 | C1-En
1709 | 136 | C2-En
1709 | 137 | C3-En
1709 | 138 | C4-En
1709 | 139 | HGP-Inst
1709 | 140 | C1RunTim
1709 | 141 | C2RunTim
1709 | 142 | C3RunTim
1709 | 143 | C4RunTim
1709 | 148 | C1OnTmr
1709 | 149 | C2OnTmr
1709 | 150 | C3OnTmr
1709 | 151 | C4OnTmr
1709 | 152 | C1ASCDTmr
1709 | 153 | C2ASCDTmr
1709 | 154 | C3ASCDTmr
1709 | 155 | C4ASCDTmr
1709 | 156 | HPS1
1709 | 157 | HPS2
1709 | 158 | HPS3
1709 | 159 | HPS4
1709 | 160 | HPS1-LO
1709 | 161 | HPS2-LO
1709 | 162 | HPS3-LO
1709 | 163 | HPS4-LO
1709 | 164 | LPS1
1709 | 165 | LPS2
1709 | 166 | LPS3
1709 | 167 | LPS4
1709 | 168 | LPS1-LO
1709 | 169 | LPS2-LO
1709 | 170 | LPS3-LO
1709 | 171 | LPS4-LO
1709 | 172 | FS1
1709 | 173 | FS2
1709 | 174 | FS3
1709 | 175 | FS4
1709 | 176 | FS1-LO
1709 | 177 | FS2-LO
1709 | 178 | FS3-LO
1709 | 179 | FS4-LO
1709 | 180 | EC1
1709 | 181 | EC2
1709 | 182 | EC3
1709 | 183 | EC4
1709 | 184 | CC1
1709 | 185 | CC2
1709 | 186 | CC3
1709 | 187 | CC4
1709 | 188 | SLP-1
1709 | 189 | SLP-2
1709 | 190 | SLP-3
1709 | 191 | SLP-4
1709 | 192 | LLP-1
1709 | 193 | LLP-2
1709 | 194 | LLP-3
1709 | 195 | LLP-4
1709 | 196 | SLT-1
1709 | 197 | SLT-2
1709 | 198 | SLT-3
1709 | 199 | SLT-4
1709 | 200 | LLT-1
1709 | 201 | LLT-2
1709 | 202 | LLT-3
1709 | 203 | LLT-4
1709 | 204 | C1-SuperHeat
1709 | 205 | C2-SuperHeat
1709 | 206 | C3-SuperHeat
1709 | 207 | C4-SuperHeat
1709 | 208 | C1-SubCool
1709 | 209 | C2-SubCool
1709 | 210 | C3-SubCool
1709 | 211 | C4-SubCool
1709 | 212 | C1-CondTempOvrAmb
1709 | 213 | C2-CondTempOvrAmb
1709 | 214 | C3-CondTempOvrAmb
1709 | 215 | C4-CondTempOvrAmb
1709 | 216 | C1-EI
1709 | 217 | C2-EI
1709 | 218 | C3-EI
1709 | 219 | C4-EI
1709 | 220 | C1-CI
1709 | 221 | C2-CI
1709 | 222 | C3-CI
1709 | 223 | C4-CI
1709 | 224 | Htg-En
1709 | 225 | Htg-S
1709 | 226 | SATHtgLimit-En
1709 | 227 | SATHtgLimit-Sp
1709 | 228 | HtgOATCutout-Sp
1709 | 229 | FSHW
1709 | 230 | MV
1709 | 231 | GV2
1709 | 232 | GV3
1709 | 233 | Limit
1709 | 234 | LimitLO
1709 | 235 | Lim2
1709 | 236 | Lim2LO
1709 | 237 | Lim3
1709 | 238 | Lim3LO
1709 | 239 | HtgOcc-En
1709 | 240 | VAVHtgOcc-SP
1709 | 241 | HtgUnocc-En
1709 | 242 | VAVHtgUnocc-Sp
1709 | 243 | VAVOprHtg-Sp
1709 | 244 | MornW-En
1709 | 245 | MornWRAT-Sp
1709 | 246 | VAV Box
1709 | 250 | #HtgStgs
1709 | 251 | H1
1709 | 252 | H2
1709 | 253 | H3
1709 | 254 | H1-S
1709 | 255 | H2-S
1709 | 256 | H3-S
1709 | 260 | H1OnTmr
1709 | 261 | H2OnTmr
1709 | 262 | H3OnTmr
1709 | 263 | H1ASCDTmr
1709 | 264 | H2ASCDTmr
1709 | 265 | H3ASCDTmr
1709 | 269 | H1RunTim
1709 | 270 | H2RunTim
1709 | 271 | H3RunTim
1709 | 275 | HWV
1709 | 276 | HydReverse
1709 | 277 | HydH1SA-Sp
1709 | 278 | HydH2SA-Sp
1709 | 279 | SATTempHydHt-En
1709 | 280 | SATTempHydHt-Sp
1709 | 281 | Econ-En
1709 | 282 | Econ
1709 | 283 | Econ-Free
1709 | 284 | Econ-S
1709 | 285 | FreeClg-Mode
1709 | 286 | FreeClg-Sel
1709 | 287 | EconOAT-SpEn
1709 | 288 | EconOAEnth-Sp
1709 | 289 | LowAmb-Sp
1709 | 290 | LowAmb-MinPos
1709 | 293 | MAT
1709 | 295 | SAH
1709 | 296 | RA-Enth
1709 | 297 | RAT
1709 | 298 | DVent-Mode
1709 | 299 | DVentMaxEconPos
1709 | 300 | DVentIAQ-Sp
1709 | 301 | DVentDiff-Sp
1709 | 309 | ExFan
1709 | 310 | ExFanVFD
1709 | 311 | ExF-S
1709 | 312 | ExFanVFDFlt
1709 | 313 | ExF-RunTim
1709 | 314 | Bldg-Sp
1709 | 315 | BldgPres
1709 | 316 | EAD-O
1709 | 317 | ExDmpPosFanOn
1709 | 318 | ExDmpPosFanOff
1709 | 319 | EconDmpPosFanOn
1709 | 320 | EconDmpPosFanOff
1709 | 321 | ERV-En
1709 | 322 | ERVUnoccFan-En
1709 | 323 | HGR-En
1709 | 324 | HGR
1709 | 325 | HGR-S
1709 | 326 | HGRHum-Sp
1709 | 327 | HGRAlt-En
1709 | 328 | HGRAltWrite
1709 | 329 | MOAFlow-Sp
1709 | 330 | Fr Air
1709 | 331 | MOA-Range
1709 | 332 | OprPurgeCmd
1709 | 333 | PurgeCmdSrc
1709 | 334 | Purge
1709 | 335 | NetPurge
1709 | 336 | SD
1709 | 337 | Language
1709 | 338 | Units
1709 | 339 | Relearn
1709 | 340 | BASCom
1709 | 341 | Comm-S
1709 | 342 | Time
1709 | 343 | Date
1709 | 349 | TimeZone
1709 | 352 | Address
1709 | 353 | DeviceId
1709 | 354 | OprBaudRate
1709 | 355 | BaudRate
1709 | 357 | UCBMainVer
1709 | 358 | UCBAppVer
1709 | 360 | UCBHardVer
1709 | 361 | EconMainVer
1709 | 362 | EconAppVer
1709 | 364 | EconHardVer
1709 | 365 | 4StgMainVer
1709 | 366 | 4StgAppVer
1709 | 368 | 4StgHardVer
1709 | 369 | FDDMMainVer
1709 | 370 | FDDMAppVer
1709 | 372 | FDDMHardVer
1709 | 373 | FDDSMainVer
1709 | 374 | FDDSAppVer
1709 | 376 | FDDSHardVer
1709 | 380 | OCC
1709 | 381 | Econ-MinPos
1709 | 382 | AirMonStation
1709 | 387 | Control
1709 | 388 | Clg
1709 | 389 | DVent
1709 | 391 | Firm
1709 | 392 | Htg
1709 | 397 | Misc
1709 | 398 | Network
1709 | 399 | NetworkInputs
1709 | 402 | PowerEx
1709 | 404 | Safeties
1709 | 405 | Sensors
1709 | 406 | Service
1709 | 408 | Setup
1709 | 409 | SmokeCtrl
1709 | 410 | Stage 1
1709 | 411 | Stage 2
1709 | 412 | Stage 3
1709 | 413 | Stage 4
1709 | 414 | Status
1709 | 415 | Thermostat
1709 | 437 | EconCntlr
1709 | 438 | 4StgCntlr
1709 | 439 | FDDMCntlr
1709 | 440 | FDDSCntlr
1709 | 442 | 3ClgStg-%Cmd
1709 | 443 | 4ClgStg-%Cmd
1709 | 444 | 3HtgStg-%Cmd
1709 | 445 | OutMeterDev-Type
1709 | 446 | DevName
1709 | 447 | LowSpeedFan-MinPos
1709 | 448 | TempOCC
1709 | 449 | EconDampPos
1709 | 450 | ExcessOutAirFlt
1709 | 451 | NotEconFlt
1709 | 452 | EconDampFlt
1709 | 453 | EconWhenShouldNotFlt
1709 | 461 | CVHtgOcc-SP
1709 | 462 | CVHtgUnocc-Sp
1709 | 463 | CVOprHtg-Sp
1709 | 464 | ResetLO
1709 | 466 | SysCntlrs
1709 | 467 | UCB
1709 | 472 | Unit
1709 | 473 | Descrip
1709 | 475 | DFSInst
1709 | 478 | ClgCktTestS-1
1709 | 479 | ClgCktTestS-2
1709 | 480 | ClgCktTestS-3
1709 | 481 | ClgCktTestS-4
1709 | 482 | UnitCap
1709 | 483 | FanPower
1709 | 484 | SuperHeatGoal
1709 | 485 | Altitude
1709 | 486 | MornC-En
1709 | 487 | MornCRAT-Sp
1709 | 488 | OptStrt-En
1709 | 489 | OccBI-En
1709 | 490 | EarlyStrtPeriod
1709 | 491 | #HtPumpStgs
1709 | 493 | TestDefrostEnable
1709 | 494 | CompDelayEnable
1709 | 495 | DefrostCurveSel
1709 | 496 | DefrostState
1709 | 528 | LoadShedEnable
1709 | 529 | LoadShedRateLim
1709 | 530 | LoadShedAdjust
1709 | 532 | T24LoadShed
1709 | 534 | C1-EvapTempValue
1709 | 535 | C2-EvapTempValue
1709 | 536 | C3-EvapTempValue
1709 | 537 | C4-EvapTempValue
1709 | 538 | TimeToNextOcc
1709 | 539 | OprMode
1709 | 550 | #GasVlvs
1709 | 551 | C1-CondTempOAHigh
1709 | 552 | C2-CondTempOAHigh
1709 | 553 | C3-CondTempOAHigh
1709 | 554 | C4-CondTempOAHigh
1709 | 555 | C1-CondTempOALow
1709 | 556 | C2-CondTempOALow
1709 | 557 | C3-CondTempOALow
1709 | 558 | C4-CondTempOALow
1709 | 559 | C1-SuperheatHigh
1709 | 560 | C2-SuperheatHigh
1709 | 561 | C3-SuperheatHigh
1709 | 562 | C4-SuperheatHigh
1709 | 563 | C1-SuperheatLow
1709 | 564 | C2-SuperheatLow
1709 | 565 | C3-SuperheatLow
1709 | 566 | C4-SuperheatLow
1709 | 567 | C1-SubcoolHigh
1709 | 568 | C2-SubcoolHigh
1709 | 569 | C3-SubcoolHigh
1709 | 570 | C4-SubcoolHigh
1709 | 571 | C1-SubcoolLow
1709 | 572 | C2-SubcoolLow
1709 | 573 | C3-SubcoolLow
1709 | 574 | C4-SubcoolLow
1709 | 575 | C1-EvapTempHigh
1709 | 576 | C2-EvapTempHigh
1709 | 577 | C3-EvapTempHigh
1709 | 578 | C4-EvapTempHigh
1709 | 579 | C1-EvapTempLow
1709 | 580 | C2-EvapTempLow
1709 | 581 | C3-EvapTempLow
1709 | 582 | C4-EvapTempLow
1709 | 583 | ModelName
1709 | 610 | Standard
1709 | 611 | FDD
1709 | 613 | RevVlv
1709 | 614 | AuxHtg
1709 | 615 | Mode
1709 | 616 | HtgAdapTunEn
1709 | 617 | ClgAdapTunEn
1709 | 618 | HeatPmp
1709 | 622 | #LimSwtchs
1709 | 623 | SZVAVEn
1709 | 624 | DATMaxHtgSP
1709 | 625 | DATSatSP
1709 | 626 | DATClgMinSP
1709 | 627 | #RefrigSys
1709 | 628 | FcBusMode
1709 | 629 | DirLoadshd
1709 | 630 | EconMechStp
1709 | 631 | HdwrReset
1709 | 632 | Redline
1709 | 633 | OffDurUnocc
1709 | 637 | Prop
1709 | 638 | SZ VAV
1709 | 639 | CntrlType
1709 | 640 | EquipType
1709 | 641 | UnitEn
1709 | 642 | HGRUnoccHum-SP
1709 | 643 | HGRUnocc-En
1709 | 644 | PmpOut-En
1709 | 646 | EconFltDetectEn
1709 | 647 | SZVAVMinFanSpd
1709 | 648 | StgClgCmd
1709 | 649 | StgHtgCmd
1709 | 650 | PropHtgCmd
1709 | 651 | PIDTunRst
1709 | 653 | EconAlrmDly
1709 | 654 | EconPosErr
1709 | 655 | EconMinErr
1709 | 656 | SZVAVClgOcc-Sp
1709 | 657 | SZVAVClgUnocc-Sp
1709 | 658 | SZVAVHtgOcc-Sp
1709 | 659 | SZVAVHtgUnocc-Sp
1709 | 660 | OprSZVAVClg-Sp
1709 | 661 | OprSZVAVHtg-Sp
1709 | 662 | LowAmb-En
1709 | 663 | VAVClgUnocc-Sp
1709 | 664 | FrAir-En
1709 | 665 | SZVAVClgLd
1709 | 666 | SZVAVHtgLd
1709 | 668 | EncodeType
1709 | 669 | HGR-Diff
1709 | 690 | ClgManualTune
1709 | 691 | HtgManualTune
1709 | 692 | LL_Enable
1709 | 693 | LL_UpSAT_SP
1709 | 694 | LL_LowSAT_SP
1709 | 695 | 4pipeEna
1709 | 696 | PreOccPurgeEna
1709 | 697 | LowAmbStart
1709 | 698 | PreOccPurgeTime
1709 | 699 | PreOccUpSAT_SP
1709 | 700 | PreOccLowSAT_SP
1709 | 701 | HtgClgSP-Mode
1709 | 702 | Common-SP
1709 | 703 | Parity
1709 | 704 | StopBits
1709 | 709 | PressurizeNotPurge
1709 | 710 | Event1Value
1709 | 711 | Event2Value
1709 | 712 | Event3Value
1709 | 713 | Event4Value
1709 | 714 | Event5Value
1709 | 715 | Event1Set
1709 | 716 | Event2Set
1709 | 717 | Event3Set
1709 | 718 | Event4Set
1709 | 719 | Event5Set
1709 | 720 | Quick Start
1709 | 721 | UseDFSforDehum
1709 | 723 | CalFaultDetectEn
1709 | 724 | OATDefPerm
1709 | 725 | DehumEvapLowSp
1709 | 726 | SatisfiedDehum
1709 | 727 | CoolDuringHeatLimit
1709 | 728 | ModHGRFullOpenAllowed
1709 | 729 | OprEvapTempSp
1709 | 730 | OprHGRTempSp
1709 | 731 | Dehum%Cmd
1709 | 732 | CondFan2OATCutoutSP
1709 | 733 | FDDAlarmEn
1709 | 736 | EconSensorFaults
1709 | 737 | ModHGR
1709 | 738 | SerialFlashSize
1709 | 753 | CondFan2MaxPosCutoutEn
1709 | 754 | Cir1HighPresUnloadEn
1709 | 755 | Cir1LowPresUnloadEn
1709 | 756 | Cir2HighPresUnloadEn
1709 | 757 | Cir2LowPresUnloadEn
1709 | 766 | NS-Calibration
1709 | 767 | ClgRapidStartEn
1709 | 768 | HtgRapidStartEn
1709 | 769 | ClgRapidStartTime
1709 | 770 | HtgRapidStartTime
1709 | 771 | Bluetooth
1709 | 772 | BT-Status
1709 | 773 | BT-Command
1709 | 774 | PIN
1709 | 775 | BT-Name
1709 | 776 | BT-Version
1709 | 777 | UseOprSTforHGR
1709 | 778 | COBP Mode
1709 | 779 | COBP SAT SP
1709 | 780 | OATHPCutout
1709 | 781 | HybridMode
1709 | 782 | HGRModVlvMaxSP
1709 | 783 | HGRModVlvMinSP
1709 | 784 | BT-Ena
1709 | 785 | BT-ClrInfo
1709 | 787 | A2LLeakAlarm
1709 | 788 | COS
1709 | 791 | A2LLeakAlarm-LO
1709 | 792 | NeuAirModHGR-En
1709 | 793 | NeuAirModHGR-Off
1709 | 794 | DualFuelHP-En
1709 | 795 | RevVlvDelay
1709 | 796 | DualFuelOATHPCutout
1709 | 797 | COS-En
1712 | 0 | Status
1712 | 1 | Summary
1712 | 2 | Commissioning
1712 | 3 | Controller
1712 | 4 | Details
1712 | 5 | Clone
1712 | 6 | Full Clone
1712 | 7 | Partial Clone 1
1712 | 8 | BACnet Objects
1712 | 9 | Network Override
1712 | 15 | Network Setup
1712 | 24 | Trend
1712 | 25 | Set Schedule
1712 | 26 | Controller Info
1712 | 44 | Options
1712 | 52 | Schedule
1712 | 159 | Alarm Points
1714 | 0 | Air Monitor Station
1714 | 5 | Control
1714 | 6 | Cooling
1714 | 7 | Demand Ventilation
1714 | 8 | Economizer
1714 | 10 | Fan
1714 | 11 | Firmware
1714 | 12 | Heating
1714 | 13 | Hot Gas Reheat
1714 | 16 | Indoor Fan
1714 | 18 | Misc
1714 | 19 | Network
1714 | 20 | Network Inputs
1714 | 23 | Power Exhaust
1714 | 25 | Safeties
1714 | 26 | Sensors
1714 | 27 | Service
1714 | 29 | Setup
1714 | 30 | Smoke Control
1714 | 31 | Stage 1
1714 | 32 | Stage 2
1714 | 33 | Stage 3
1714 | 34 | Stage 4
1714 | 35 | Status
1714 | 36 | Thermostat
1714 | 39 | Compressor Stage 1 Status
1714 | 40 | Compressor Stage 1 Enabled
1714 | 41 | Min On Time Remaining 1
1714 | 42 | Anti-Short Cycle Delay Time Remaining 1
1714 | 43 | Compressor Stage Accumulated Runtime 1
1714 | 44 | Evaporator Coil Temp 1
1714 | 45 | Condenser Coil Temp 1
1714 | 46 | Suction Pressure 1
1714 | 47 | Liquid Pressure 1
1714 | 48 | Suction Temperature 1
1714 | 49 | Liquid Temperature 1
1714 | 52 | Efficiency Index 1
1714 | 53 | Capacity Index 1
1714 | 54 | Condensing Temperature over Ambient 1
1714 | 55 | Compressor Stage 2 Status
1714 | 56 | Compressor Stage 2 Enabled
1714 | 57 | Min On Time Remaining 2
1714 | 58 | Anti-Short Cycle Delay Time Remaining 2
1714 | 59 | Compressor Stage Accumulated Runtime 2
1714 | 60 | Evaporator Coil Temp 2
1714 | 61 | Condenser Coil Temp 2
1714 | 62 | Suction Pressure 2
1714 | 63 | Liquid Pressure 2
1714 | 64 | Suction Temperature 2
1714 | 65 | Liquid Temperature 2
1714 | 68 | Efficiency Index 2
1714 | 69 | Capacity Index 2
1714 | 70 | Condensing Temperature over Ambient 2
1714 | 71 | Compressor Stage 3 Status
1714 | 72 | Compressor Stage 3 Enabled
1714 | 73 | Min On Time Remaining 3
1714 | 74 | Anti-Short Cycle Delay Time Remaining 3
1714 | 75 | Compressor Stage Accumulated Runtime 3
1714 | 76 | Evaporator Coil Temp 3
1714 | 77 | Condenser Coil Temp 3
1714 | 78 | Suction Pressure 3
1714 | 79 | Liquid Pressure 3
1714 | 80 | Suction Temperature 3
1714 | 81 | Liquid Temperature 3
1714 | 84 | Efficiency Index 3
1714 | 85 | Capacity Index 3
1714 | 86 | Condensing Temperature over Ambient 3
1714 | 87 | Compressor Stage 4 Status
1714 | 88 | Compressor Stage 4 Enabled
1714 | 89 | Min On Time Remaining 4
1714 | 90 | Anti-Short Cycle Delay Time Remaining 4
1714 | 91 | Compressor Stage Accumulated Runtime 4
1714 | 92 | Evaporator Coil Temp 4
1714 | 93 | Condenser Coil Temp 4
1714 | 94 | Suction Pressure 4
1714 | 95 | Liquid Pressure 4
1714 | 96 | Suction Temperature 4
1714 | 97 | Liquid Temperature 4
1714 | 100 | Efficiency Index 4
1714 | 101 | Capacity Index 4
1714 | 102 | Condensing Temperature over Ambient 4
1714 | 103 | Heating Stage 1 Status
1714 | 104 | Heating Stage 1 Enabled
1714 | 105 | Heating Stage 1 Min On Time Remaining
1714 | 106 | Heating Stage 1 Anti-Short Cycle Delay Time Remaining
1714 | 108 | Heating Stage 1 Accumulated Runtime
1714 | 109 | Heating Stage 2 Status
1714 | 111 | Heating Stage 2 Min On Time Remaining
1714 | 112 | Heating Stage 2 Anti-Short Cycle Delay Time Remaining
1714 | 114 | Heating Stage 2 Accumulated Runtime
1714 | 115 | Heating Stage 3 Status
1714 | 117 | Heating Stage 3 Min On Time Remaining
1714 | 118 | Heating Stage 3 Anti-Short Cycle Delay Time Remaining
1714 | 120 | Heating Stage 3 Accumulated Runtime
1714 | 121 | High Pressure Limit 1
1714 | 122 | Low Pressure Limit 1
1714 | 123 | High Pressure Limit 2
1714 | 124 | Low Pressure Limit 2
1714 | 125 | High Pressure Limit 3
1714 | 126 | Low Pressure Limit 3
1714 | 127 | High Pressure Limit 4
1714 | 128 | Low Pressure Limit 4
1714 | 129 | High Pressure Lockout 1
1714 | 130 | Low Pressure Lockout 1
1714 | 131 | Freeze Condition 1
1714 | 132 | Freeze Condition Lockout 1
1714 | 133 | High Pressure Lockout 2
1714 | 134 | Low Pressure Lockout 2
1714 | 135 | Freeze Condition 2
1714 | 136 | Freeze Condition Lockout 2
1714 | 137 | High Pressure Lockout 3
1714 | 138 | Low Pressure Lockout 3
1714 | 139 | Freeze Condition 3
1714 | 140 | Freeze Condition Lockout 3
1714 | 141 | High Pressure Lockout 4
1714 | 142 | Low Pressure Lockout 4
1714 | 143 | Freeze Condition 4
1714 | 144 | Freeze Condition Lockout 4
1714 | 145 | Compressor Stage Command 1
1714 | 146 | Compressor Stage Command 2
1714 | 147 | Compressor Stage Command 3
1714 | 148 | Compressor Stage Command 4
1714 | 149 | Heating Stage Command 1
1714 | 150 | Heating Stage Command 2
1714 | 151 | Heating Stage Command 3
1714 | 153 | Unit
1714 | 154 | UCB
1714 | 155 | 4 Stage
1714 | 156 | FDD Manager
1714 | 157 | FDD Subordinate
1714 | 162 | Load Shed
1714 | 164 | Evaporating Temperature Value Circuit 1
1714 | 165 | Evaporating Temperature Value Circuit 2
1714 | 166 | Evaporating Temperature Value Circuit 3
1714 | 167 | Evaporating Temperature Value Circuit 4
1714 | 179 | FDD
1714 | 180 | Heat Pump
1714 | 194 | Proportional
1714 | 195 | Single Zone VAV
1714 | 198 | Diagnostics
1714 | 202 | Radio Code Version
1714 | 203 | Active Channel
1714 | 204 | Signal Strength
1714 | 205 | Connection Status
1714 | 206 | Network State
1714 | 207 | IEEE Address
1714 | 208 | Short Address
1714 | 209 | Lost Coordinator Counter
1714 | 210 | Low Memory Counter
1714 | 211 | Dropped Message Counter
1714 | 212 | Heat Cool Setpoint Mode
1714 | 213 | Condenser Fans
1714 | 214 | Fault
1714 | 215 | Heating Stage 1
1714 | 216 | Heating Stage 2
1714 | 217 | Heating Stage 3
1714 | 218 | Cooling Stage 1
1714 | 219 | Cooling Stage 2
1714 | 220 | Cooling Stage 3
1714 | 221 | Cooling Stage 4
1714 | 222 | Pressurize Instead Of Purge
1714 | 223 | Quick Start
1714 | 224 | Use DFS For Dehum
1714 | 226 | Calibration Fault Detect Enable
1714 | 227 | OAT Defrost Permission
1714 | 228 | Dehumidify In Satisfied
1714 | 229 | Dehum Evap Low Setpoint
1714 | 230 | Cooling Allowed During Heat Limit
1714 | 231 | Modulating HGR Valve Full Open Allowed
1714 | 232 | Operational Evap Temperature Sp
1714 | 233 | Operational HGR Temperature Sp
1714 | 234 | Dehumidification % Command
1714 | 235 | Condenser Fan 2 OAT Cutout Setpoint
1714 | 236 | FDD Alarm Enable
1714 | 245 | Modulating Compressor Max Speed
1714 | 246 | Modulating Compressor Min Speed
1714 | 247 | Modulating Cond Fan Max Speed
1714 | 248 | Modulating Cond Fan Min Speed
1714 | 249 | Modulating Cond Fan SDT Low Limit
1714 | 250 | Modulating Cond Fan SDT High Limit
1714 | 251 | Hybrid Mode
1714 | 252 | Mod Hot Gas Reheat
1714 | 253 | Condenser Fan 2 Max Pos Cutout Enable
1714 | 254 | Circuit 1 High Pressure Unload Enable
1714 | 255 | Circuit 1 Low Pressure Unload Enable
1714 | 256 | Circuit 2 High Pressure Unload Enable
1714 | 257 | Circuit 2 Low Pressure Unload Enable
1714 | 258 | Modulating Cond Fan 2 Min Speed
1714 | 259 | Modulating Cond Fan 2 Max Speed
1714 | 260 | Modulating Cond Fan 2 SDT Low Limit
1714 | 261 | Modulating Cond Fan 2 SDT High Limit
1714 | 262 | Modulating Cond Fan SDT Off Setpoint
1714 | 263 | Modulating Cond Fan 2 SDT Off Setpoint
1714 | 264 | DLT Protection Enable
1714 | 265 | High Discharge Line Temp Lockout
1714 | 266 | Netsensor Calibration
1714 | 267 | Cooling Rapid Start Enable
1714 | 268 | Heating Rapid Start Enable
1714 | 269 | Cooling Rapid Start Time
1714 | 270 | Heating Rapid Start Time
1714 | 271 | Bluetooth
1714 | 272 | Use OprST for HGR
1714 | 273 | OAT Heat Pump Cutout
1714 | 274 | HGR Mod Valve Min Setpoint
1714 | 275 | HGR Mod Valve Max Setpoint
1714 | 276 | A2L Leak Detector Alarm
1714 | 277 | Condensate Overflow Switch
1714 | 278 | A2L Lockout Option
1714 | 279 | A2L Lockout Time Interval
1714 | 280 | A2L Leak Detector Alarm-Lockout
1714 | 281 | Neutral Air ModHGR Enable
1714 | 282 | Neutral Air ModHGR Offset
1714 | 283 | Dual Fuel HP Enable
1714 | 284 | Reversing Valve Delay
1714 | 285 | Dual Fuel OAT HP Cutout
1715 | 0 | Unreliable
1715 | 1 | Return Air Temp
1715 | 2 | Local Input
1715 | 3 | Network Sensor
1715 | 4 | BAS Override
1715 | 5 | Not Available
1716 | 0 | None
1716 | 1 | Event Generator Configuration Error
1716 | 2 | Calibration Error
1716 | 100 | Parameters Not Configured, Use Default
1716 | 101 | Economizer Firmware Failure
1716 | 102 | 4-Stage Firmware Failure
1716 | 103 | Main Controller Firmware Failure
1716 | 104 | C1 Locked Out Due to High Pressure
1716 | 105 | C2 Locked Out Due to High Pressure
1716 | 106 | C3 Locked Out Due to High Pressure
1716 | 107 | C4 Locked Out Due to High Pressure
1716 | 108 | C1 Locked Out Due to Low Pressure
1716 | 109 | C2 Locked Out Due to Low Pressure
1716 | 110 | C3 Locked Out Due to Low Pressure
1716 | 111 | C4 Locked Out Due to Low Pressure
1716 | 112 | C1 Locked Out Due to Coil Freeze
1716 | 113 | C2 Locked Out Due to Coil Freeze
1716 | 114 | C3 Locked Out Due to Coil Freeze
1716 | 115 | C4 Locked Out Due to Coil Freeze
1716 | 116 | Exhaust Fan VFD Failure
1716 | 117 | HS1 Locked Out Due to Limit Switch
1716 | 118 | HS2 Locked Out Due to Limit Switch
1716 | 119 | HS3 Locked Out Due to Limit Switch
1716 | 120 | Outputs Disabled Due to Low Input V
1716 | 121 | Outputs Limited Due to Brownout Input V
1716 | 122 | 4-Stg Outs Disabled Due to Low Input V
1716 | 123 | 4-Stg Outs Limited Due to Brownout V
1716 | 124 | 4-Stage O24 VAC Supply Input Failure
1716 | 125 | 4-Stage Communication Failure
1716 | 126 | Economizer Communication Failure
1716 | 127 | Unit Shutdown Due to Smoke, etc
1716 | 128 | Unit Locked Out Due to APS
1716 | 129 | Duct-P Incorrectly Reading Low
1716 | 130 | Unit Locked Out Due to High Duct-P
1716 | 131 | Unit Locked Out Due to Supply Fan OL
1716 | 132 | Supply Fan VFD Failure
1716 | 133 | No Heat-Cool Due to Unreliable Space-T
1716 | 134 | Unit Has Shutdown-Duct-P Sensor Failure
1716 | 135 | MFC HS1 Locked Out Due to Limit Switch
1716 | 136 | MFC HS2 Locked Out Due to Limit Switch
1716 | 137 | MFC HS3 Locked Out Due to Limit Switch
1716 | 138 | MFC HS4 Locked Out Due to Limit Switch
1716 | 139 | MFC HS1 Locked Out Due to Gas Valve
1716 | 140 | MFC HS2 Locked Out Due to Gas Valve
1716 | 141 | MFC HS3 Locked Out Due to Gas Valve
1716 | 142 | MFC HS4 Locked Out Due to Gas Valve
1716 | 143 | MFC Locked Out Due to No APS
1716 | 144 | MFC Locked Out Due to APS Stuck Closed
1716 | 145 | MFC Microelectronics Failure
1716 | 146 | MFC Shutdown Due to Bad Firmware
1716 | 147 | MFC Locked Out Due to Low Input V
1716 | 148 | C1 Locked Out Due to Condensate Overflow
1716 | 149 | Outputs Disabled Due to High Input V
1716 | 150 | EWT Out of Bounds, Comp Oper Suspended
1716 | 151 | LWT Out of Bounds, Comp Oper Suspended
1716 | 152 | SAT Out of Bounds, Comp Oper Suspended
1716 | 153 | C1 Locked Out Due to Water Coil Freeze
1716 | 154 | C1 Locked Out Due to Air Coil Freeze
1716 | 155 | Option Communication Failure
1716 | 156 | CTB Communication Failure
1716 | 157 | Condenser 1 Communication Failure
1716 | 158 | Condenser 2 Communication Failure
1716 | 159 | CTB Outs Disabled Due to Low Input V
1716 | 160 | CTB Outs Limited Due to Brownout V
1716 | 161 | Cond 1 Outs Disabled Due to Low Input V
1716 | 162 | Cond 1 Outs Limited Due to Brownout V
1716 | 163 | Cond 2 Outs Disabled Due to Low Input V
1716 | 164 | Cond 2 Outs Limited Due to Brownout V
1716 | 165 | Option Outs Disabled Due to Low Input V
1716 | 166 | Option Outs Limited Due to Brownout V
1716 | 167 | Exhaust Fan VFD 1 Failure
1716 | 168 | Exhaust Fan VFD 2 Failure
1716 | 169 | Supply Fan VFD 1 Failure
1716 | 170 | Supply Fan VFD 2 Failure
1716 | 171 | Unit Locked Out - Airflow Proof Failure
1716 | 172 | C1A Locked Out Due to High Pressure
1716 | 173 | C1B Locked Out Due to High Pressure
1716 | 174 | C1C Locked Out Due to High Pressure
1716 | 175 | C2A Locked Out Due to High Pressure
1716 | 176 | C2B Locked Out Due to High Pressure
1716 | 177 | C2C Locked Out Due to High Pressure
1716 | 178 | C1A Locked Out Due to Low Pressure
1716 | 179 | C1B Locked Out Due to Low Pressure
1716 | 180 | C1C Locked Out Due to Low Pressure
1716 | 181 | C2A Locked Out Due to Low Pressure
1716 | 182 | C2B Locked Out Due to Low Pressure
1716 | 183 | C2C Locked Out Due to Low Pressure
1716 | 184 | Circuit 1 Locked Out Due to Low Pressure
1716 | 185 | Circuit 2 Locked Out Due to Low Pressure
1716 | 186 | Circuit 1 Locked Out Due to Safety Chain
1716 | 187 | Circuit 2 Locked Out Due to Safety Chain
1716 | 188 | Cooling Locked Out - Condensate Overflow
1716 | 189 | C1A Locked Out - Exceeded Op Env Limits
1716 | 190 | C1A Locked Out Due to Oil Switch
1716 | 191 | Furnace Module 1 Lockout
1716 | 192 | Furnace Module 2 Lockout
1716 | 193 | Furnace Module 3 Lockout
1716 | 194 | Furnace Module 4 Lockout
1716 | 195 | Furnace Module 5 Lockout
1716 | 196 | C1A Locked Out Due to VFD Failure
1716 | 197 | Unit Shut Down by Safety Switch Input
1716 | 198 | Freeze Protect Disabled - Bad Sensor
1716 | 199 | Unit Shut Down by Phase Monitor
1716 | 200 | Condensate Alarm
1716 | 201 | C1 Locked Out - Exceeded Op Env Limits
1716 | 202 | C1 Locked Out Due to VFD Failure
1716 | 203 | C1 Locked Out Due to Oil Switch
1716 | 204 | C1 Locked Out - High Discharge Pressure
1716 | 205 | C2 Locked Out - High Discharge Pressure
1716 | 206 | C3 Locked Out - High Discharge Pressure
1716 | 207 | C4 Locked Out - High Discharge Pressure
1716 | 208 | C1 Locked Out - Low Suction Pressure
1716 | 209 | C2 Locked Out - Low Suction Pressure
1716 | 210 | C3 Locked Out - Low Suction Pressure
1716 | 211 | C4 Locked Out - Low Suction Pressure
1716 | 212 | Unit Locked Out - Iso Damper Closed
1716 | 213 | C1A Locked Out - High Pressure Unload
1716 | 214 | C1B Locked Out - High Pressure Unload
1716 | 215 | C1C Locked Out - High Pressure Unload
1716 | 216 | C2A Locked Out - High Pressure Unload
1716 | 217 | C2B Locked Out - High Pressure Unload
1716 | 218 | C2C Locked Out - High Pressure Unload
1716 | 219 | C1A Locked Out - Low Pressure Unload
1716 | 220 | C1B Locked Out - Low Pressure Unload
1716 | 221 | C1C Locked Out - Low Pressure Unload
1716 | 222 | C2A Locked Out - Low Pressure Unload
1716 | 223 | C2B Locked Out - Low Pressure Unload
1716 | 224 | C2C Locked Out - Low Pressure Unload
1716 | 225 | Unit has Received a Shutdown Request
1716 | 226 | Defrost Disabled - Bad Sensor
1716 | 227 | C1 Locked Out - High Discharge Line Temp
1716 | 228 | Circuit 1 Locked Out Due to Coil Freeze
1716 | 229 | Circuit 2 Locked Out Due to Coil Freeze
1716 | 230 | A2L Leak Detector Alarm
1716 | 231 | A2L Leak Detector Alarm-Lockout
1716 | 232 | Application Failed to Load
1717 | 0 | None
1717 | 1 | Firmware versions do not match package
1717 | 100 | FDD Firmware Failure
1717 | 101 | No Dehum Due to Space Humidity
1717 | 102 | No Air Quality Control Due to IAQ
1717 | 103 | Building Pressure Sensor Failure
1717 | 104 | Outdoor Air Temperature Sensor Failure
1717 | 105 | Return Air Temperature Sensor Failure
1717 | 106 | Supply Air Temperature Sensor Failure
1717 | 107 | 24 VAC Supply Input Failure
1717 | 108 | Evaporator Coil Temp 1 Sensor Failure
1717 | 109 | Condenser Coil Temp 1 Sensor Failure
1717 | 110 | Evaporator Coil Temp 2 Sensor Failure
1717 | 111 | Condenser Coil Temp 2 Sensor Failure
1717 | 112 | Evaporator Coil Temp 3 Sensor Failure
1717 | 113 | Condenser Coil Temp 3 Sensor Failure
1717 | 114 | Evaporator Coil Temp 4 Sensor Failure
1717 | 115 | Condenser Coil Temp 4 Sensor Failure
1717 | 116 | Unit Shutdown Due to Air Proving Switch
1717 | 117 | Unit Shutdown Due to Supply Fan Overload
1717 | 118 | Main Controller Calibration Error
1717 | 119 | FDDM Controller Calibration Error
1717 | 120 | Econ Controller Calibration Error
1717 | 121 | 4 Stage Controller Calibration Error
1717 | 122 | Duct Pressure Sensor Failure
1717 | 123 | FDDS Controller Calibration Error
1717 | 124 | MFC SAT Sensor Failure
1717 | 125 | MFC MAT Sensor Failure
1717 | 126 | MFC Jumper Set to Elite
1717 | 127 | Leaving Water Temp Sensor Failure
1717 | 128 | Return Water Temp Sensor Failure
1717 | 129 | C1 Shutdown Due to Condensate Overflow
1717 | 130 | C1 Shutdown Due to Water Coil Freeze
1717 | 131 | C1 Shutdown Due to Air Coil Freeze
1717 | 132 | SAT Out of Bounds, Check Unit Operation
1717 | 133 | Entering Water Temp Sensor Failure
1717 | 134 | Discharge Air Temperature Sensor Failure
1717 | 135 | Return Fan Pressure Sensor Failure
1717 | 136 | Unit Shutdown Airflow Validation Fail
1717 | 137 | C1A Shutdown Due To High Pressure
1717 | 138 | C1B Shutdown Due To High Pressure
1717 | 139 | C1C Shutdown Due To High Pressure
1717 | 140 | C2A Shutdown Due To High Pressure
1717 | 141 | C2B Shutdown Due To High Pressure
1717 | 142 | C2C Shutdown Due To High Pressure
1717 | 143 | C1A Shutdown Due To Low Pressure
1717 | 144 | C1B Shutdown Due To Low Pressure
1717 | 145 | C1C Shutdown Due To Low Pressure
1717 | 146 | C2A Shutdown Due To Low Pressure
1717 | 147 | C2B Shutdown Due To Low Pressure
1717 | 148 | C2C Shutdown Due To Low Pressure
1717 | 149 | Circuit 1 Shutdown Due To Low Pressure
1717 | 150 | Circuit 2 Shutdown Due To Low Pressure
1717 | 151 | HGR Locked Out - Valve Stuck Open
1717 | 152 | HGR Locked Out - Valve Stuck Closed
1717 | 153 | Option Controller Calibration Error
1717 | 154 | Cond 1 Controller Calibration Error
1717 | 155 | Cond 2 Controller Calibration Error
1717 | 156 | CTB Controller Calibration Error
1717 | 157 | C1A Shutdown - Exceeded Op Env Limits
1717 | 158 | MAT Sensor Failure
1717 | 159 | Supply Fan 1 Failure
1717 | 160 | Supply Fan 2 Failure
1717 | 161 | C1 Shutdown - Exceeded Op Env Limits
1717 | 162 | C1 Shutdown - High Discharge Pressure
1717 | 163 | C2 Shutdown - High Discharge Pressure
1717 | 164 | C3 Shutdown - High Discharge Pressure
1717 | 165 | C4 Shutdown - High Discharge Pressure
1717 | 166 | C1 Shutdown - Low Suction Pressure
1717 | 167 | C2 Shutdown - Low Suction Pressure
1717 | 168 | C3 Shutdown - Low Suction Pressure
1717 | 169 | C4 Shutdown - Low Suction Pressure
1717 | 170 | C1A Shutdown - High Pressure Unload
1717 | 171 | C1B Shutdown - High Pressure Unload
1717 | 172 | C1C Shutdown - High Pressure Unload
1717 | 173 | C2A Shutdown - High Pressure Unload
1717 | 174 | C2B Shutdown - High Pressure Unload
1717 | 175 | C2C Shutdown - High Pressure Unload
1717 | 176 | C1A Shutdown - Low Pressure Unload
1717 | 177 | C1B Shutdown - Low Pressure Unload
1717 | 178 | C1C Shutdown - Low Pressure Unload
1717 | 179 | C2A Shutdown - Low Pressure Unload
1717 | 180 | C2B Shutdown - Low Pressure Unload
1717 | 181 | C2C Shutdown - Low Pressure Unload
1717 | 182 | Exhaust Fan 1 Failure
1717 | 183 | Exhaust Fan 2 Failure
1717 | 184 | Return Fan 1 Failure
1717 | 185 | Outdoor Air Damper BAS Source Lost
1717 | 186 | Exhaust Damper BAS Source Lost
1717 | 187 | Exhaust Fan BAS Source Lost
1718 | 0 | None
1718 | 1 | Reboot
1718 | 100 | Econ Not Economizing When It Should
1718 | 101 | Econ Economizing When It Should Not
1718 | 102 | Economizer Damper Not Modulating
1718 | 103 | Economizer Letting In Excess Outdoor Air
1718 | 104 | Duct Pressure Sensor Failure
1718 | 105 | Return Air Humidity Sensor Failure
1718 | 106 | Outdoor Air Humidity Sensor Failure
1718 | 107 | Supply Humidity Sensor Failure
1718 | 108 | Indoor Air Quality Sensor Failure
1718 | 109 | Outdoor Air Quality Sensor Failure
1718 | 110 | Fresh Air Intake Sensor Failure
1718 | 111 | Mixed Air Temp Sensor Failure
1718 | 112 | Space Indoor Temp Sensor Failure
1718 | 113 | Space Offset Sensor Failure
1718 | 114 | C1 Liquid Pressure Sensor Failure
1718 | 115 | C1 Suction Pressure Sensor Failure
1718 | 116 | C1 Evap Saturation Temp Sensor Failure
1718 | 117 | C1 Cond Saturation Temp Sensor Failure
1718 | 118 | C2 Liquid Pressure Sensor Failure
1718 | 119 | C2 Suction Pressure Sensor Failure
1718 | 120 | C2 Evap Saturation Temp Sensor Failure
1718 | 121 | C2 Cond Saturation Temp Sensor Failure
1718 | 122 | C3 Liquid Pressure Sensor Failure
1718 | 123 | C3 Suction Pressure Sensor Failure
1718 | 124 | C3 Evap Saturation Temp Sensor Failure
1718 | 125 | C3 Cond Saturation Temp Sensor Failure
1718 | 126 | C4 Liquid Pressure Sensor Failure
1718 | 127 | C4 Suction Pressure Sensor Failure
1718 | 128 | C4 Evap Saturation Temp Sensor Failure
1718 | 129 | C4 Cond Saturation Temp Sensor Failure
1718 | 130 | Air Proving Switch is Stuck Closed
1718 | 131 | Duplicate MSTP Address - No Comm
1718 | 132 | C1 Shutdown Due to High Pressure
1718 | 133 | C2 Shutdown Due to High Pressure
1718 | 134 | C3 Shutdown Due to High Pressure
1718 | 135 | C4 Shutdown Due to High Pressure
1718 | 136 | C1 Shutdown Due to Low Pressure
1718 | 137 | C2 Shutdown Due to Low Pressure
1718 | 138 | C3 Shutdown Due to Low Pressure
1718 | 139 | C4 Shutdown Due to Low Pressure
1718 | 140 | C1 Shutdown Due to Coil Freeze
1718 | 141 | C2 Shutdown Due to Coil Freeze
1718 | 142 | C3 Shutdown Due to Coil Freeze
1718 | 143 | C4 Shutdown Due to Coil Freeze
1718 | 144 | Excessive Supply Air Temp Cooling
1718 | 145 | Low Outdoor Air Temp Cooling Cutout
1718 | 146 | Not Economizing - No Outdoor Air Sensor
1718 | 147 | Not Economizing - No Supply Air Sensor
1718 | 148 | Excess Outdoor Air
1718 | 149 | HS1 Shutdown Due to Limit Switch
1718 | 150 | HS2 Shutdown Due to Limit Switch
1718 | 151 | HS3 Shutdown Due to Limit Switch
1718 | 152 | HS1 Off Due to Gas Valve
1718 | 153 | HS2 Off Due to Gas Valve
1718 | 154 | HS3 Off Due to Gas Valve
1718 | 155 | HS1 Gas Valve Failure
1718 | 156 | HS2 Gas Valve Failure
1718 | 157 | HS3 Gas Valve Failure
1718 | 158 | Hot H2o FS Open to Prevent Coil Freeze
1718 | 159 | Hot H2o FS Opened When It Should Not
1718 | 160 | Excessive Supply Air Temp Heating
1718 | 161 | Heating Locked Out Due to OA Temp
1718 | 162 | FDD 1 Communication Failure
1718 | 163 | FDD 2 Communication Failure
1718 | 164 | Stepped Heat Communication Failure
1718 | 165 | Unit is Starting
1718 | 166 | Unit has Received a Purge Request
1718 | 167 | Dirty Filter
1718 | 168 | Using Return Instead of Space Temp
1718 | 169 | Space Temperature Cooling Alarm
1718 | 170 | Real Time Clock Not Set
1718 | 171 | C1 Basic Data Not Available
1718 | 172 | C2 Basic Data Not Available
1718 | 173 | C3 Basic Data Not Available
1718 | 174 | C4 Basic Data Not Available
1718 | 175 | C1 Return Air Wet-Bulb Temp Out Of Range
1718 | 176 | C2 Return Air Wet-Bulb Temp Out Of Range
1718 | 177 | C3 Return Air Wet-Bulb Temp Out Of Range
1718 | 178 | C4 Return Air Wet-Bulb Temp Out Of Range
1718 | 179 | C1 Ambient Temp Too Low
1718 | 180 | C2 Ambient Temp Too Low
1718 | 181 | C3 Ambient Temp Too Low
1718 | 182 | C4 Ambient Temp Too Low
1718 | 183 | C1 Ambient Temp Too High
1718 | 184 | C2 Ambient Temp Too High
1718 | 185 | C3 Ambient Temp Too High
1718 | 186 | C4 Ambient Temp Too High
1718 | 187 | C1 Return Air Wet-Bulb Temp Too Low
1718 | 188 | C2 Return Air Wet-Bulb Temp Too Low
1718 | 189 | C3 Return Air Wet-Bulb Temp Too Low
1718 | 190 | C4 Return Air Wet-Bulb Temp Too Low
1718 | 191 | C1 Return Air Wet-Bulb Temp Too High
1718 | 192 | C2 Return Air Wet-Bulb Temp Too High
1718 | 193 | C3 Return Air Wet-Bulb Temp Too High
1718 | 194 | C4 Return Air Wet-Bulb Temp Too High
1718 | 195 | C1 Condensing Temp Less Than Ambient
1718 | 196 | C2 Condensing Temp Less Than Ambient
1718 | 197 | C3 Condensing Temp Less Than Ambient
1718 | 198 | C4 Condensing Temp Less Than Ambient
1718 | 199 | C1 Liquid Temp Greater Than Cond Temp
1718 | 200 | C2 Liquid Temp Greater Than Cond Temp
1718 | 201 | C3 Liquid Temp Greater Than Cond Temp
1718 | 202 | C4 Liquid Temp Greater Than Cond Temp
1718 | 203 | C1 Suction Temp Less Than Evap Temp
1718 | 204 | C2 Suction Temp Less Than Evap Temp
1718 | 205 | C3 Suction Temp Less Than Evap Temp
1718 | 206 | C4 Suction Temp Less Than Evap Temp
1718 | 207 | C1 Evap Temp Greater Than Ambient Temp
1718 | 208 | C2 Evap Temp Greater Than Ambient Temp
1718 | 209 | C3 Evap Temp Greater Than Ambient Temp
1718 | 210 | C4 Evap Temp Greater Than Ambient Temp
1718 | 211 | C1 Liquid Temp Less Than Ambient Temp
1718 | 212 | C2 Liquid Temp Less Than Ambient Temp
1718 | 213 | C3 Liquid Temp Less Than Ambient Temp
1718 | 214 | C4 Liquid Temp Less Than Ambient Temp
1718 | 215 | C1 Invalid Suction or Ambient Temp
1718 | 216 | C2 Invalid Suction or Ambient Temp
1718 | 217 | C3 Invalid Suction or Ambient Temp
1718 | 218 | C4 Invalid Suction or Ambient Temp
1718 | 219 | C1 Invalid RA Dry-Bulb or Wet-Bulb Temp
1718 | 220 | C2 Invalid RA Dry-Bulb or Wet-Bulb Temp
1718 | 221 | C3 Invalid RA Dry-Bulb or Wet-Bulb Temp
1718 | 222 | C4 Invalid RA Dry-Bulb or Wet-Bulb Temp
1718 | 223 | C1 Invalid Liquid and Suction Pressure
1718 | 224 | C2 Invalid Liquid and Suction Pressure
1718 | 225 | C3 Invalid Liquid and Suction Pressure
1718 | 226 | C4 Invalid Liquid and Suction Pressure
1718 | 227 | C1 Invalid Suction Temp
1718 | 228 | C2 Invalid Suction Temp
1718 | 229 | C3 Invalid Suction Temp
1718 | 230 | C4 Invalid Suction Temp
1718 | 231 | C1 Invalid Liquid and Suction Temp
1718 | 232 | C2 Invalid Liquid and Suction Temp
1718 | 233 | C3 Invalid Liquid and Suction Temp
1718 | 234 | C4 Invalid Liquid and Suction Temp
1718 | 235 | C1 Refrigerant Low
1718 | 236 | C2 Refrigerant Low
1718 | 237 | C3 Refrigerant Low
1718 | 238 | C4 Refrigerant Low
1718 | 239 | C1 Excessive Refrigerant Flow
1718 | 240 | C2 Excessive Refrigerant Flow
1718 | 241 | C3 Excessive Refrigerant Flow
1718 | 242 | C4 Excessive Refrigerant Flow
1718 | 243 | C1 Inefficient Compressor
1718 | 244 | C2 Inefficient Compressor
1718 | 245 | C3 Inefficient Compressor
1718 | 246 | C4 Inefficient Compressor
1718 | 247 | C1 Refrigerant Flow Restriction
1718 | 248 | C2 Refrigerant Flow Restriction
1718 | 249 | C3 Refrigerant Flow Restriction
1718 | 250 | C4 Refrigerant Flow Restriction
1718 | 251 | C1 High Side Heat Transfer Problem
1718 | 252 | C2 High Side Heat Transfer Problem
1718 | 253 | C3 High Side Heat Transfer Problem
1718 | 254 | C4 High Side Heat Transfer Problem
1718 | 255 | C1 Low Side Heat Transfer Problem
1718 | 256 | C2 Low Side Heat Transfer Problem
1718 | 257 | C3 Low Side Heat Transfer Problem
1718 | 258 | C4 Low Side Heat Transfer Problem
1718 | 259 | C1 Reduce Evaporator Airflow
1718 | 260 | C2 Reduce Evaporator Airflow
1718 | 261 | C3 Reduce Evaporator Airflow
1718 | 262 | C4 Reduce Evaporator Airflow
1718 | 263 | C1 Add Charge
1718 | 264 | C2 Add Charge
1718 | 265 | C3 Add Charge
1718 | 266 | C4 Add Charge
1718 | 267 | C1 Insufficient Refrigerant Flow
1718 | 268 | C2 Insufficient Refrigerant Flow
1718 | 269 | C3 Insufficient Refrigerant Flow
1718 | 270 | C4 Insufficient Refrigerant Flow
1718 | 271 | C1 Recover Charge
1718 | 272 | C2 Recover Charge
1718 | 273 | C3 Recover Charge
1718 | 274 | C4 Recover Charge
1718 | 275 | C1 Safe And Reasonable Performance
1718 | 276 | C2 Safe And Reasonable Performance
1718 | 277 | C3 Safe And Reasonable Performance
1718 | 278 | C4 Safe And Reasonable Performance
1718 | 279 | C1 Return Air Dry-Bulb Temp Too Low
1718 | 280 | C2 Return Air Dry-Bulb Temp Too Low
1718 | 281 | C3 Return Air Dry-Bulb Temp Too Low
1718 | 282 | C4 Return Air Dry-Bulb Temp Too Low
1718 | 283 | C1 Return Air Dry-Bulb Temp Too High
1718 | 284 | C2 Return Air Dry-Bulb Temp Too High
1718 | 285 | C3 Return Air Dry-Bulb Temp Too High
1718 | 286 | C4 Return Air Dry-Bulb Temp Too High
1718 | 287 | C1 FDD Not Functioning Sensor Unreliable
1718 | 288 | C2 FDD Not Functioning Sensor Unreliable
1718 | 289 | C3 FDD Not Functioning Sensor Unreliable
1718 | 290 | C4 FDD Not Monitoring Sensor Unreliable
1718 | 291 | C1 FDD Not Monitoring Conditions
1718 | 292 | C2 FDD Not Monitoring Conditions
1718 | 293 | C3 FDD Not Monitoring Conditions
1718 | 294 | C4 FDD Not Monitoring Conditions
1718 | 295 | C1 FDD Not Monitoring Equipment Data
1718 | 296 | C2 FDD Not Monitoring Equipment Data
1718 | 297 | C3 FDD Not Monitoring Equipment Data
1718 | 298 | C4 FDD Not Monitoring Equipment Data
1718 | 299 | C1 Non-Condensables Present
1718 | 300 | C2 Non-Condensables Present
1718 | 301 | C3 Non-Condensables Present
1718 | 302 | C4 Non-Condensables Present
1718 | 303 | C1 Unit Off
1718 | 304 | C2 Unit Off
1718 | 305 | C3 Unit Off
1718 | 306 | C4 Unit Off
1718 | 307 | Parameter Corruption Using Defaults
1718 | 308 | FDD Test Not Functioning Basic Data N/A
1718 | 309 | C1 FDD Test Inconsistent Sensors
1718 | 310 | C2 FDD Test Inconsistent Sensors
1718 | 311 | C3 FDD Test Inconsistent Sensors
1718 | 312 | C1 Faulty TxV valve
1718 | 313 | Space Temperature Heating Alarm
1718 | 314 | C1 EI Below 75% Expected Performance
1718 | 315 | C2 EI Below 75% Expected Performance
1718 | 316 | C3 EI Below 75% Expected Performance
1718 | 317 | C4 EI Below 75% Expected Performance
1718 | 318 | C1 CI Below 75% Expected Performance
1718 | 319 | C2 CI Below 75% Expected Performance
1718 | 320 | C3 CI Below 75% Expected Performance
1718 | 321 | C4 CI Below 75% Expected Performance
1718 | 322 | C1 EI+CI Below 75% Expected Performance
1718 | 323 | C2 EI+CI Below 75% Expected Performance
1718 | 324 | C3 EI+CI Below 75% Expected Performance
1718 | 325 | C4 EI+CI Below 75% Expected Performance
1718 | 326 | C1 Unknown Status
1718 | 327 | C2 Unknown Status
1718 | 328 | C3 Unknown Status
1718 | 329 | C4 Unknown Status
1718 | 330 | C1 RAT and Humidity Not Avail
1718 | 331 | C2 RAT and Humidity Not Avail
1718 | 332 | C3 RAT and Humidity Not Avail
1718 | 333 | C4 RAT and Humidity Not Avail
1718 | 334 | C1 Ambient Temp Out of Range
1718 | 335 | C2 Ambient Temp Out of Range
1718 | 336 | C3 Ambient Temp Out of Range
1718 | 337 | C4 Ambient Temp Out of Range
1718 | 338 | C1 Ambient and RAT WB Out of Range
1718 | 339 | C2 Ambient and RAT WB Out of Range
1718 | 340 | C3 Ambient and RAT WB Out of Range
1718 | 341 | C4 Ambient and RAT WB Out of Range
1718 | 342 | C1 Invalid Suction Pressure or RAT
1718 | 343 | C2 Invalid Suction Pressure or RAT
1718 | 344 | C3 Invalid Suction Pressure or RAT
1718 | 345 | C4 Invalid Suction Pressure or RAT
1718 | 346 | C1 Invalid Liquid Temp or RAT
1718 | 347 | C2 Invalid Liquid Temp or RAT
1718 | 348 | C3 Invalid Liquid Temp or RAT
1718 | 349 | C4 Invalid Liquid Temp or RAT
1718 | 350 | C1 Invalid Liquid Pressure or Ambient
1718 | 351 | C2 Invalid Liquid Pressure or Ambient
1718 | 352 | C3 Invalid Liquid Pressure or Ambient
1718 | 353 | C4 Invalid Liquid Pressure or Ambient
1718 | 354 | C1 Invalid RAT or SAT
1718 | 355 | C2 Invalid RAT or SAT
1718 | 356 | C3 Invalid RAT or SAT
1718 | 357 | C4 Invalid RAT or SAT
1718 | 358 | C1 Invalid SAT or Suction Pressure
1718 | 359 | C2 Invalid SAT or Suction Pressure
1718 | 360 | C3 Invalid SAT or Suction Pressure
1718 | 361 | C4 Invalid SAT or Suction Pressure
1718 | 362 | C1 Invalid SAT or SAT WB
1718 | 363 | C2 Invalid SAT or SAT WB
1718 | 364 | C3 Invalid SAT or SAT WB
1718 | 365 | C4 Invalid SAT or SAT WB
1718 | 366 | C1 Invalid RAT WB or SAT WB
1718 | 367 | C2 Invalid RAT WB or SAT WB
1718 | 368 | C3 Invalid RAT WB or SAT WB
1718 | 369 | C4 Invalid RAT WB or SAT WB
1718 | 370 | C1 Unfavorable Test Conditions - Retest
1718 | 371 | C2 Unfavorable Test Conditions - Retest
1718 | 372 | C3 Unfavorable Test Conditions - Retest
1718 | 373 | C4 Unfavorable Test Conditions - Retest
1718 | 374 | C1 Unit Energy Efficiency Ratio Too Low
1718 | 375 | C2 Unit Energy Efficiency Ratio Too Low
1718 | 376 | C3 Unit Energy Efficiency Ratio Too Low
1718 | 377 | C4 Unit Energy Efficiency Ratio Too Low
1718 | 378 | C1 Unit Energy Efficiency Ratio Too High
1718 | 379 | C2 Unit Energy Efficiency Ratio Too High
1718 | 380 | C3 Unit Energy Efficiency Ratio Too High
1718 | 381 | C4 Unit Energy Efficiency Ratio Too High
1718 | 382 | Self Test Alarm
1718 | 383 | Fan Runtime Alarm
1718 | 384 | SAT High Temp Alarm
1718 | 385 | SAT Low Temp Alarm
1718 | 390 | DAT Cannot Reach Cooling Setpoint
1718 | 391 | DAT Cannot Reach Heating Setpoint
1718 | 392 | Unit Continuous Runtime Exceeds Limit
1718 | 393 | Trim And Respond Not Changing Setpoint
1718 | 394 | Idle Time While Occupied Exceeds Limit
1718 | 395 | Pre Filter Pressure Sensor Failure
1718 | 396 | Final Filter Pressure Sensor Failure
1718 | 397 | Zone Air Humidity Sensor Failure
1718 | 398 | Heat Entering Temperature Sensor Failure
1718 | 399 | Outdoor Air Flow Sensor Failure
1718 | 400 | Disch Air Velocity Pressure Sensor Fail
1718 | 401 | Return Air Velocity Pressure Sensor Fail
1718 | 402 | Sensor Calibration Fault
1718 | 403 | Airflow Detected Without Supply Fan
1718 | 404 | UV Light Needs Service
1718 | 405 | C1 Liquid Temperature Sensor Failure
1718 | 406 | C2 Liquid Temperature Sensor Failure
1718 | 407 | C1 Suction Temperature Sensor Failure
1718 | 408 | C2 Suction Temperature Sensor Failure
1718 | 409 | C1 Discharge Pressure Sensor Failure
1718 | 410 | C2 Discharge Pressure Sensor Failure
1718 | 411 | C1 Discharge Temperature Sensor Failure
1718 | 412 | C2 Discharge Temperature Sensor Failure
1718 | 413 | Circuit 1 Shutdown Due To Safety Chain
1718 | 414 | Circuit 2 Shutdown Due To Safety Chain
1718 | 415 | Zone Temperature Sensor Failure
1718 | 416 | Return Air Quality Sensor Failure
1718 | 417 | Discharge Air Humidity Sensor Failure
1718 | 418 | Exhaust Heat Recovery Temp Sensor Fail
1718 | 419 | Slab Humidity Sensor Failure
1718 | 420 | Slab Temperature Sensor Failure
1718 | 421 | Simultaneous Cooling and Heating Calls
1718 | 422 | Unit has Received a Pressurize Request
1718 | 423 | Unit has Received a Depressurize Request
1718 | 424 | Proof Of Air Flow With No Fan Command
1718 | 425 | Circuit 1 Shutdown Due to Coil Freeze
1718 | 426 | Circuit 2 Shutdown Due to Coil Freeze
1719 | 0 | None
1719 | 1 | Event Generator Configuration Error
1719 | 2 | Calibration Error
1719 | 100 | Parameters Not Configured, Use Default
1719 | 101 | Economizer Firmware Failure
1719 | 102 | 4-Stage Firmware Failure
1719 | 103 | Main Controller Firmware Failure
1719 | 104 | C1 Locked Out Due to High Pressure
1719 | 105 | C2 Locked Out Due to High Pressure
1719 | 106 | C3 Locked Out Due to High Pressure
1719 | 107 | C4 Locked Out Due to High Pressure
1719 | 108 | C1 Locked Out Due to Low Pressure
1719 | 109 | C2 Locked Out Due to Low Pressure
1719 | 110 | C3 Locked Out Due to Low Pressure
1719 | 111 | C4 Locked Out Due to Low Pressure
1719 | 112 | C1 Locked Out Due to Coil Freeze
1719 | 113 | C2 Locked Out Due to Coil Freeze
1719 | 114 | C3 Locked Out Due to Coil Freeze
1719 | 115 | C4 Locked Out Due to Coil Freeze
1719 | 116 | Exhaust Fan VFD Failure
1719 | 117 | HS1 Locked Out Due to Limit Switch
1719 | 118 | HS2 Locked Out Due to Limit Switch
1719 | 119 | HS3 Locked Out Due to Limit Switch
1719 | 120 | Outputs Disabled Due to Low Input V
1719 | 121 | Outputs Limited Due to Brownout Input V
1719 | 122 | 4-Stg Outs Disabled Due to Low Input V
1719 | 123 | 4-Stg Outs Limited Due to Brownout V
1719 | 124 | 4-Stage O24 VAC Supply Input Failure
1719 | 125 | 4-Stage Communication Failure
1719 | 126 | Economizer Communication Failure
1719 | 127 | Unit Shutdown Due to Smoke, etc
1719 | 128 | Unit Locked Out Due to APS
1719 | 129 | Duct-P Incorrectly Reading Low
1719 | 130 | Unit Locked Out Due to High Duct-P
1719 | 131 | Unit Locked Out Due to Supply Fan OL
1719 | 132 | Supply Fan VFD Failure
1719 | 133 | No Heat-Cool Due to Unreliable Space-T
1719 | 134 | Unit Has Shutdown-Duct-P Sensor Failure
1719 | 135 | MFC HS1 Locked Out Due to Limit Switch
1719 | 136 | MFC HS2 Locked Out Due to Limit Switch
1719 | 137 | MFC HS3 Locked Out Due to Limit Switch
1719 | 138 | MFC HS4 Locked Out Due to Limit Switch
1719 | 139 | MFC HS1 Locked Out Due to Gas Valve
1719 | 140 | MFC HS2 Locked Out Due to Gas Valve
1719 | 141 | MFC HS3 Locked Out Due to Gas Valve
1719 | 142 | MFC HS4 Locked Out Due to Gas Valve
1719 | 143 | MFC Locked Out Due to No APS
1719 | 144 | MFC Locked Out Due to APS Stuck Closed
1719 | 145 | MFC Microelectronics Failure
1719 | 146 | MFC Shutdown Due to Bad Firmware
1719 | 147 | MFC Locked Out Due to Low Input V
1719 | 148 | C1 Locked Out Due to Condensate Overflow
1719 | 149 | Outputs Disabled Due to High Input V
1719 | 150 | EWT Out of Bounds, Comp Oper Suspended
1719 | 151 | LWT Out of Bounds, Comp Oper Suspended
1719 | 152 | SAT Out of Bounds, Comp Oper Suspended
1719 | 153 | C1 Locked Out Due to Water Coil Freeze
1719 | 154 | C1 Locked Out Due to Air Coil Freeze
1719 | 155 | Option Communication Failure
1719 | 156 | CTB Communication Failure
1719 | 157 | Condenser 1 Communication Failure
1719 | 158 | Condenser 2 Communication Failure
1719 | 159 | CTB Outs Disabled Due to Low Input V
1719 | 160 | CTB Outs Limited Due to Brownout V
1719 | 161 | Cond 1 Outs Disabled Due to Low Input V
1719 | 162 | Cond 1 Outs Limited Due to Brownout V
1719 | 163 | Cond 2 Outs Disabled Due to Low Input V
1719 | 164 | Cond 2 Outs Limited Due to Brownout V
1719 | 165 | Option Outs Disabled Due to Low Input V
1719 | 166 | Option Outs Limited Due to Brownout V
1719 | 167 | Exhaust Fan VFD 1 Failure
1719 | 168 | Exhaust Fan VFD 2 Failure
1719 | 169 | Supply Fan VFD 1 Failure
1719 | 170 | Supply Fan VFD 2 Failure
1719 | 171 | Unit Locked Out - Airflow Proof Failure
1719 | 172 | C1A Locked Out Due to High Pressure
1719 | 173 | C1B Locked Out Due to High Pressure
1719 | 174 | C1C Locked Out Due to High Pressure
1719 | 175 | C2A Locked Out Due to High Pressure
1719 | 176 | C2B Locked Out Due to High Pressure
1719 | 177 | C2C Locked Out Due to High Pressure
1719 | 178 | C1A Locked Out Due to Low Pressure
1719 | 179 | C1B Locked Out Due to Low Pressure
1719 | 180 | C1C Locked Out Due to Low Pressure
1719 | 181 | C2A Locked Out Due to Low Pressure
1719 | 182 | C2B Locked Out Due to Low Pressure
1719 | 183 | C2C Locked Out Due to Low Pressure
1719 | 184 | Circuit 1 Locked Out Due to Low Pressure
1719 | 185 | Circuit 2 Locked Out Due to Low Pressure
1719 | 186 | Circuit 1 Locked Out Due to Safety Chain
1719 | 187 | Circuit 2 Locked Out Due to Safety Chain
1719 | 188 | Cooling Locked Out - Condensate Overflow
1719 | 189 | C1A Locked Out - Exceeded Op Env Limits
1719 | 190 | C1A Locked Out Due to Oil Switch
1719 | 191 | Furnace Module 1 Lockout
1719 | 192 | Furnace Module 2 Lockout
1719 | 193 | Furnace Module 3 Lockout
1719 | 194 | Furnace Module 4 Lockout
1719 | 195 | Furnace Module 5 Lockout
1719 | 196 | C1A Locked Out Due to VFD Failure
1719 | 197 | Unit Shut Down by Safety Switch Input
1719 | 198 | Freeze Protect Disabled - Bad Sensor
1719 | 199 | Unit Shut Down by Phase Monitor
1719 | 200 | Condensate Alarm
1719 | 201 | C1 Locked Out - Exceeded Op Env Limits
1719 | 202 | C1 Locked Out Due to VFD Failure
1719 | 203 | C1 Locked Out Due to Oil Switch
1719 | 204 | C1 Locked Out - High Discharge Pressure
1719 | 205 | C2 Locked Out - High Discharge Pressure
1719 | 206 | C3 Locked Out - High Discharge Pressure
1719 | 207 | C4 Locked Out - High Discharge Pressure
1719 | 208 | C1 Locked Out - Low Suction Pressure
1719 | 209 | C2 Locked Out - Low Suction Pressure
1719 | 210 | C3 Locked Out - Low Suction Pressure
1719 | 211 | C4 Locked Out - Low Suction Pressure
1719 | 212 | Unit Locked Out - Iso Damper Closed
1719 | 213 | C1A Locked Out - High Pressure Unload
1719 | 214 | C1B Locked Out - High Pressure Unload
1719 | 215 | C1C Locked Out - High Pressure Unload
1719 | 216 | C2A Locked Out - High Pressure Unload
1719 | 217 | C2B Locked Out - High Pressure Unload
1719 | 218 | C2C Locked Out - High Pressure Unload
1719 | 219 | C1A Locked Out - Low Pressure Unload
1719 | 220 | C1B Locked Out - Low Pressure Unload
1719 | 221 | C1C Locked Out - Low Pressure Unload
1719 | 222 | C2A Locked Out - Low Pressure Unload
1719 | 223 | C2B Locked Out - Low Pressure Unload
1719 | 224 | C2C Locked Out - Low Pressure Unload
1719 | 225 | Unit has Received a Shutdown Request
1719 | 226 | Defrost Disabled - Bad Sensor
1719 | 227 | C1 Locked Out - High Discharge Line Temp
1719 | 228 | Circuit 1 Locked Out Due to Coil Freeze
1719 | 229 | Circuit 2 Locked Out Due to Coil Freeze
1719 | 230 | A2L Leak Detector Alarm
1719 | 231 | A2L Leak Detector Alarm-Lockout
1719 | 232 | Application Failed to Load
1720 | 0 | None
1720 | 1 | Firmware versions do not match package
1720 | 100 | FDD Firmware Failure
1720 | 101 | No Dehum Due to Space Humidity
1720 | 102 | No Air Quality Control Due to IAQ
1720 | 103 | Building Pressure Sensor Failure
1720 | 104 | Outdoor Air Temperature Sensor Failure
1720 | 105 | Return Air Temperature Sensor Failure
1720 | 106 | Supply Air Temperature Sensor Failure
1720 | 107 | 24 VAC Supply Input Failure
1720 | 108 | Evaporator Coil Temp 1 Sensor Failure
1720 | 109 | Condenser Coil Temp 1 Sensor Failure
1720 | 110 | Evaporator Coil Temp 2 Sensor Failure
1720 | 111 | Condenser Coil Temp 2 Sensor Failure
1720 | 112 | Evaporator Coil Temp 3 Sensor Failure
1720 | 113 | Condenser Coil Temp 3 Sensor Failure
1720 | 114 | Evaporator Coil Temp 4 Sensor Failure
1720 | 115 | Condenser Coil Temp 4 Sensor Failure
1720 | 116 | Unit Shutdown Due to Air Proving Switch
1720 | 117 | Unit Shutdown Due to Supply Fan Overload
1720 | 118 | Main Controller Calibration Error
1720 | 119 | FDDM Controller Calibration Error
1720 | 120 | Econ Controller Calibration Error
1720 | 121 | 4 Stage Controller Calibration Error
1720 | 122 | Duct Pressure Sensor Failure
1720 | 123 | FDDS Controller Calibration Error
1720 | 124 | MFC SAT Sensor Failure
1720 | 125 | MFC MAT Sensor Failure
1720 | 126 | MFC Jumper Set to Elite
1720 | 127 | Leaving Water Temp Sensor Failure
1720 | 128 | C1 Shutdown Due to Condensate Overflow
1720 | 129 | C1 Shutdown Due to Water Coil Freeze
1720 | 130 | C1 Shutdown Due to Air Coil Freeze
1720 | 131 | SAT Out of Bounds, Check Unit Operation
1720 | 132 | Entering Water Temp Sensor Failure
1720 | 134 | Discharge Air Temperature Sensor Failure
1720 | 135 | Return Fan Pressure Sensor Failure
1720 | 136 | Unit Shutdown Airflow Validation Fail
1720 | 137 | C1A Shutdown Due To High Pressure
1720 | 138 | C1B Shutdown Due To High Pressure
1720 | 139 | C1C Shutdown Due To High Pressure
1720 | 140 | C2A Shutdown Due To High Pressure
1720 | 141 | C2B Shutdown Due To High Pressure
1720 | 142 | C2C Shutdown Due To High Pressure
1720 | 143 | C1A Shutdown Due To Low Pressure
1720 | 144 | C1B Shutdown Due To Low Pressure
1720 | 145 | C1C Shutdown Due To Low Pressure
1720 | 146 | C2A Shutdown Due To Low Pressure
1720 | 147 | C2B Shutdown Due To Low Pressure
1720 | 148 | C2C Shutdown Due To Low Pressure
1720 | 149 | Circuit 1 Shutdown Due To Low Pressure
1720 | 150 | Circuit 2 Shutdown Due To Low Pressure
1720 | 151 | HGR Locked Out - Valve Stuck Open
1720 | 152 | HGR Locked Out - Valve Stuck Closed
1720 | 153 | Option Controller Calibration Error
1720 | 154 | Cond 1 Controller Calibration Error
1720 | 155 | Cond 2 Controller Calibration Error
1720 | 156 | CTB Controller Calibration Error
1720 | 157 | C1A Shutdown - Exceeded Op Env Limits
1720 | 158 | MAT Sensor Failure
1720 | 159 | Supply Fan 1 Failure
1720 | 160 | Supply Fan 2 Failure
1720 | 161 | C1 Shutdown - Exceeded Op Env Limits
1720 | 162 | C1 Shutdown - High Discharge Pressure
1720 | 163 | C2 Shutdown - High Discharge Pressure
1720 | 164 | C3 Shutdown - High Discharge Pressure
1720 | 165 | C4 Shutdown - High Discharge Pressure
1720 | 166 | C1 Shutdown - Low Suction Pressure
1720 | 167 | C2 Shutdown - Low Suction Pressure
1720 | 168 | C3 Shutdown - Low Suction Pressure
1720 | 169 | C4 Shutdown - Low Suction Pressure
1720 | 170 | C1A Shutdown - High Pressure Unload
1720 | 171 | C1B Shutdown - High Pressure Unload
1720 | 172 | C1C Shutdown - High Pressure Unload
1720 | 173 | C2A Shutdown - High Pressure Unload
1720 | 174 | C2B Shutdown - High Pressure Unload
1720 | 175 | C2C Shutdown - High Pressure Unload
1720 | 176 | C1A Shutdown - Low Pressure Unload
1720 | 177 | C1B Shutdown - Low Pressure Unload
1720 | 178 | C1C Shutdown - Low Pressure Unload
1720 | 179 | C2A Shutdown - Low Pressure Unload
1720 | 180 | C2B Shutdown - Low Pressure Unload
1720 | 181 | C2C Shutdown - Low Pressure Unload
1720 | 182 | Exhaust Fan 1 Failure
1720 | 183 | Exhaust Fan 2 Failure
1720 | 184 | Return Fan 1 Failure
1720 | 185 | Outdoor Air Damper BAS Source Lost
1720 | 186 | Exhaust Damper BAS Source Lost
1720 | 187 | Exhaust Fan BAS Source Lost
1721 | 0 | None
1721 | 1 | Reboot
1721 | 100 | Econ Not Economizing When It Should
1721 | 101 | Econ Economizing When It Should Not
1721 | 102 | Economizer Damper Not Modulating
1721 | 103 | Economizer Letting In Excess Outdoor Air
1721 | 104 | Duct Pressure Sensor Failure
1721 | 105 | Return Air Humidity Sensor Failure
1721 | 106 | Outdoor Air Humidity Sensor Failure
1721 | 107 | Supply Humidity Sensor Failure
1721 | 108 | Indoor Air Quality Sensor Failure
1721 | 109 | Outdoor Air Quality Sensor Failure
1721 | 110 | Fresh Air Intake Sensor Failure
1721 | 111 | Mixed Air Temp Sensor Failure
1721 | 112 | Space Indoor Temp Sensor Failure
1721 | 113 | Space Offset Sensor Failure
1721 | 114 | C1 Liquid Pressure Sensor Failure
1721 | 115 | C1 Suction Pressure Sensor Failure
1721 | 116 | C1 Evap Saturation Temp Sensor Failure
1721 | 117 | C1 Cond Saturation Temp Sensor Failure
1721 | 118 | C2 Liquid Pressure Sensor Failure
1721 | 119 | C2 Suction Pressure Sensor Failure
1721 | 120 | C2 Evap Saturation Temp Sensor Failure
1721 | 121 | C2 Cond Saturation Temp Sensor Failure
1721 | 122 | C3 Liquid Pressure Sensor Failure
1721 | 123 | C3 Suction Pressure Sensor Failure
1721 | 124 | C3 Evap Saturation Temp Sensor Failure
1721 | 125 | C3 Cond Saturation Temp Sensor Failure
1721 | 126 | C4 Liquid Pressure Sensor Failure
1721 | 127 | C4 Suction Pressure Sensor Failure
1721 | 128 | C4 Evap Saturation Temp Sensor Failure
1721 | 129 | C4 Cond Saturation Temp Sensor Failure
1721 | 130 | Air Proving Switch is Stuck Closed
1721 | 131 | Duplicate MSTP Address - No Comm
1721 | 132 | C1 Shutdown Due to High Pressure
1721 | 133 | C2 Shutdown Due to High Pressure
1721 | 134 | C3 Shutdown Due to High Pressure
1721 | 135 | C4 Shutdown Due to High Pressure
1721 | 136 | C1 Shutdown Due to Low Pressure
1721 | 137 | C2 Shutdown Due to Low Pressure
1721 | 138 | C3 Shutdown Due to Low Pressure
1721 | 139 | C4 Shutdown Due to Low Pressure
1721 | 140 | C1 Shutdown Due to Coil Freeze
1721 | 141 | C2 Shutdown Due to Coil Freeze
1721 | 142 | C3 Shutdown Due to Coil Freeze
1721 | 143 | C4 Shutdown Due to Coil Freeze
1721 | 144 | Excessive Supply Air Temp Cooling
1721 | 145 | Low Outdoor Air Temp Cooling Cutout
1721 | 146 | Not Economizing - No Outdoor Air Sensor
1721 | 147 | Not Economizing - No Supply Air Sensor
1721 | 148 | Excess Outdoor Air
1721 | 149 | HS1 Shutdown Due to Limit Switch
1721 | 150 | HS2 Shutdown Due to Limit Switch
1721 | 151 | HS3 Shutdown Due to Limit Switch
1721 | 152 | HS1 Off Due to Gas Valve
1721 | 153 | HS2 Off Due to Gas Valve
1721 | 154 | HS3 Off Due to Gas Valve
1721 | 155 | HS1 Gas Valve Failure
1721 | 156 | HS2 Gas Valve Failure
1721 | 157 | HS3 Gas Valve Failure
1721 | 158 | Hot H2o FS Open to Prevent Coil Freeze
1721 | 159 | Hot H2o FS Opened When It Should Not
1721 | 160 | Excessive Supply Air Temp Heating
1721 | 161 | Heating Locked Out Due to OA Temp
1721 | 162 | FDD 1 Communication Failure
1721 | 163 | FDD 2 Communication Failure
1721 | 164 | Stepped Heat Communication Failure
1721 | 165 | Unit is Starting
1721 | 166 | Unit has Received a Purge Request
1721 | 167 | Dirty Filter
1721 | 168 | Using Return Instead of Space Temp
1721 | 169 | Space Temperature Cooling Alarm
1721 | 170 | Real Time Clock Not Set
1721 | 171 | C1 Basic Data Not Available
1721 | 172 | C2 Basic Data Not Available
1721 | 173 | C3 Basic Data Not Available
1721 | 174 | C4 Basic Data Not Available
1721 | 175 | C1 Return Air Wet-Bulb Temp Out Of Range
1721 | 176 | C2 Return Air Wet-Bulb Temp Out Of Range
1721 | 177 | C3 Return Air Wet-Bulb Temp Out Of Range
1721 | 178 | C4 Return Air Wet-Bulb Temp Out Of Range
1721 | 179 | C1 Ambient Temp Too Low
1721 | 180 | C2 Ambient Temp Too Low
1721 | 181 | C3 Ambient Temp Too Low
1721 | 182 | C4 Ambient Temp Too Low
1721 | 183 | C1 Ambient Temp Too High
1721 | 184 | C2 Ambient Temp Too High
1721 | 185 | C3 Ambient Temp Too High
1721 | 186 | C4 Ambient Temp Too High
1721 | 187 | C1 Return Air Wet-Bulb Temp Too Low
1721 | 188 | C2 Return Air Wet-Bulb Temp Too Low
1721 | 189 | C3 Return Air Wet-Bulb Temp Too Low
1721 | 190 | C4 Return Air Wet-Bulb Temp Too Low
1721 | 191 | C1 Return Air Wet-Bulb Temp Too High
1721 | 192 | C2 Return Air Wet-Bulb Temp Too High
1721 | 193 | C3 Return Air Wet-Bulb Temp Too High
1721 | 194 | C4 Return Air Wet-Bulb Temp Too High
1721 | 195 | C1 Condensing Temp Less Than Ambient
1721 | 196 | C2 Condensing Temp Less Than Ambient
1721 | 197 | C3 Condensing Temp Less Than Ambient
1721 | 198 | C4 Condensing Temp Less Than Ambient
1721 | 199 | C1 Liquid Temp Greater Than Cond Temp
1721 | 200 | C2 Liquid Temp Greater Than Cond Temp
1721 | 201 | C3 Liquid Temp Greater Than Cond Temp
1721 | 202 | C4 Liquid Temp Greater Than Cond Temp
1721 | 203 | C1 Suction Temp Less Than Evap Temp
1721 | 204 | C2 Suction Temp Less Than Evap Temp
1721 | 205 | C3 Suction Temp Less Than Evap Temp
1721 | 206 | C4 Suction Temp Less Than Evap Temp
1721 | 207 | C1 Evap Temp Greater Than Ambient Temp
1721 | 208 | C2 Evap Temp Greater Than Ambient Temp
1721 | 209 | C3 Evap Temp Greater Than Ambient Temp
1721 | 210 | C4 Evap Temp Greater Than Ambient Temp
1721 | 211 | C1 Liquid Temp Less Than Ambient Temp
1721 | 212 | C2 Liquid Temp Less Than Ambient Temp
1721 | 213 | C3 Liquid Temp Less Than Ambient Temp
1721 | 214 | C4 Liquid Temp Less Than Ambient Temp
1721 | 215 | C1 Invalid Suction or Ambient Temp
1721 | 216 | C2 Invalid Suction or Ambient Temp
1721 | 217 | C3 Invalid Suction or Ambient Temp
1721 | 218 | C4 Invalid Suction or Ambient Temp
1721 | 219 | C1 Invalid RA Dry-Bulb or Wet-Bulb Temp
1721 | 220 | C2 Invalid RA Dry-Bulb or Wet-Bulb Temp
1721 | 221 | C3 Invalid RA Dry-Bulb or Wet-Bulb Temp
1721 | 222 | C4 Invalid RA Dry-Bulb or Wet-Bulb Temp
1721 | 223 | C1 Invalid Liquid and Suction Pressure
1721 | 224 | C2 Invalid Liquid and Suction Pressure
1721 | 225 | C3 Invalid Liquid and Suction Pressure
1721 | 226 | C4 Invalid Liquid and Suction Pressure
1721 | 227 | C1 Invalid Suction Temp
1721 | 228 | C2 Invalid Suction Temp
1721 | 229 | C3 Invalid Suction Temp
1721 | 230 | C4 Invalid Suction Temp
1721 | 231 | C1 Invalid Liquid and Suction Temp
1721 | 232 | C2 Invalid Liquid and Suction Temp
1721 | 233 | C3 Invalid Liquid and Suction Temp
1721 | 234 | C4 Invalid Liquid and Suction Temp
1721 | 235 | C1 Refrigerant Low
1721 | 236 | C2 Refrigerant Low
1721 | 237 | C3 Refrigerant Low
1721 | 238 | C4 Refrigerant Low
1721 | 239 | C1 Excessive Refrigerant Flow
1721 | 240 | C2 Excessive Refrigerant Flow
1721 | 241 | C3 Excessive Refrigerant Flow
1721 | 242 | C4 Excessive Refrigerant Flow
1721 | 243 | C1 Inefficient Compressor
1721 | 244 | C2 Inefficient Compressor
1721 | 245 | C3 Inefficient Compressor
1721 | 246 | C4 Inefficient Compressor
1721 | 247 | C1 Refrigerant Flow Restriction
1721 | 248 | C2 Refrigerant Flow Restriction
1721 | 249 | C3 Refrigerant Flow Restriction
1721 | 250 | C4 Refrigerant Flow Restriction
1721 | 251 | C1 High Side Heat Transfer Problem
1721 | 252 | C2 High Side Heat Transfer Problem
1721 | 253 | C3 High Side Heat Transfer Problem
1721 | 254 | C4 High Side Heat Transfer Problem
1721 | 255 | C1 Low Side Heat Transfer Problem
1721 | 256 | C2 Low Side Heat Transfer Problem
1721 | 257 | C3 Low Side Heat Transfer Problem
1721 | 258 | C4 Low Side Heat Transfer Problem
1721 | 259 | C1 Reduce Evaporator Airflow
1721 | 260 | C2 Reduce Evaporator Airflow
1721 | 261 | C3 Reduce Evaporator Airflow
1721 | 262 | C4 Reduce Evaporator Airflow
1721 | 263 | C1 Add Charge
1721 | 264 | C2 Add Charge
1721 | 265 | C3 Add Charge
1721 | 266 | C4 Add Charge
1721 | 267 | C1 Insufficient Refrigerant Flow
1721 | 268 | C2 Insufficient Refrigerant Flow
1721 | 269 | C3 Insufficient Refrigerant Flow
1721 | 270 | C4 Insufficient Refrigerant Flow
1721 | 271 | C1 Recover Charge
1721 | 272 | C2 Recover Charge
1721 | 273 | C3 Recover Charge
1721 | 274 | C4 Recover Charge
1721 | 275 | C1 Safe And Reasonable Performance
1721 | 276 | C2 Safe And Reasonable Performance
1721 | 277 | C3 Safe And Reasonable Performance
1721 | 278 | C4 Safe And Reasonable Performance
1721 | 279 | C1 Return Air Dry-Bulb Temp Too Low
1721 | 280 | C2 Return Air Dry-Bulb Temp Too Low
1721 | 281 | C3 Return Air Dry-Bulb Temp Too Low
1721 | 282 | C4 Return Air Dry-Bulb Temp Too Low
1721 | 283 | C1 Return Air Dry-Bulb Temp Too High
1721 | 284 | C2 Return Air Dry-Bulb Temp Too High
1721 | 285 | C3 Return Air Dry-Bulb Temp Too High
1721 | 286 | C4 Return Air Dry-Bulb Temp Too High
1721 | 287 | C1 FDD Not Functioning Sensor Unreliable
1721 | 288 | C2 FDD Not Functioning Sensor Unreliable
1721 | 289 | C3 FDD Not Functioning Sensor Unreliable
1721 | 290 | C4 FDD Not Monitoring Sensor Unreliable
1721 | 291 | C1 FDD Not Monitoring Conditions
1721 | 292 | C2 FDD Not Monitoring Conditions
1721 | 293 | C3 FDD Not Monitoring Conditions
1721 | 294 | C4 FDD Not Monitoring Conditions
1721 | 295 | C1 FDD Not Monitoring Equipment Data
1721 | 296 | C2 FDD Not Monitoring Equipment Data
1721 | 297 | C3 FDD Not Monitoring Equipment Data
1721 | 298 | C4 FDD Not Monitoring Equipment Data
1721 | 299 | C1 Non-Condensables Present
1721 | 300 | C2 Non-Condensables Present
1721 | 301 | C3 Non-Condensables Present
1721 | 302 | C4 Non-Condensables Present
1721 | 303 | C1 Unit Off
1721 | 304 | C2 Unit Off
1721 | 305 | C3 Unit Off
1721 | 306 | C4 Unit Off
1721 | 307 | Parameter Corruption Using Defaults
1721 | 308 | FDD Test Not Functioning Basic Data N/A
1721 | 309 | C1 FDD Test Inconsistent Sensors
1721 | 310 | C2 FDD Test Inconsistent Sensors
1721 | 311 | C3 FDD Test Inconsistent Sensors
1721 | 312 | C1 Faulty TxV valve
1721 | 313 | Space Temperature Heating Alarm
1721 | 314 | C1 EI Below 75% Expected Performance
1721 | 315 | C2 EI Below 75% Expected Performance
1721 | 316 | C3 EI Below 75% Expected Performance
1721 | 317 | C4 EI Below 75% Expected Performance
1721 | 318 | C1 CI Below 75% Expected Performance
1721 | 319 | C2 CI Below 75% Expected Performance
1721 | 320 | C3 CI Below 75% Expected Performance
1721 | 321 | C4 CI Below 75% Expected Performance
1721 | 322 | C1 EI+CI Below 75% Expected Performance
1721 | 323 | C2 EI+CI Below 75% Expected Performance
1721 | 324 | C3 EI+CI Below 75% Expected Performance
1721 | 325 | C4 EI+CI Below 75% Expected Performance
1721 | 326 | C1 Unknown Status
1721 | 327 | C2 Unknown Status
1721 | 328 | C3 Unknown Status
1721 | 329 | C4 Unknown Status
1721 | 330 | C1 RAT and Humidity Not Avail
1721 | 331 | C2 RAT and Humidity Not Avail
1721 | 332 | C3 RAT and Humidity Not Avail
1721 | 333 | C4 RAT and Humidity Not Avail
1721 | 334 | C1 Ambient Temp Out of Range
1721 | 335 | C2 Ambient Temp Out of Range
1721 | 336 | C3 Ambient Temp Out of Range
1721 | 337 | C4 Ambient Temp Out of Range
1721 | 338 | C1 Ambient and RAT WB Out of Range
1721 | 339 | C2 Ambient and RAT WB Out of Range
1721 | 340 | C3 Ambient and RAT WB Out of Range
1721 | 341 | C4 Ambient and RAT WB Out of Range
1721 | 342 | C1 Invalid Suction Pressure or RAT
1721 | 343 | C2 Invalid Suction Pressure or RAT
1721 | 344 | C3 Invalid Suction Pressure or RAT
1721 | 345 | C4 Invalid Suction Pressure or RAT
1721 | 346 | C1 Invalid Liquid Temp or RAT
1721 | 347 | C2 Invalid Liquid Temp or RAT
1721 | 348 | C3 Invalid Liquid Temp or RAT
1721 | 349 | C4 Invalid Liquid Temp or RAT
1721 | 350 | C1 Invalid Liquid Pressure or Ambient
1721 | 351 | C2 Invalid Liquid Pressure or Ambient
1721 | 352 | C3 Invalid Liquid Pressure or Ambient
1721 | 353 | C4 Invalid Liquid Pressure or Ambient
1721 | 354 | C1 Invalid RAT or SAT
1721 | 355 | C2 Invalid RAT or SAT
1721 | 356 | C3 Invalid RAT or SAT
1721 | 357 | C4 Invalid RAT or SAT
1721 | 358 | C1 Invalid SAT or Suction Pressure
1721 | 359 | C2 Invalid SAT or Suction Pressure
1721 | 360 | C3 Invalid SAT or Suction Pressure
1721 | 361 | C4 Invalid SAT or Suction Pressure
1721 | 362 | C1 Invalid SAT or SAT WB
1721 | 363 | C2 Invalid SAT or SAT WB
1721 | 364 | C3 Invalid SAT or SAT WB
1721 | 365 | C4 Invalid SAT or SAT WB
1721 | 366 | C1 Invalid RAT WB or SAT WB
1721 | 367 | C2 Invalid RAT WB or SAT WB
1721 | 368 | C3 Invalid RAT WB or SAT WB
1721 | 369 | C4 Invalid RAT WB or SAT WB
1721 | 370 | C1 Unfavorable Test Conditions - Retest
1721 | 371 | C2 Unfavorable Test Conditions - Retest
1721 | 372 | C3 Unfavorable Test Conditions - Retest
1721 | 373 | C4 Unfavorable Test Conditions - Retest
1721 | 374 | C1 Unit Energy Efficiency Ratio Too Low
1721 | 375 | C2 Unit Energy Efficiency Ratio Too Low
1721 | 376 | C3 Unit Energy Efficiency Ratio Too Low
1721 | 377 | C4 Unit Energy Efficiency Ratio Too Low
1721 | 378 | C1 Unit Energy Efficiency Ratio Too High
1721 | 379 | C2 Unit Energy Efficiency Ratio Too High
1721 | 380 | C3 Unit Energy Efficiency Ratio Too High
1721 | 381 | C4 Unit Energy Efficiency Ratio Too High
1721 | 382 | Self Test Alarm
1721 | 383 | Fan Runtime Alarm
1721 | 384 | SAT High Temp Alarm
1721 | 385 | SAT Low Temp Alarm
1721 | 390 | DAT Cannot Reach Cooling Setpoint
1721 | 391 | DAT Cannot Reach Heating Setpoint
1721 | 392 | Unit Continuous Runtime Exceeds Limit
1721 | 393 | Trim And Respond Not Changing Setpoint
1721 | 394 | Idle Time While Occupied Exceeds Limit
1721 | 395 | Pre Filter Pressure Sensor Failure
1721 | 396 | Final Filter Pressure Sensor Failure
1721 | 397 | Zone Air Humidity Sensor Failure
1721 | 398 | Heat Entering Temperature Sensor Failure
1721 | 399 | Outdoor Air Flow Sensor Failure
1721 | 400 | Disch Air Velocity Pressure Sensor Fail
1721 | 401 | Return Air Velocity Pressure Sensor Fail
1721 | 402 | Sensor Calibration Fault
1721 | 403 | Airflow Detected Without Supply Fan
1721 | 404 | UV Light Needs Service
1721 | 405 | C1 Liquid Temperature Sensor Failure
1721 | 406 | C2 Liquid Temperature Sensor Failure
1721 | 407 | C1 Suction Temperature Sensor Failure
1721 | 408 | C2 Suction Temperature Sensor Failure
1721 | 409 | C1 Discharge Pressure Sensor Failure
1721 | 410 | C2 Discharge Pressure Sensor Failure
1721 | 411 | C1 Discharge Temperature Sensor Failure
1721 | 412 | C2 Discharge Temperature Sensor Failure
1721 | 413 | Circuit 1 Shutdown Due To Safety Chain
1721 | 414 | Circuit 2 Shutdown Due To Safety Chain
1721 | 415 | Zone Temperature Sensor Failure
1721 | 416 | Return Air Quality Sensor Failure
1721 | 417 | Discharge Air Humidity Sensor Failure
1721 | 418 | Exhaust Heat Recovery Temp Sensor Fail
1721 | 419 | Slab Humidity Sensor Failure
1721 | 420 | Slab Temperature Sensor Failure
1721 | 421 | Simultaneous Cooling and Heating Calls
1721 | 422 | Unit has Received a Pressurize Request
1721 | 423 | Unit has Received a Depressurize Request
1721 | 424 | Proof Of Air Flow With No Fan Command
1721 | 425 | Circuit 1 Shutdown Due to Coil Freeze
1721 | 426 | Circuit 2 Shutdown Due to Coil Freeze
1722 | 0 | MicroChannel
1722 | 1 | Tube and Fin
1724 | 0 | Not Installed
1724 | 1 | BACnet
1724 | 2 | N2
1724 | 3 | Modbus
1727 | 0 | Firmware Versions OK
1727 | 1 | Firmware Versions Do Not Match the Package
1728 | 0 | Schedule
1728 | 1 | External
1729 | 0 | Disabled
1729 | 1 | Controlled by IAQ
1729 | 2 | Diff between IAQ and OAQ
1730 | 7 | English
1730 | 10 | French
1730 | 28 | Spanish
1731 | 51 | Eastern
1731 | 53 | Central
1731 | 57 | Mountain
1731 | 58 | Pacific
1731 | 69 | Newfoundland
1731 | 70 | Atlantic
1731 | 71 | Alaska
1731 | 72 | Hawaii
1732 | 0 | Unreliable
1732 | 1 | Local Input
1732 | 2 | Network Sensor
1732 | 3 | High Priority
1732 | 4 | BAS Override
1732 | 5 | Input Not Available
1737 | 0 | Idle
1737 | 1 | SD Alarm
1737 | 2 | Purge Command
1737 | 3 | Self Test
1737 | 4 | Morning Warm Up
1737 | 5 | Air Tempering
1737 | 6 | Dehumidification
1737 | 7 | Heating
1737 | 8 | Cooling
1737 | 9 | Economizer
1737 | 10 | Fan Only
1737 | 11 | Comfort Ventilation
1737 | 12 | Startup Delay
1738 | 0 | Disabled
1738 | 1 | Damper Not Functional
1738 | 2 | Purge
1738 | 3 | Unavailable-Sensor Fault
1738 | 4 | Econ Loading
1738 | 5 | SA-T High Limit
1738 | 6 | Mixed Air Low Limit Cycle
1738 | 7 | Demand Ventilation Air Quality
1738 | 8 | Outdoor Airflow Control
1738 | 9 | Free Cooling is Active
1738 | 10 | Minimum Position
1738 | 11 | Test
1738 | 12 | Comfort Ventilation
1738 | 13 | Low OA Ambient
1739 | 0 | Off-Idle
1739 | 1 | On-Purge
1739 | 2 | On-Gas Valve or Limit Fault
1739 | 3 | On-Defrost
1739 | 4 | On-Thermostat Request
1739 | 5 | On-Fan Off Delay For Cool
1739 | 6 | On-Fan Off Delay For Heat
1739 | 7 | On-Continuous Fan Occupied Operation
1739 | 8 | On-Normal Command
1739 | 9 | Off-Exceeding Duct Pressure Shutdown SP
1739 | 10 | Off-Low Voltage
1739 | 11 | Off-Fan Overload Lockout
1739 | 12 | Off-Fan VFD Fault
1739 | 13 | Off-Hot Water Freeze Stat
1739 | 14 | Off-Air Proving Switch
1739 | 15 | Off-Minimum Off Delay
1739 | 16 | Off-Fan On Delay For Heat
1739 | 17 | Off-Fan Off Delay For Cool
1740 | 0 | Off-Idle
1740 | 1 | Thermostat Cooling
1740 | 2 | Unoccupied Cooling
1740 | 3 | Occupied Cooling
1740 | 4 | Off-OAT Lockout
1740 | 5 | Off-Disabled
1740 | 6 | Off-Lockout
1740 | 7 | Off-Low Supply Voltage
1740 | 8 | Off-Low Ambient
1740 | 9 | Off-Low Ambient Pre-Run Delay
1740 | 10 | Off-Waiting For Changeover Delay
1740 | 11 | Off-Free Cooling
1740 | 12 | Comfort Ventilation
1741 | 0 | Off-Idle
1741 | 1 | On-Minimum On Time
1741 | 2 | On-Normal Command
1741 | 3 | Off-Cooling Is Disabled
1741 | 4 | Off-OAT Cutout
1741 | 5 | Off-Low Ambient Temperature
1741 | 6 | Off-Low Supply Voltage
1741 | 7 | Off-High Pressure Lockout
1741 | 8 | Off-Low Pressure Lockout
1741 | 9 | Off-Freeze Condition
1741 | 10 | Off-Anti-Short Cycle Delay
1741 | 11 | Off-Cooling Stage Is Disabled
1741 | 12 | On-Envelope Control Speed Override
1741 | 13 | On-Oil Management Speed Override
1741 | 14 | Shutdown-VFD Alarm
1741 | 15 | Shutdown-Compressor Safety Chain
1741 | 16 | Shutdown-Envelope Limit
1741 | 17 | Shutdown-Low Oil Level
1741 | 18 | Shutdown-High Liquid Line Pressure Unloading
1741 | 19 | Shutdown-Low Suction Pressure Unloading
1741 | 20 | Shutdown-Low Pressure Safety
1741 | 21 | Lockout-VFD Alarm
1741 | 22 | Lockout-Compressor Safety Chain
1741 | 23 | Lockout-Envelope Limit
1741 | 24 | Lockout-Low Oil Level
1741 | 25 | Lockout-High Liquid Line Pressure Unloading
1741 | 26 | Lockout-Low Suction Pressure Unloading
1741 | 27 | Lockout-Low Pressure Safety
1741 | 28 | Shutdown-High Discharge Line Pressure Unloading
1741 | 29 | Lockout-High Discharge Line Pressure Unloading
1742 | 0 | Off-Idle
1742 | 1 | On-Defrost
1742 | 2 | SAT Tempering
1742 | 3 | Morning Warmup
1742 | 4 | Thermostat Heating
1742 | 5 | Unoccupied Heating
1742 | 6 | Occupied Heating
1742 | 7 | Off-Disabled
1742 | 8 | Off-OAT Lockout
1742 | 9 | Off-SAT Limit
1742 | 10 | Off-Waiting For Changeover Delay
1742 | 11 | Comfort Ventilation
1743 | 0 | Off-Idle
1743 | 1 | On-Minimum Runtime Timer
1743 | 2 | On-Normal Command
1743 | 3 | Off-Heating Is Disabled
1743 | 4 | Off-Gas Valve Lost Proof
1743 | 5 | Off-Gas Valve False Proof
1743 | 6 | Off-Heating Limit Lockout
1743 | 7 | Off-Anti-Short Cycle Timer
1743 | 8 | Off-Heating Stage Is Disabled
1744 | 0 | Off-Idle
1744 | 1 | On-Normal Command
1744 | 2 | On-Alternate Operation Command
1744 | 3 | Off-Disabled
1745 | 0 | Off-Idle
1745 | 1 | On-Normal Command
1745 | 2 | Off-Disabled
1745 | 3 | Off-VFD Fault
1745 | 4 | Off-Low Building Static Pressure
1745 | 5 | Off-Economizer Damper Position
1752 | 0 | Option A
1752 | 1 | Option B
1790 | 0 | Exhaust Fan
1793 | 0 | False
1793 | 1 | True
2513 | 0 | Normal
2513 | 1 | Lost Coordinator
2513 | 2 | Network Reforming
2513 | 3 | Single Neighbor
2513 | 4 | Duplicate Address
2513 | 5 | Invalid PAN ID
2513 | 6 | Weak Route
2513 | 7 | No Neighbors
2594 | 0 | None
2594 | 1 | Chiller 1 Interlock Alarm
2594 | 2 | Chiller 2 Interlock Alarm
2594 | 3 | Chiller 3 Interlock Alarm
2594 | 4 | Chiller 4 Interlock Alarm
2594 | 5 | Chilled Water Pump 1 Interlock Alarm
2594 | 6 | Chilled Water Pump 2 Interlock Alarm
2594 | 7 | Chilled Water Pump 3 Interlock Alarm
2594 | 8 | Chilled Water Pump 4 Interlock Alarm
2594 | 9 | Cooling Tower 1 Interlock Alarm
2594 | 10 | Cooling Tower 2 Interlock Alarm
2594 | 11 | Cooling Tower 3 Interlock Alarm
2594 | 12 | Cooling Tower 4 Interlock Alarm
2594 | 13 | Condenser Water Pump 1 Interlock Alarm
2594 | 14 | Condenser Water Pump 2 Interlock Alarm
2594 | 15 | Condenser Water Pump 3 Interlock Alarm
2594 | 16 | Condenser Water Pump 4 Interlock Alarm
2594 | 17 | Chiller 1 Chilled Water DP Failure
2594 | 18 | Chiller 2 Chilled Water DP Failure
2594 | 19 | Chiller 3 Chilled Water DP Failure
2594 | 20 | Chiller 4 Chilled Water DP Failure
2594 | 21 | Building Chilled Water DP Failure
2594 | 22 | Primary Chilled Water Flow Failure
2594 | 23 | Chiller 1 Chilled Water Supply Temp Fail
2594 | 24 | Chiller 2 Chilled Water Supply Temp Fail
2594 | 25 | Chiller 3 Chilled Water Supply Temp Fail
2594 | 26 | Chiller 4 Chilled Water Supply Temp Fail
2594 | 27 | Chiller 1 Chilled Water Return Temp Fail
2594 | 28 | Chiller 2 Chilled Water Return Temp Fail
2594 | 29 | Chiller 3 Chilled Water Return Temp Fail
2594 | 30 | Chiller 4 Chilled Water Return Temp Fail
2594 | 31 | Chiller 1 Cond Water Supply Temp Fail
2594 | 32 | Chiller 2 Cond Water Supply Temp Fail
2594 | 33 | Chiller 3 Cond Water Supply Temp Fail
2594 | 34 | Chiller 4 Cond Water Supply Temp Fail
2594 | 35 | Outside Air Temperature Failure
2594 | 36 | Outside Air Humidity Failure
2594 | 37 | Chiller 1 IOM Comm Failure
2594 | 38 | Chiller 2 IOM Comm Failure
2594 | 39 | Chiller 3 IOM Comm Failure
2594 | 40 | Chiller 4 IOM Comm Failure
2594 | 41 | Cooling Tower 1 and 2 IOM Comm Failure
2594 | 42 | Cooling Tower 3 and 4 IOM Comm Failure
2594 | 43 | Chiller 1 SC-Equip Comm Failure
2594 | 44 | Chiller 2 SC-Equip Comm Failure
2594 | 45 | Chiller 3 SC-Equip Comm Failure
2594 | 46 | Chiller 4 SC-Equip Comm Failure
2596 | 0 | Common Setpoint
2596 | 1 | Individual Setpoints
2644 | 39 | Operating Cooling Discharge Air Temp Setpoint
2644 | 40 | Operating Heating Discharge Air Temp Setpoint
2644 | 208 | Supply Fan Command
2644 | 227 | Discharge Air Static Pressure Minimum
2644 | 228 | Discharge Air Static Pressure Alarm Delay
2644 | 238 | Hot Gas Reheat Bleed Valve Command
2644 | 274 | Mixed Air Temperature Cooling Limit
2644 | 292 | Modulating Compressor Output
2644 | 293 | Modulating Condenser Fan 1 Output
2644 | 294 | Modulating Condenser Fan 2 Output
2644 | 323 | Circuit 1 Modulating Condenser Fan Installed
2644 | 324 | Circuit 2 Modulating Condenser Fan Installed
2644 | 366 | Suction Superheat 1
2644 | 370 | Saturated Discharge Temperature 1
2644 | 371 | Saturated Discharge Temperature 2
2644 | 374 | Saturated Suction Temperature 1
2644 | 375 | Saturated Suction Temperature 2
2644 | 378 | Discharge Line Pressure 1
2644 | 379 | Discharge Line Pressure 2
2644 | 380 | Discharge Line Temperature 1
2644 | 381 | Discharge Line Temperature 2
2644 | 383 | Condensate Alarm Enable
2644 | 418 | Oil Switch Installed
2644 | 442 | Circuit 1 OAT Cooling Cutout
2644 | 443 | Circuit 2 OAT Cooling Cutout
2644 | 447 | Commissioning Time Remaining
2644 | 448 | Extend Commissioning Time
2644 | 482 | Discharge Line Pressure
2644 | 483 | Discharge Line Temperature
2644 | 484 | Compressor VFD Alarm
2644 | 507 | Oil Level Switch
2644 | 549 | A2L Fan Speed
2645 | 110 | EVAP-T
2645 | 244 | DAP-Min
2645 | 245 | DAP-AlmDly
2645 | 293 | MATClgLim
2645 | 311 | ModCompOut
2645 | 312 | ModCondFan1Out
2645 | 313 | ModCondFan2Out
2645 | 342 | ModCondFanCir1En
2645 | 343 | ModCondFanCir2En
2645 | 358 | OprClgDAT-SP
2645 | 359 | OprHtgDAT-SP
2645 | 369 | HGRB-C
2645 | 374 | SucSuperheat1
2645 | 378 | SatDischTemp1
2645 | 379 | SatDischTemp2
2645 | 382 | SatSucTemp1
2645 | 383 | SatSucTemp2
2645 | 386 | DLP1
2645 | 387 | DLP2
2645 | 388 | DLT1
2645 | 389 | DLT2
2645 | 425 | Circ1ClgOATCutout
2645 | 426 | Circ2ClgOATCutout
2645 | 428 | CommishTimeRemaining
2645 | 429 | ExtendCommishTime
2645 | 440 | OprClg-Sp
2645 | 441 | OprHtg-Sp
2645 | 445 | CompVFD-Alarm
2645 | 467 | OIL-A
3338 | 0 | Dry Bulb Temperature
3338 | 1 | Differential Dry Bulb
3338 | 2 | Single Enthalpy
3338 | 3 | Dual Enthalpy
3338 | 4 | Unreliable
3356 | 0 | Standard
3356 | 1 | Tandem Cir1 With 2 Stage Cir2
3356 | 2 | 2 Stage Cir1 With 2 Stage Cir2
3356 | 3 | 2 Stage Cir1 With Single Cir2
3356 | 4 | Tandem Cir1 With Single Cir2
3356 | 5 | Inverted Single Cir1 With Single Cir2
3356 | 6 | Single Modulating Cir1 With 2 Stage Cir2
3356 | 7 | Single Modulating Cir1 With Single Cir2
3356 | 8 | Single Modulating Cir1 With Tandem Cir2
3356 | 9 | Hybrid Tandem Cir1 With 2 Stage Cir2
3356 | 10 | Hybrid Tandem Cir1 With Tandem Cir2
3398 | 0 | Dry Bulb Temperature
3398 | 1 | Single Enthalpy
3398 | 2 | Dual Enthalpy
3398 | 3 | Auto
3398 | 4 | Differential Dry Bulb
3452 | 0 | No Lockout
3452 | 1 | Three Strikes
3452 | 2 | Always Lockout
40548 | 0 | Not Connected
40548 | 1 | Waiting for Connection
40548 | 2 | Connected
40548 | 3 | Disabled
40548 | 4 | Error
40549 | 0 | Start
40549 | 1 | Stop
40549 | 2 | Started
40549 | 3 | Stopped